## Neutral scenario
Deploy Option C2 and D1 by start of 2025 financial year
Neutral scenario | Financial year
Constraint description | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | Comments
No prior outage. Avoid overload of Ballarat to Terang for loss of Moorabool to Terang. | 0 | 0 | 0 | 659 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load flow studies showed that these constraints can be managed using a control scheme. If implemeted, this will reduce some of the negative dispatch benefits in Victoria.
No prior outage. Avoid overload of Kerang to Bendigo for loss of Red Cliffs to Buronga. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No binding constraints after Red Cliffs to Buronga upgrade is implemented
No prior outage. Avoid overload of Kerang to Bendigo for loss of Ballarat to Waubra. | 275 | 256 | 282 | 561 | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Kerang for loss of Horsham to Ararat. | 7 | 4 | 8 | 53 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Red Cliffs for loss of Bendigo to Kerang. | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 3 | 2 | 1 | 1 | 1
No prior outage. Avoid overload of Ballarat to Bendigo for loss of Horsham to Red Cliffs. | 0 | 2 | 10 | 13 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Bendigo to Kerang. | 637 | 544 | 508 | 555 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Horsham to Red Cliffs. | 1800 | 1787 | 1748 | 2502 | 2219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary binding constraint and source of market benefits.
No prior outage. Avoid overload of Ballarat to Waubra during system normal. | 10 | 5 | 5 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ararat to Waubra for loss of Horsham to Red Cliffs. | 67 | 75 | 67 | 151 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Ballarat for loss of Elaine to Moorabool. | 0 | 18 | 11 | 6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Moorabool for loss of Elaine to Ballarat. | 0 | 0 | 38 | 114 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Neutral with storage scenario
Deploy Option C2 and D1 by start of 2025 financial year
Neutral with storage scenario | Financial year
Constraint description | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | Comments
No prior outage. Avoid overload of Ballarat to Terang for loss of Moorabool to Terang. | 0 | 0 | 0 | 658 | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load flow studies showed that these constraints can be managed using a control scheme. If implemeted, this will reduce some of the negative dispatch benefits in Victoria.
No prior outage. Avoid overload of Kerang to Bendigo for loss of Red Cliffs to Buronga. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No binding constraints after Red Cliffs to Buronga upgrade is implemented
No prior outage. Avoid overload of Kerang to Bendigo for loss of Ballarat to Waubra. | 280 | 263 | 285 | 564 | 471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Kerang for loss of Horsham to Ararat. | 7 | 4 | 8 | 52 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Red Cliffs for loss of Bendigo to Kerang. | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 2 | 2 | 1 | 1 | 1
No prior outage. Avoid overload of Ballarat to Bendigo for loss of Horsham to Red Cliffs. | 0 | 3 | 11 | 10 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Bendigo to Kerang. | 629 | 542 | 511 | 566 | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Horsham to Red Cliffs. | 1804 | 1786 | 1750 | 2492 | 2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary binding constraint and source of market benefits.
No prior outage. Avoid overload of Ballarat to Waubra during system normal. | 11 | 4 | 4 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ararat to Waubra for loss of Horsham to Red Cliffs. | 74 | 77 | 66 | 148 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Ballarat for loss of Elaine to Moorabool. | 0 | 18 | 11 | 6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Moorabool for loss of Elaine to Ballarat. | 0 | 0 | 39 | 113 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Fast change scenario
Deploy Option C2 and D1 by start of 2025 financial year
Fast change scenario | Financial year
Constraint description | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | Comments
No prior outage. Avoid overload of Ballarat to Terang for loss of Moorabool to Terang. | 0 | 0 | 0 | 638 | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load flow studies showed that these constraints can be managed using a control scheme. If implemeted, this will reduce some of the negative dispatch benefits in Victoria.
No prior outage. Avoid overload of Kerang to Bendigo for loss of Red Cliffs to Buronga. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No binding constraints after Red Cliffs to Buronga upgrade is implemented
No prior outage. Avoid overload of Kerang to Bendigo for loss of Ballarat to Waubra. | 184 | 156 | 183 | 303 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Kerang for loss of Horsham to Ararat. | 2 | 2 | 3 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Red Cliffs for loss of Bendigo to Kerang. | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 5 | 5 | 2 | 2 | 2
No prior outage. Avoid overload of Ballarat to Bendigo for loss of Horsham to Red Cliffs. | 0 | 3 | 10 | 11 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Bendigo to Kerang. | 597 | 492 | 460 | 459 | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Horsham to Red Cliffs. | 1903 | 1878 | 1825 | 2708 | 2448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary binding constraint and source of market benefits.
No prior outage. Avoid overload of Ballarat to Waubra during system normal. | 11 | 8 | 5 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ararat to Waubra for loss of Horsham to Red Cliffs. | 118 | 73 | 84 | 218 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Ballarat for loss of Elaine to Moorabool. | 0 | 18 | 9 | 7 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Moorabool for loss of Elaine to Ballarat. | 0 | 0 | 47 | 123 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slow change scenario
Deploy Option C2 and D1 by start of 2025 financial year
Slow change scenario | Financial year
Constraint description | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | Comments
No prior outage. Avoid overload of Ballarat to Terang for loss of Moorabool to Terang. | 0 | 0 | 0 | 669 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load flow studies showed that these constraints can be managed using a control scheme. If implemeted, this will reduce some of the negative dispatch benefits in Victoria.
No prior outage. Avoid overload of Kerang to Bendigo for loss of Red Cliffs to Buronga. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No binding constraints after Red Cliffs to Buronga upgrade is implemented
No prior outage. Avoid overload of Kerang to Bendigo for loss of Ballarat to Waubra. | 224 | 190 | 222 | 364 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Kerang for loss of Horsham to Ararat. | 1 | 1 | 4 | 28 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Wemen to Red Cliffs for loss of Bendigo to Kerang. | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Bendigo for loss of Horsham to Red Cliffs. | 0 | 1 | 10 | 30 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Bendigo to Kerang. | 549 | 468 | 427 | 378 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ballarat to Waubra for loss of Horsham to Red Cliffs. | 1868 | 1836 | 1806 | 2445 | 1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary binding constraint and source of market benefits.
No prior outage. Avoid overload of Ballarat to Waubra during system normal. | 5 | 3 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Ararat to Waubra for loss of Horsham to Red Cliffs. | 93 | 70 | 77 | 131 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Ballarat for loss of Elaine to Moorabool. | 0 | 18 | 10 | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No prior outage. Avoid overload of Elaine to Moorabool for loss of Elaine to Ballarat. | 0 | 0 | 39 | 97 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Update - IC binding hours
Constraint binding hours for Victorian interconnectors
Interconnector constraints grouped by direction of flow when constraints are binding, included all thermal and stability constraints
Scenario | Constraint | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Neutral | NSW to Vic | 1727 | 1470 | 1723 | 1241 | 765 | 335 | 282 | 239 | 238 | 222 | 301 | 351 | 259
Neutral | Vic to NSW | 1096 | 1171 | 1173 | 1926 | 3708 | 5306 | 3981 | 4890 | 3465 | 3691 | 5036 | 4974 | 4230
Neutral | SA to Vic | 722 | 710 | 749 | 1610 | 1922 | 1130 | 1236 | 1148 | 1110 | 1227 | 1226 | 1299 | 1216
Neutral | Vic to SA | 16 | 20 | 22 | 19 | 28 | 909 | 1078 | 1168 | 1136 | 1119 | 1153 | 1170 | 1101
Neutral with Storage | NSW to Vic | 1737 | 1451 | 1761 | 1233 | 782 | 487 | 529 | 333 | 664 | 302 | 215 | 259 | 323
NeutralwStorage | Vic to NSW | 1087 | 1199 | 1197 | 1948 | 3680 | 5060 | 3886 | 4888 | 3666 | 3819 | 4965 | 4788 | 4130
NeutralwStorage | SA to Vic | 705 | 708 | 742 | 1597 | 1905 | 1036 | 1015 | 971 | 968 | 1003 | 1020 | 991 | 943
NeutralwStorage | Vic to SA | 17 | 23 | 21 | 18 | 27 | 1002 | 946 | 1023 | 1005 | 851 | 929 | 910 | 794
Fast Change | NSW to Vic | 3601 | 3355 | 3223 | 1810 | 1127 | 273 | 460 | 411 | 961 | 227 | 118 | 139 | 141
| Vic to NSW | 923 | 986 | 882 | 1343 | 2838 | 3956 | 3012 | 3685 | 1973 | 2045 | 2528 | 2638 | 2243
| SA to Vic | 330 | 343 | 365 | 479 | 792 | 385 | 376 | 338 | 274 | 535 | 1380 | 1303 | 1589
| Vic to SA | 29 | 25 | 15 | 20 | 39 | 1241 | 1082 | 1132 | 888 | 760 | 1078 | 1034 | 432
Slow Change | NSW to Vic | 630 | 673 | 499 | 796 | 1563 | 490 | 419 | 448 | 309 | 399 | 534 | 535 | 374
Slow Change | Vic to NSW | 1910 | 2019 | 2780 | 5197 | 7068 | 8540 | 7029 | 8281 | 6674 | 6558 | 7993 | 7855 | 7002
Slow Change | SA to Vic | 599 | 572 | 637 | 1158 | 1478 | 669 | 603 | 532 | 581 | 516 | 543 | 515 | 474
Slow Change | Vic to SA | 9 | 17 | 13 | 13 | 12 | 833 | 827 | 788 | 835 | 787 | 765 | 752 | 740