## Introduction
How to use this document
Parameters that need to be supplied by the solar farm to AEMO are listed and marked as 'Required'.
Sampling rates for dynamic parameters are specified. These denote the sampling intervals for data. Aggregation of this data will be done within MMS or the ECM.
Document structure
The document is divided by technology types. To this end:
the 'ECM PV' worksheet contains parameters for solar PV farms with and without tracking technology
the 'ECM CPV' worksheet contains parameters for concentrating solar PV technologies
the 'ECM CST' worksheet contains parameters for concentrating solar thermal technologies
Facility hierarchy
There is an assumed hierarchy of sub-components that constitute a solar farm. These are illustrated in the diagram below
In the event that multiple sub-components are available, parameters applicable to these sub-components will need to be provided for each sub-component.
E.g. There are multiple clusters in a facility. Parameters that are applicable to every cluster in the ECM PV worksheet will need to be provided
Terms and definitions
Term | Definition
Cluster | A cluster is defined as a subset of a solar farm Facility with: - the same module types (manufacturer, model and material), if any modules - the same inverter type (manufacturer, model and rating), if any inverters - the same combination and number of modules connected to each inverter, if any inverters - the same actual turbine(s), if any turbines - the same fixed slope and azimuth angles of modules, if fixed - the same tracking algorithm and ranges, if tracking - the same concentrator attributes, if concentrating - geographically close location of all modules / concentrators See definition by technology on corresponding worksheet.
Facility | The entire solar farm
Module | For PV farms, is the individual solar panel
Slope angle | The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
Azimuth angle | The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc)
Cluster definition examples
Example 1 | Solar PV without tracking, one module type and one inverter type for the entire facility, same number of modules connected to each inverter
In this case, the cluster definition is straightforward. There would only need to be one cluster with all the inverters contained in that cluster.
Example 2 | Solar PV without tracking, two module types and one inverter type for the entire facility
The combination of module types must be identical for all inverters in that cluster. All parameters related to modules must be specified for each module type. For example, one cluster has 3000 modules of Type A and 4000 modules of Type B connected to each inverter in the cluster. If other module configurations exist (e.g. 8000 modules of Type A and 2000 modules of Type B), they must be in a different cluster.
Example 3 | Solar PV without tracking, one module type and two inverter types for the entire facility
Two clusters would be specified. The first cluster would relate to the first inverter type, the second cluster would relate to the second inverter type.
Modules/concentrators
Inverter/turbine
Facility
An inverter/turbine is fed by multiple modules or concentrators
A cluster is potentially comprised of multiple inverters/turbines
A facility is potentially comprised of multiple clusters
Cluster

## ECM PV
Solar energy conversion model for non-concentrating PV farms | [6 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
*required parameters in bold | Data type | Units | Valid range | Required | Interval | Value | Description
Static parameters | Parameters that change infrequently or not at all
Solar farm identification
DUID | Descriptive string. MMS DUID | n/a |  | Yes |  |  | DUID of the solar farm to be proposed by the participant. Maximum 8 characters allowed. Example - SYDNSLR. NOTE: DUID to be same as specified in the Registration process.
Facility Name | Descriptive string | n/a |  | Yes |  |  | Name of the Solar farm. To be same as specified in the registration process.
Region | Descriptive string | n/a |  | Yes |  |  | Name of NEM region of the facility. To be same as specified in the registration process.
Solar farm nominal data
Nameplate rating | Scalar decimal number | MW |  | Yes |  |  | This Item corresponds to "Nameplate Rating" in Sections C and I.5 of "Application for Registration as a Generator in the NEM."
Maximum capacity | Scalar Decimal Number | MW |  | Yes |  |  | Maximum generation to which the semi-scheduled generating unit may be dispatched. This definition can be found in sections C, I.4 and I.5 of "Application for Registration as a Generator in the NEM",
Solar farm status
Status of the solar farm | Descriptive string, e.g. "pre-construction" | n/a | {pre-construction, construction, commissioning, operational, decommissioning, decommissioned} | Yes |  |  | Status of the solar farm.
From which date is or will the solar farm be fully operational? | Date | dd/mm/yyyy |  | Yes |  |  | Provide the plan for progressive commissioning of the solar farm with expected dates of commissioning
From which date will the solar farm be first connected to the grid or energised? | Date | dd/mm/yyyy |  | Yes |  |  | Provide the date when the solar farm is expected to commence generation.
Solar farm location and terrain data
Facility latitude | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the collector area
Facility longitude | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the collector area
Facility altitude | Scalar decimal number | metres ASL | (-15,2228) | Yes |  |  | Defined at the centre of the collector area
Facility map | PDF / high resolution image | n/a |  | Yes |  |  | Terrain map file with positions of receivers, strings, measuring devices marked
Facility time zone | Descriptive string, e.g Australia/New South Wales | n/a |  | No |  |  | Facility time zone
Solar farm miscellaneous
Number of clusters | Scalar positive integer | n/a | >0 | Yes |  |  | Number of clusters of the facility, for cross-checking
List of measurement devices (Device ID) | Descriptive string, e.g. a device type and model number eg "TSP-700 Pyranometer" | n/a |  | Yes
Solar farm SCADA to AEMO | [6 empty] | Unless otherwise stated, instantaneous measurements are required. Instantaneous means values updated at least every 4-10 seconds. If only averages are available, maximum 15-second average update is required
Global horizontal irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Yes | 4-10 secs |  | Per cluster Measured using a ISO First class pyranometer
Global inclined irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Yes | 4-10 secs |  | Same orientation of the panel Per cluster Measured using a ISO First class pyranometer
Ambient temperature | Scalar decimal number | ºC | (-50,100) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Wind speed | Scalar decimal number | m/s | >=0 | Yes | 4-10 secs |  | To be representative of the whole solar farm
Wind direction | Scalar decimal number (bearing) | º | (0,360) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Relative humidity | Scalar non-negative decimal number | % | (0,100) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Barometric pressure | Scalar decimal number | hPa | (0,2000) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Module surface temperature | Scalar decimal number | ºC | (-50,100) | Yes | 4-10 secs |  | Per cluster Averaged across all modules in a cluster
Solar farm control system set-point | Scalar non-negative decimal number | MW | >=0 | Yes | 4-10 secs |  | MW set-point applied in the solar farm’s control system to limit (down regulate) its output. At other time when no limit applies, the set-point to be set to above the solar farm’s nameplate rating, but below 250% of it.
Local limit | Scalar non-negative decimal number | MW | >=0 | Yes, unless otherwise agreed by AEMO. | 4-10 secs |  | In MW, the SCADA Local Limit is the lower of plant availability and of the limitation on capacity of connection assets on the export of energy from the solar farm. When implemented in ASEFS1, the SCADA Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO's compliance with clause 3.7B(c)(6) of the Rules), and other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Inverters Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits of less than 5-minute duration may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate rating and the Maximum Capacity of the solar farm.
Active power generation | Scalar non-negative decimal number | MW | >=0 | Yes | 4-10 secs |  | Per facility
Reactive power generation | Scalar non-negative decimal number | MVAr | >=0 | No | 4-10 secs |  | Per facility
Number of inverters available | Scalar non-negative decimal number | n/a | >=0 | Yes | 4-10 secs |  | Per cluster The number of inverters that are available to deliver active power if sufficient sunlight is available
Reduction through soiling | Scalar non-negative decimal number | % | (0,100) | No | 4-10 secs |  | Per cluster The percentage reduction of module production caused by soiling If this parameter is measured at the facility, then it will be requested by AEMO to be provided but is optional.
Actual tracking slope angle | Scalar non-negative decimal number | º | (0,90) | Required for tracking systems only | 4-10 secs |  | Per cluster
Actual tracking azimuth angle | Scalar non-negative decimal number | º | (0,360) | Required for tracking systems only | 4-10 secs |  | Per cluster
Tracking share of modules not on track | Scalar non-negative decimal number | % | >=0 | Required for tracking systems only | 4-10 secs |  | Per cluster
Trackers online | Scalar non-negative integer | n/a | >=0 | Optional for tracking systems only | 4-10 secs |  | Per Cluster
Ends
A cluster is defined as a subset of the Facility with:
- the same inverter type (manufacturer, model and rating)
- the same combination and number of modules connected to each inverter
- the same fixed slope and azimuth angles of modules, if fixed
- the same tracking algorithm and ranges, if tracking
- geographically close location of all modules

## ECM PV Cluster
Solar energy conversion model for non-concentrating PV farms | [6 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
*required parameters in bold | Data type | Units | Valid range | Required | Interval | Value | Description
Cluster | Parameters that apply to a cluster Please copy this sheet into a separate tab for each additional cluster.
Cluster identification
Cluster ID | Scalar | n/a | >0 | Yes |  |  | Unique ID of the cluster in the farm to be provided by the participant. Maximum 10 characters allowed. Example- SYDSLR_CL1. NOTE: to be same as specified in registration process
Cluster Characteristics
Technology type | Descriptive string. E.g. {PV static, PV single axis azimuth tracking, PV single axis slope tracking, PV dual axis tracking} | n/a |  | Yes |  |  | The type of technology used in the cluster including information on tracking.
Cluster centre latitude | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the module area of the cluster
Cluster centre longitude | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the module area of the cluster
Cluster centre altitude | Scalar decimal number | meters | (-15,2228) | Yes |  |  | Defined at the centre of the module area of the cluster
Number of modules in cluster | Scalar number | n/a | >0 | Yes |  |  | The total number of modules in this cluster
Number of inverters | Scalar | n/a | >0 | Yes |  |  | The number of inverters in this cluster
Inverter manufacturer | String |  |  | Yes |  |  | Name of manufacturer of inverters in this cluster
Inverter model ID | String |  |  | Yes |  |  | Model ID for inverters in this cluster
Inverter DC power rating | Scalar non-negative decimal number | kW DC | >0 | Yes |  |  | DC power rating for inverters in this cluster
Inverter AC power rating | Scalar non-negative decimal number | kW AC | >0 | Yes |  |  | AC power rating for inverters in this cluster
Inverter temperature rating | 2-vector (min, max) | min ºC |  | Yes |  |  | Operating temperature range of inverter as specified by manufacturer
|  | max ºC |  | Yes
Inverter response | 2-vector (power, efficiency) | power: kW | >=0 | Yes |  |  | See the inverter response example worksheet
|  | efficiency: % | (0,100) | Yes
Total DC power of modules in cluster | Scalar decimal number | MW |  | Yes |  |  | The total sum DC nameplate rating of all modules in this cluster, used for cross-checking and documenting overprovisioning ratio
Total DC power of inverters in cluster | Scalar decimal number | MW |  | Yes |  |  | The total sum DC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Total AC power of inverters in cluster | Scalar decimal number | MW |  | Yes |  |  | The total sum AC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Tracking slope angle range | 2-vector (min, max) | min degrees | (0,90) | Required for tracking systems only |  |  | Minimum slope angle for clusters with slope tracking of the modules. The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
|  | max degrees |  |  |  |  | Maximum slope angle for clusters with slope tracking of the modules.
Slope tracking direction | String |  |  | Required for tracking systems only |  |  | Direction in which slope tracking is done. Specify "north-south" if panels are tilted in the north/south direction over an east-west axis. Specify "east-west" if panels are tilted from east to west over a north-south axis. For any other angles/cases, specify the compass orientation of the tracking (see "azimuth", perpendicular to axis' compass orientation) and attach additional information on the tracking
Tracking azimuth angle range | 2-vector (min, max) | min degrees | (0,360) | Required for tracking systems only |  |  | Minimum azimuth angle for clusters with azimuth tracking of the modules. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc)
|  | max degrees | (0,360) |  |  |  | Maximum azimuth angle for clusters with azimuth tracking of the modules.
Fixed slope angle | Scalar decimal number | degrees | (0,90) | Required for non-tracking systems |  |  | Fixed slope angle of the modules for clusters without slope tracking. The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
Fixed azimuth angle | Scalar decimal number | degrees | (0,360) | Required for non-tracking systems |  |  | Fixed azimuth angle of the modules for clusters without azimuth tracking of the modules. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc)
Module Type Used In This Cluster | Parameters that apply to a module type used within a cluster (part of cluster definition) Please copy this section of the sheet for each module type used in this cluster, if more than one (see Example 2 of Introduction worksheet)
Module manufacturer | String | n/a |  | Yes |  |  | Manufacturer of PV modules in this cluster
Module model ID | String | n/a |  | Yes |  |  | Model ID for PV modules in this cluster
Module material | String | n/a |  | Yes |  |  | PV material used for all modules in this cluster Material of interest is the substance that is used to convert sunlight to electricity (e.g. monocrystalline silicon, cadmium telluride)
Module DC power rating | Scalar decimal number | W DC |  | Yes |  |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Module surface area | Scalar number | m2 | >0 | Yes |  |  | Surface area of a single module
Module temperature response | 2-vector (temperature, response) | temperature: ºC | (-50,100) | No |  |  | Module temperature response Provide in extra sheet
|  | response: n/a | (0,1) | No |  |  | Alternatively, 0-100%
Module normalised spectral response | 2-vector (wavelength, response) | wavelength: nm | (200,4000) | No |  |  | See the spectral response worksheet
|  | response: n/a | (0,1) | No |  |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation,degradation) | year since installation: n/a | >=0 | No |  |  | Provide in extra sheet
|  | degradation | % | No
Module annual degradation rate | Scalar number | %/year | (0,100) | No |  |  | Fallback if degradation curve is not supplied
Number of modules per inverter | Scalar number | n/a | >0 | Yes |  |  | The number of modules of this type attached to each inverter in this cluster
Inverter | Parameters that apply to an individual inverter Please copy this section of the sheet for each inverter of the cluster.
Inverter ID | Descriptive string, eg INV_1045 | n/a |  | Yes |  |  | Unique ID for this inverter (may be built of cluster ID plus count)
Centre latitude of modules connected to inverter | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the module area of modules connected to this inverter
Centre longitude of modules connected to inverter | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the module area of modules connected to this inverter
Centre altitude of modules connected to inverter | Scalar decimal number | m ASL | (-15,2228) | Yes |  |  | Defined at the centre of the module area of modules connected to this inverter
Ends
A cluster is defined as a subset of the Facility with:
- the same inverter type (manufacturer, model and rating)
- the same combination and number of modules connected to each inverter
- the same fixed slope and azimuth angles of modules, if fixed
- the same tracking algorithm and ranges, if tracking
- geographically close location of all modules

## ECM CPV
Solar energy conversion model for concentrating PV farms | [6 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
*required parameters in bold | Data type | Units | Valid range | Required | Interval | Value | Description
Static parameters | Parameters that change infrequently or not at all
Solar farm identification
DUID | Descriptive string. MMS DUID | n/a |  | Yes |  |  | DUID of the solar farm to be proposed by the participant. Maximum 8 characters allowed. Example - SYDNSLR. NOTE: DUID to be same as specified in the Registration process.
Facility Name | Descriptive string | n/a |  | Yes |  |  | Name of the Solar farm. To be same as specified in the registration process.
Region | Descriptive string | n/a |  | Yes |  |  | Name of NEM region of the facility. To be same as specified in the registration process.
Solar farm nominal data
Nameplate rating | Scalar decimal number | MW |  | Yes |  |  | This Item corresponds to "Nameplate Rating" in Sections C and I.5 of "Application for Registration as a Generator in the NEM."
Maximum capacity | Scalar Decimal Number | MW |  | Yes |  |  | Maximum generation to which the semi-scheduled generating unit may be dispatched. This definition can be found in sections C, I.4 and I.5 of "Application for Registration as a Generator in the NEM",
Solar farm status
Status of the solar farm | Descriptive string, e.g. "pre-construction" | n/a | {pre-construction, construction, commissioning, operational, decommissioning, decommissioned} | Yes |  |  | Status of the solar farm.
From which date is or will the solar farm be fully operational? | Date | dd/mm/yyyy |  | Yes |  |  | Provide the plan for progressive commissioning of the solar farm with expected dates of commissioning
From which date will the solar farm be first connected to the grid or energised? | Date | dd/mm/yyyy |  | Yes |  |  | Provide the date when the solar farm is expected to commence generation.
Solar farm location and terrain data
Facility latitude | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the collector area
Facility longitude | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the collector area
Facility altitude | Scalar decimal number | metres ASL | (-15,2228) | Yes |  |  | Defined at the centre of the collector area
Facility map | PDF / high resolution image | n/a |  | Yes |  |  | Terrain map file with positions of receivers, strings, measuring devices marked
Facility time zone | Descriptive string, e.g Australia/New South Wales | n/a |  | No |  |  | Facility time zone
Solar farm miscellaneous
Number of clusters | Scalar positive integer | n/a | >0 | Yes |  |  | Number of clusters of the facility, for cross-checking
List of measurement devices (Device ID) | Descriptive string, e.g. a device type and model number eg "TSP-700 Pyranometer" | n/a |  | Yes
Solar farm SCADA to AEMO | [6 empty] | Unless otherwise stated, instantaneous measurements are required. Instantaneous means values updated at least every 4-10 seconds. If only averages are available, maximum 15-second average update is required
Global horizontal irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Required | 4-10 secs |  | Per cluster Measured using a ISO First class pyranometer
Global inclined irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Required | 4-10 secs |  | Same orientation as the panel Per cluster Measured using a ISO First class pyranometer
Direct normal irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Required | 4-10 secs |  | Same orientation as the modules Per cluster Measured using a ISO First class pyrheliometer
Ambient temperature | Scalar decimal number | ºC | (-50,100) | Required | 4-10 secs |  | To be representative of the whole solar farm
Wind speed | Scalar decimal number | m/s | >=0 | Required | 4-10 secs |  | To be representative of the whole solar farm
Wind direction | Scalar decimal number (bearing) | º | (0,360) | Required | 4-10 secs |  | To be representative of the whole solar farm
Relative humidity | Scalar non-negative decimal number | % | (0,100) | Required | 4-10 secs |  | To be representative of the whole solar farm
Barometric pressure | Scalar decimal number | hPa | (0,2000) | Required | 4-10 secs |  | To be representative of the whole solar farm
Module surface temperature | Scalar decimal number | ºC | (-50,100) | Required | 4-10 secs |  | Per cluster Averaged across all modules in a cluster
Solar farm control system set-point | Scalar non-negative decimal number | MW | >=0 | Yes | 4-10 secs |  | MW set-point applied in the solar farm’s control system to limit (down regulate) its output. At other time when no limit applies, the set-point to be set to above the solar farm’s nameplate rating, but below 250% of it.
Local limit | Scalar non-negative decimal number | MW | >=0 | Yes, unless otherwise agreed by AEMO. | 4-10 secs |  | In MW, the lower of plant availability and of the limitation on capacity of connection assets on the export of energy from the solar farm. When implemented in ASEFS1, the SCADA Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO's compliance with clause 3.7B(c)(6) of the Rules), and other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Inverters Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits of less than 5-minute duration may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate rating and the Maximum Capacity of the solar farm.
Distribution network limit | Scalar non-negative decimal number | MW | >=0 | No | 4-10 secs |  | In MW, the lowest limit currently applying to the solar farm due to distribution network limitations. This must exclude: - Limits already reflected in the SCADA Local Limit - Limits managed by AEMO through the central dispatch process, including the dispatch level during a semi-dispatch interval The SCADA Distribution Network Limit should not exceed the higher of the nameplate rating and the Maximum Capacity of the wind farm. When allowed by the Rules and implemented in ASEFS1, the lower of the Distribution Network Limit and Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe.
Active power generation | Scalar non-negative decimal number | MW | >=0 | Required | 4-10 secs |  | Per facility
Reactive power generation | Scalar non-negative decimal number | MVAr | >=0 | Optional | 4-10 secs |  | Per facility
Number of inverters available | Scalar non-negative decimal number | n/a | >=0 | Required | 4-10 secs |  | Per cluster The number of inverters that are available to deliver active power if sufficient sunlight is available
Reduction through soiling | Scalar non-negative decimal number | % | (0,100) | Optional | 4-10 secs |  | Per cluster The percentage reduction of module production caused by soiling If this parameter is measured at the facility, then it will be requested by AEMO to be provided but is optional.
Actual tracking slope angle | Scalar non-negative decimal number | º | (0,90) | Required | 4-10 secs |  | Per cluster
Actual tracking azimuth angle | Scalar non-negative decimal number | º | (0,360) | Required | 4-10 secs |  | Per cluster
Tracking share of modules/concentrators not on track | Scalar non-negative decimal number | % | >=0 | Required | 4-10 secs |  | Per cluster
Trackers online | Scalar non-negative integer | n/a | >=0 | Optional | 4-10 secs |  | Per cluster
Ends

## ECM CPV Cluster
Solar energy conversion model for concentrating PV farms | [6 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
*required parameters in bold | Data type | Units | Valid range | Required | Interval | Value | Description
Cluster | Parameters that apply to a cluster Please copy this section of the sheet for each cluster.
Cluster identification
Cluster ID | Scalar | n/a | >0 | Yes |  |  | Unique ID of the cluster in the farm to be provided by the participant. Maximum 10 characters allowed. Example- SYDSLR_CL1. NOTE: to be same as specified in registration process
Cluster Characteristics
Technology type | Descriptive string. | n/a |  | Yes |  |  | The type of technology used in the cluster including information on tracking.
Cluster centre latitude | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre longitude | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre altitude | Scalar decimal number | meters | (-15,2228) | Yes |  |  | Defined at the centre of the module/concentrator area of the cluster
Number of modules in cluster | Scalar number | n/a | >0 | Yes |  |  | Total number of modules in this cluster
Module manufacturer | String | n/a |  | Yes |  |  | Manufacturer of PV modules in this cluster
Module model ID | String | n/a |  | Yes |  |  | Model ID for PV modules in this cluster
Module material | String | n/a |  | Yes |  |  | PV material used for all modules in this cluster Material of interest is the substance that is used to convert sunlight to electricity (e.g. monocrystalline silicon, cadmium telluride)
Module DC power rating | Scalar decimal number | W DC |  | Yes |  |  | The power rating for each single module in this cluster at standard test conditions. Standard test conditions are defined as irradiance of 1000 W/m2 at AM 1.5 solar spectrum and temperature 25 ± 2 °C
Total DC power of modules in cluster | Scalar decimal number | MW |  | Yes |  |  | The total sum DC nameplate rating of all modules in this cluster, used for cross-checking and documenting overprovisioning ratio
Module surface area | Scalar number | m2 | >0 | Yes |  |  | Surface area of a single receiver module
Module temperature response | 2-vector (temperature, response) | temperature: ºC | (-50,100) | No |  |  | Module temperature response (provide in extra sheet)
|  | response: n/a | (0,1) | No |  |  | Alternatively, 0-100%
Module normalised spectral response | 2-vector (wavelength, response) | wavelength: nm | (200,4000) | No |  |  | See the spectral response worksheet
|  | response: n/a | (0,1) | No |  |  | Alternatively, 0-100%
Module degradation curve | 2-vector (year since installation,degradation) | year since installation: n/a | >=0 | No |  |  | Provide in extra sheet
|  | degradation | % | No
Module annual degradation rate | Scalar number | %/year | (0,100) | No |  |  | Fallback if degradation curve is not supplied
Number of modules in cluster | Scalar number | n/a | >0 | Yes |  |  | The total number of modules in this cluster
Number of inverters | Scalar | n/a | >0 | Yes |  |  | The number of inverters in this cluster
Inverter manufacturer | String |  |  | Yes |  |  | Manufacturer of inverters in this cluster
Inverter model ID | String |  |  | Yes |  |  | Model ID for inverters in this cluster
Inverter DC power rating | Scalar non-negative decimal number | kW DC | >0 | Yes |  |  | DC power rating for inverters in this cluster
Total DC power of inverters in cluster | Scalar decimal number | MW |  | Yes |  |  | The total sum DC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Inverter AC power rating | Scalar non-negative decimal number | kW AC | >0 | Yes |  |  | AC power rating for inverters in this cluster
Total AC power of inverters in cluster | Scalar decimal number | MW |  | Yes |  |  | The total sum AC nameplate rating of all inverters in this cluster, used for cross-checking and documenting overprovisioning ratio
Inverter temperature rating | 2-vector (min, max) | min ºC |  | Yes |  |  | Operating temperature range of inverter as specified by manufacturer
max ºC
Inverter response | 2-vector (power, efficiency) | power: kW | >=0 | Yes |  |  | See inverter response example worksheet.
|  | efficiency: % | (0,100)
Number of modules per inverter | Scalar number | n/a | >0 | Yes |  |  | The number of modules attached to each inverter
Number of concentrators per inverter | Scalar number | n/a | >0 | Yes |  |  | The number of concentrators attached to each inverter
Number of concentrators in cluster | Scalar number | n/a | >0 | Yes |  |  | Total number of concentrators in this cluster
Concentrator manufacturer | String | n/a |  | Yes |  |  | Manufacturer of concentrators in this cluster
Concentrator model ID | String | n/a |  | Yes |  |  | Model ID for concentrators in this cluster
Concentrator technology | Descriptive string. E.g. {dish, trough, fresnel} | n/a |  | Yes |  |  | Technology of the concentrator
Concentrator concentrating factor | Scalar decimal number | n/a |  | Yes |  |  | Concentrating factor of concentrator
Concentrator aperture width | Scalar decimal number | meters |  | Yes |  |  | Aperture width of concentrator
Concentrator receiver length | Scalar decimal number | meters |  | Yes |  |  | Receiver length of concentrator
Concentrator aperture area | Scalar decimal number | m2 |  | Yes |  |  | Aperture area of concentrator
Tracking slope angle range | 2-vector (min, max) | min degrees | (0,90) | Required for tracking systems only |  |  | Minimum slope angle The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
|  | max degrees | (0,90) |  |  |  | Maximum slope angle.
Slope tracking direction | String |  |  | Required for tracking systems only |  |  | Direction in which slope tracking is done. Specify "north-south" if panels are tilted in the north/south direction over an east-west axis. Specify "east-west" if panels are tilted from east to west over a north-south axis. For any other angles/cases, specify the compass orientation of the tracking (see "azimuth", perpendicular to axis' compass orientation) and attach additional information on the tracking
Tracking azimuth angle range | 2-vector (min, max) | min degrees | (0,360) | Required for tracking systems only |  |  | Minimum azimuth angle. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc)
|  | max degrees | (0,360) |  |  |  | Maximum azimuth angle.
Inverter | Parameters that apply to an individual inverter Please copy this section of the sheet for each inverter in the cluster
Inverter ID | Descriptive string, eg INV_1045 | n/a |  | Yes |  |  | Unique ID for this inverter (may be built of cluster ID plus count)
Centre latitude of modules connected to inverter | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the module / concentrator area of modules connected to this inverter
Centre longitude of modules connected to inverter | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the module / concentrator area of modules connected to this inverter
Centre altitude of modules connected to inverter | Scalar decimal number | m ASL | (-15,2228) | Yes |  |  | Defined at the centre of the module / concentrator area of modules connected to this inverter
Ends
A cluster is defined as a subset of the Facility with:
- the same module type (manufacturer, model and material)
- the same inverter type (manufacturer, model and rating)
- the same number of modules connected to each inverter
- the same tracking algorithm and ranges
- the same concentrator attributes
- geographically close location of all modules

## ECM CST
Solar energy conversion model for concentrating solar-thermal farms | [6 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
*required parameters in bold | Data type | Units | Valid range | Required | Interval | Value | Description
Static parameters | Parameters that change infrequently or not at all
Solar farm identification
DUID | Descriptive string. MMS DUID | n/a |  | Yes |  |  | DUID of the solar farm to be proposed by the participant. Maximum 8 characters allowed. Example - SYDNSLR. NOTE: DUID to be same as specified in the Registration process.
Facility Name | Descriptive string | n/a |  | Yes |  |  | Name of the Solar farm. To be same as specified in the registration process.
Region | Descriptive string | n/a |  | Yes |  |  | Name of NEM region of the facility. To be same as specified in the registration process.
Solar farm nominal data
Nameplate rating | Scalar decimal number | MW |  | Yes |  |  | This Item corresponds to "Nameplate Rating" in Sections C and I.5 of "Application for Registration as a Generator in the NEM."
Maximum capacity | Scalar Decimal Number | MW |  | Yes |  |  | Maximum generation to which the semi-scheduled generating unit may be dispatched. This definition can be found in sections C, I.4 and I.5 of "Application for Registration as a Generator in the NEM",
Solar farm status
Status of the solar farm | Descriptive string, e.g. "pre-construction" | n/a | {pre-construction, construction, commissioning, operational, decommissioning, decommissioned} | Yes |  |  | Status of the solar farm.
From which date is or will the solar farm be fully operational? | Date | dd/mm/yyyy |  | Yes |  |  | Provide the plan for progressive commissioning of the solar farm with expected dates of commissioning
From which date will the solar farm be first connected to the grid or energised? | Date | dd/mm/yyyy |  | Yes |  |  | Provide the date when the solar farm is expected to commence generation.
Solar farm location and terrain data
Facility latitude | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the collector area
Facility longitude | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the collector area
Facility altitude | Scalar decimal number | metres ASL | (-15,2228) | Yes |  |  | Defined at the centre of the collector area
Facility map | PDF / high resolution image | n/a |  | Yes |  |  | Terrain map file with positions of receivers, strings, measuring devices marked
Facility time zone | Descriptive string, e.g Australia/New South Wales | n/a |  | No |  |  | Facility time zone
Solar farm miscellaneous
Number of clusters | Scalar positive integer | n/a | >0 | Yes |  |  | Number of clusters of the facility, for cross-checking
List of measurement devices (Device ID) | Descriptive string, e.g. a device type and model number eg "TSP-700 Pyranometer" | n/a |  | Yes
Solar farm SCADA to AEMO | [6 empty] | Unless otherwise stated, instantaneous measurements are required. Instantaneous means values updated at least every 4-10 seconds. If only averages are available, maximum 15-second average update is required
Global horizontal irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Yes | 4-10 secs |  | Per cluster Measured using a ISO First class pyranometer
Global inclined irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Yes | 4-10 secs |  | Same orientation of the panel Per cluster Measured using a ISO First class pyranometer
Direct normal irradiance | Scalar non-negative decimal number | W/m2 | (0,1415) | Yes | 4-10 secs |  | Same orientation as the modules Per cluster Measured using a ISO First class pyrheliometer
Ambient temperature | Scalar decimal number | ºC | (-50,100) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Wind speed | Scalar decimal number | m/s | >=0 | Yes | 4-10 secs |  | To be representative of the whole solar farm
Wind direction | Scalar decimal number (bearing) | º | (0,360) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Relative humidity | Scalar non-negative decimal number | % | (0,100) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Barometric pressure | Scalar decimal number | hPa | (0,2000) | Yes | 4-10 secs |  | To be representative of the whole solar farm
Module receiver surface temperature | Scalar decimal number | ºC | (-50,100) | Yes | 4-10 secs |  | Per cluster Averaged across all receivers in a cluster
Solar farm control system set-point | Scalar non-negative decimal number | MW | >=0 | Yes | 4-10 secs |  | MW set-point applied in the solar farm’s control system to limit (down regulate) its output. At other time when no limit applies, the set-point to be set to above the solar farm’s nameplate rating, but below 250% of it.
Local limit | Scalar non-negative decimal number | MW | >=0 | Yes, unless otherwise agreed by AEMO. | 4-10 secs |  | In MW, the lower of plant availability and of the limitation on capacity of connection assets on the export of energy from the solar farm. When implemented in ASEFS1, the SCADA Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO's compliance with clause 3.7B(c)(6) of the Rules), and other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Inverters Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits of less than 5-minute duration may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate rating and the Maximum Capacity of the solar farm.
Distribution network limit | Scalar non-negative decimal number | MW | >=0 | No | 4-10 secs |  | In MW, the lowest limit currently applying to the solar farm due to distribution network limitations. This must exclude: - Limits already reflected in the SCADA Local Limit - Limits managed by AEMO through the central dispatch process, including the dispatch level during a semi-dispatch interval The SCADA Distribution Network Limit should not exceed the higher of the nameplate rating and the Maximum Capacity of the wind farm. When allowed by the Rules and implemented in ASEFS1, the lower of the Distribution Network Limit and Local Limit is used to cap the UIGF for the solar farm in the dispatch timeframe.
Active power generation | Scalar non-negative decimal number | MW | >=0 | Yes | 4-10 secs |  | Per facility
Reactive power generation | Scalar non-negative decimal number | MVAr | >=0 | No | 4-10 secs |  | Per facility
Number of turbines available | Scalar non-negative decimal number | n/a | >=0 | Yes | 4-10 secs |  | Per cluster The number of turbines that are available to deliver active power if sufficient sunlight is available
Reduction through soiling | Scalar non-negative decimal number | % | (0,100) | Yes | 4-10 secs |  | Per cluster The percentage reduction of module production caused by soiling
Actual tracking slope angle | Scalar non-negative decimal number | º | (0,90) | Yes | 4-10 secs |  | Per cluster
Actual tracking azimuth angle | Scalar non-negative decimal number | º | (0,360) | Yes | 4-10 secs |  | Per cluster
Tracking share of concetrators not on track | Scalar non-negative decimal number | % | >=0 | Yes | 4-10 secs |  | Per cluster
Trackers online | Scalar non-negative integer | n/a | >=0 | No | 4-10 secs |  | Per cluster
Ends

## ECM CST Cluster
Solar energy conversion model for concentrating solar-thermal farms | [6 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
*required parameters in bold | Data type | Units | Valid range | Required | Interval | Value | Description
Static parameters | Parameters that change infrequently or not at all
Cluster | Parameters that apply to a cluster Please copy this section of the sheet for each cluster
Cluster identification
Cluster ID | Scalar | n/a | >0 | Yes |  |  | Unique ID of the cluster in the farm to be provided by the participant. Maximum 10 characters allowed. Example- SYDSLR_CL1. NOTE: to be same as specified in registration process
Cluster Characteristics
Technology type | Data type: Descriptive string | n/a |  | Yes |  |  | The type of solar-thermal technology used in the cluster
Cluster centre latitude | Scalar decimal number | Decimal degrees | (-90,90) | Yes |  |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre longitude | Scalar decimal number | Decimal degrees | (-180,180) | Yes |  |  | Defined at the centre of the module/concentrator area of the cluster
Cluster centre altitude | Scalar decimal number | meters | (-15,2228) | Yes |  |  | Defined at the centre of the module/concentrator area of the cluster
Turbine manufacturer | String | n/a |  | Yes |  |  | Manufacturer of turbine(s) in this cluster
Turbine model ID | String | n/a |  | Yes |  |  | Model ID for turbine(s) in this cluster
Turbine AC power rating | Scalar decimal number | W DC | >0 | Yes |  |  | The power rating for each single turbine in this cluster
Turbine response | 2-vector (irradiance, power) | irradiance: W/m2 | >=0 | Yes |  |  | Concentrator and turbine response to irraditation (provide in extra sheet)
|  | power: kW | (0,100) |  |  |  | Alternatively, 0-100%
Number of steam turbines in cluster | Scalar | n/a | >0 | Yes |  |  | Total number of turbines in this cluster
Concentrator manufacturer | String | n/a |  | Yes |  |  | Manufacturer of concentrators in this cluster
Concentrator model ID | String | n/a |  | Yes |  |  | Model ID for concentrators in this cluster
Concentrator technology | Descriptive string. E.g. {dish, trough, fresnel} | n/a |  | Yes |  |  | Technology of the concentrator
Concentrator concentrating factor | Scalar decimal number | n/a |  | Yes |  |  | Concentrating factor of concentrator
Concentrator aperture width | Scalar decimal number | meters |  | Yes |  |  | Aperture width of concentrator
Concentrator receiver length | Scalar decimal number | meters |  | Yes |  |  | Receiver length of concentrator
Concentrator aperture area | Scalar decimal number | square meters |  | Yes |  |  | Aperture area of concentrator
Concentrating factor | Scalar decimal number | n/a |  | Yes
Operating temperature | 2-vector (min, max) | min ºC |  | Yes |  |  | Operational temperature range
max ºC
Receiver diameter | Scalar decimal number | millimeters |  | Yes |  |  | Receiver diameter
Number of concentrators per turbine | Scalar number | n/a | >0 | Yes |  |  | Number of concentrators per turbine
Receiver rows distance | Scalar decimal number | meters |  | Yes
Optical efficiency of mirror without soiling | Scalar decimal number | n/a | <1 | Yes
Absorbance of receiver | Scalar decimal number | n/a | <1 | Yes
Emissivity of receiver | Scalar decimal number | n/a | <1 | Yes
Heat transfer coefficient of receiver | Scalar decimal number | W/m2/K |  | Yes
Heat transfer collection pipes | Scalar decimal number | W/m2/K |  | Yes
Rated power steam turbine | Scalar decimal number | kW |  | Yes
Steam turbine efficiency | 2-vector (efficiency, power) | Efficiency: % | <1 | Yes
power: kW
Tracking slope angle range | 2-vector (min, max) | min degrees | (0,90) | Required for tracking systems only |  |  | Minimum slope angle. The slope angle between the collector plane and the horizontal surface which varies between 0° for a horizontal plane and 90° for a vertical plane.
|  | max degrees | (0,90) |  |  |  | Maximum slope angle
Slope tracking direction | String |  |  | Required for tracking systems only |  |  | Direction in which slope tracking is done. Specify "north-south" if panels are tilted in the north/south direction over an east-west axis. Specify "east-west" if panels are tilted from east to west over a north-south axis. For any other angles/cases, specify the compass orientation of the tracking (see "azimuth", perpendicular to axis' compass orientation) and attach additional information on the tracking
Tracking azimuth angle range | 2-vector (min, max) | min degrees | (0,360) | Required for tracking systems only |  |  | Minimum azimuth angle. The surface azimuth angle ° as the deviation of the normal vector of the plane from the local meridian. Degrees counted clockwise from N where its value is 0° (thus for E it is 90°, for S it is 180° etc)
|  | max degrees | (0,360) |  |  |  | Maximum azimuth angle.
Ends
A cluster is defined as a subset of the facility with:
- the same actual turbine(s)
- the same tracking algorithm and ranges
- the same concentrator attributes
- geographically close location of all modules

## Spectral response example
Spectral response | Values outside the provided range are assumed to be zero
Wavelength (nm) | Response
350 | 0.03
360 | 0.033
370 | 0.036
380 | 0.039
390 | 0.042
400 | 0.045
410 | 0.048
420 | 0.051
430 | 0.054
440 | 0.057
450 | 0.063
460 | 0.07
470 | 0.076
480 | 0.088
490 | 0.1
500 | 0.2
510 | 0.3
520 | 0.4
530 | 0.5
540 | 0.6
550 | 0.7
560 | 0.8
570 | 0.82
580 | 0.84
590 | 0.85
600 | 0.846
610 | 0.842
620 | 0.838
630 | 0.834
640 | 0.83
650 | 0.826
660 | 0.822
670 | 0.818
680 | 0.814
690 | 0.81
700 | 0.806
710 | 0.802
720 | 0.798
730 | 0.794
740 | 0.79
750 | 0.786
760 | 0.782
770 | 0.778
780 | 0.774
790 | 0.77
800 | 0.766
810 | 0.762
820 | 0.758
830 | 0.754
840 | 0.75
850 | 0.6
860 | 0.45
870 | 0.3
880 | 0.15
890 | 0
900 | 0
910 | 0
920 | 0
930 | 0
940 | 0
950 | 0
960 | 0
970 | 0
980 | 0
990 | 0
1000 | 0

## Inverter response example
Inverter efficiency response |  | Values outside the provided range are assumed to be zero
Power (kW) | Response
10 | 0.3
20 | 0.5
30 | 0.8
40 | 0.95
50 | 0.979
60 | 0.9795
70 | 0.98
80 | 0.9805
90 | 0.981
100 | 0.9815
110 | 0.982
120 | 0.9825
130 | 0.983
140 | 0.9835
150 | 0.984
160 | 0.9845
170 | 0.985
180 | 0.9855
190 | 0.986
200 | 0.9865
210 | 0.986
220 | 0.9855
230 | 0.985
240 | 0.9845
250 | 0.984
260 | 0.9835
270 | 0.983
280 | 0.9825
290 | 0.982
300 | 0.9815
310 | 0.981
320 | 0.9805
330 | 0.98
340 | 0.979
350 | 0.978
360 | 0.977
370 | 0.976
380 | 0.975
390 | 0.974
400 | 0.973
410 | 0.972
420 | 0.971
430 | 0.97
440 | 0.969
450 | 0.968
460 | 0.967
470 | 0.966
480 | 0.965
490 | 0.964
500 | 0.963
510 | 0.962
520 | 0.961
530 | 0.959
540 | 0.957
550 | 0.955
560 | 0.953
570 | 0.951
580 | 0.949
590 | 0.947
600 | 0.945
610 | 0.943
620 | 0.941
630 | 0.939
640 | 0.937
650 | 0.935
660 | 0.933