## South Australia Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer at http://www.aemo.com.au/Electricity/Planning/Related-Information/Generation-Information
South Australia Summary
Changes since last update
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around March – May 2016.
New Development: Leigh Creek Energy Project, Lincoln Gap Wind Farm, Mount Hill, Palmer Wind Farm, Pelican Point S2, Port Augusta Renewable Energy Park, Stony Gap, Waterloo, Willogoleche, Woakwine Wind Farm, Kingfisher solar storage project, Roxby Downs Solar Farm, Yorke Penninsula Biomass Energy, Infratech’s floating PV plant are added.
Generation Withdrawals
Withdrawn
Pelican Point Power Station: Pelican Point Power Limited advised that the station capacity has been reduced to half from 1 April 2015 (to 239 MW), and will be reduced to 0 MW for winter 2016.
Announced Withdrawals (i.e. Mothballed, Seasonal Shut down etc.)
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around March – May 2016.
Playford B Power Station: Alinta Energy advises that Playford B Power Station (240 MW) is planned to retire around March - May 2016.
Torrens Island Power Station A: AGL Energy advises that Torrens Island Power Station A (480 MW) is to be taken out of service in 2017, subject to review if market conditions change materially.
Committed projects
Coal, CCGT, OCGT, Gas other, Water, Biomass, Geo-thermal, Other : None to report.
Wind: HWF 1 Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Proposed Projects
Please refer to information presented in the worksheet titled 'New Developments'.
Plant Limitations
Pelican Point Power Station: Pelican Point Power Limited advises Pelican Point Power Station’s available capacity has been reduced to 0 MW (-239 MW) in winter 2016.
Playford B Power Station: Playford B Power Station's available capacity has been reduced to 0 MW.
South Australia existing and potential new developments by generation type (MW)

## Change Log
South Australia Change Log
Lists all key updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Snowtown S2: TrustPower advises that the Snowtown 2 project is now in a Committed status. Snowtown Stage 2 project will consist of two separately
metered wind farms, Snowtown 2 North (144 MW) and Snowtown 2 South (126 MW), sharing a single transmission line owned by TrustPower.
Publication Date: | 2013-06-30
Playford B Power Station: Alinta energy advises that Playford B power station will be available with a recall time of around 90 days.
Alinta Energy have also revised the output from last year's in summer and winter from 200 MW to 180 MW (-20 MW) due to Turbine 2 being out of service.
However should AEMO require it, Turbine 2 can be brought back into service, taking the longer-term availability of Playford B Power Station up to 200 MW.
Hallett 4 North Brown Hill: AGL advises that Hallett 4 North Brown Hill's available capacity has been revised from 81.9 MW to 99.2 MW (+17.3 MW) in summer,
due to de-rating applied to all Suzlon S88/S97 machines.
Hallett Stage 1 Brown Hill: AGL advises that Hallett Stage 1 Brown Hill's available capacity has been revised from 58.5 MW to 70.9 MW (+12.4 MW) in summer,
due to de-rating applied to all Suzlon S88/S97 machines.
Publication Date: | 2013-11-15
Palmer Wind Farm: TrustPower Australia advises that Palmer Wind Farm (up to 390 MW) has been newly announced. At this stage there has been no advice on construction and commissioning dates.
Port Macdonnell: Oceanlinx Limited advises that the status of the Port Macdonnell (1 MW) wave energy project is now Committed, with full commissioning in December 2013.
Publication Date: | 2014-02-28
Port Macdonnell: Oceanlinx Limited advises that the Port Macdonnell (1 MW) wave energy project commissioning date was revised to March 2014.
Publication Date: | 2014-05-30
Port Macdonnell: Oceanlinx Limited advises that the future of the Port Macdonnell (1 MW) wave energy project is uncertain and rests with company receivers. This project remains as a committed project with a commissioning date to be advised.
Publication Date: | 2014-08-07
Paralana Project: Pertatherm Limited advises that Paralana project capacity has been revised to 3.5 MW.
Paralana Stage 2: Pertatherm Limited advises that Paralana Stage 2 capacity has been revised to 3.5 MW.
Publication Date: | 2014-12-10
Northern Power Station: Alinta Energy advises that Northern Power Station Returned back to normal service in October 2014.
Snowtown S2: TrustPower advises that the Snowtown 2 wind farm (270 MW) project is now completed and in full commercial operation since November 2014.
Publication Date: | 2015-04-15
Pelican Point Power Station: Pelican Point Power Limited advises that Pelican Point Power Station is to reduce the stations capacity to half from 1 April 2015 with unit 2 only being available on a 48 hour recall.
Torrens Island Power Station A: AGL Energy advises that Torrens Island Power Station is to be taken out of service in 2017.
Hornsdale Wind Farm (Stage 1): Hornsdale Wind Farm Pty Ltd advises construction to start in October 2015 and full commercial operation expected in November 2017.
Publication Date: | 2015-08-13
Northern Power Station: Alinta Energy advised in June 2015 that Northern Power Station would retire by March 2018 at the latest, but not before March 2016. In late July Alinta Energy advised that Northern Power Station will retire by March 2017.
Playford B Power Station: Alinta energy advises that Playford B power station (240 MW) will retire by April 2017.
Publication Date: | 2015-10-23
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around 31 March 2016.
Playford B Power Station: Alinta Energy advises that Playford B Power Station (240 MW) is planned to cease generation around 31 March 2016.
Pelican Point Power Station: Pelican Point Power Limited advises Pelican Point Power Station’s available capacity has been reduced to 0 MW (-239 MW) in winter 2016 given the current dynamics and outlook in the electricity and gas markets.
Hornsdale Wind Farm (Stage 1): Hornsdale Wind Farm Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Port Augusta Renewable Energy Park: DP Energy advises of the Port Augusta Renewable Energy Park wind and solar project totalling 375 MW.
Point Paterson Project: Acquasol Infrastructure Pty Ltd advises that the proposed Point Paterson Projects has been put on hold.
Publication Date: | 2016-03-03
Hornsdale Wind Farm (Stage 1): HWF 1 Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around March – May 2016.
New Development: Leigh Creek Energy Project, Lincoln Gap Wind Farm, Mount Hill, Palmer Wind Farm, Pelican Point S2, Port Augusta Renewable Energy Park, Stony Gap, Waterloo, Willogoleche, Woakwine Wind Farm, Kingfisher solar storage project, Roxby Downs Solar Farm, Yorke Penninsula Biomass Energy, Infratech’s floating PV plant, Epuron Uluru PV plant are added
Publication Date: | 2016-04-15
Hornsdale Wind Farm (Stage 1): HWF 1 Pty Ltd advises that Stage 1 of Hornsdale Wind Farm (102.4 MW) is a committed project. Full commercial operation is expected in November 2016.
Northern Power Station: Alinta Energy advises that Northern Power Station (546 MW) is planned to cease generation around March – May 2016.
Playford B Power Station: Alinta Energy advises that Playford B Power Station (240 MW) is planned to will retire around March - May 2016.
New Development: Leigh Creek Energy Project, Lincoln Gap Wind Farm, Mount Hill, Palmer Wind Farm, Pelican Point S2, Port Augusta Renewable Energy Park, Stony Gap, Waterloo, Willogoleche, Woakwine Wind Farm, Kingfisher solar storage project, Roxby Downs Solar Farm, Yorke Penninsula Biomass Energy, Infratech’s floating PV plant, are added.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Nameplate Capacity (MW) | Technology Type | Fuel Type | Dispatch Type | Service Status
Clements Gap | Pacific Hydro Clements Gap Pty Ltd | 27 x 2.1 | 56.7 | Wind - Onshore | Wind | SS | In Service
Dry Creek GT | Synergen Power Pty Ltd | 3 x 52 | 156 | OCGT | Natural Gas Pipeline | S | In Service
Hallett 4 North Brown Hill | Brown Hill North Pty Ltd | 63 x 2.1 | 132.3 | Wind - Onshore | Wind | SS | In Service
Hallett 5 The Bluff WF | Eurus Energy | 25 x 2.1 | 52.5 | Wind - Onshore | Wind | SS | In Service
Hallett GT | EnergyAustralia | 2 x 24.8 1 x 27.5 2 x 17.3 3 x 17 4 x 16.4 | 228.3 | OCGT | Natural Gas Pipeline | S | In Service
Hallett Stage 1 Brown Hill | Palisade Investment Partner Limited | 45 x 2.1 | 94.5 | Wind - Onshore | Wind | SS | In Service
Hallett Stage 2 Hallett Hill | Infrastructure Capital Group Limited | 34 x 2.1 | 71.4 | Wind - Onshore | Wind | SS | In Service
Ladbroke Grove | Origin Energy Power Limited | 2 x 40 | 80 | OCGT | Natural Gas Pipeline | S | In Service
Lake Bonney 2 Wind Farm | Lake Bonney Wind Power Pty Ltd | 53 x 3 | 159 | Wind - Onshore | Wind | SS | In Service
Lake Bonney 3 Wind Farm | Lake Bonney Wind Power Pty Ltd | 13 x 3 | 39 | Wind - Onshore | Wind | SS | In Service
Lonsdale | Infratil Energy Australia Pty Ltd | 1 x 20.7 | 20.7 | Compression Reciprocating Engine | Diesel | S | In Service
Mintaro GT | Synergen Power Pty Ltd | 1 x 90 | 90 | OCGT | Natural Gas Pipeline | S | In Service
Northern | Flinders Operating Services Pty Ltd | 2 x 273 | 546 | Steam Sub Critical | Brown Coal | S | Announced Withdrawal
Osborne | Osborne Cogeneration Pty Ltd | 1 x 118 1 x 62 | 180 | CCGT | Natural Gas Pipeline | S | In Service
Pelican Point* | Pelican Point Power Limited | 2 x 239 | 239 | CCGT | Natural Gas Pipeline | S | Half Capacity In Service
Playford B | Flinders Operating Services Pty Ltd | 4 x 60 | 240 | Steam Sub Critical | Brown Coal | S | Announced Withdrawal
Port Lincoln GT | Synergen Power Pty Ltd | 2 x 25 1 x 23.5 | 73.5 | OCGT | Diesel | S | In Service
Portt Stanvac A | Infratil Energy Australia Pty Ltd | 1x28.8 | 28.8 | Compression Reciprocating Engine | Diesel | S | In Service
Portt Stanvac B | Infratil Energy Australia Pty Ltd | 1x28.8 | 28.8 | Compression Reciprocating Engine | Diesel | S | In Service
Quarantine | Origin Energy Power Limited | 4 x 24 1 x 128 | 224 | OCGT | Natural Gas Pipeline | S | In Service
Snowtown | Snowtown Wind Farm Pty Ltd | 47 x 2.1 | 98.7 | Wind - Onshore | Wind | SS | In Service
Snowtown S2 North | Snowtown Wind Farm Pty Ltd | 48 x 3 | 144 | Wind - Onshore | Wind | SS | In Service
Snowtown S2 South | Snowtown Wind Farm Pty Ltd | 42 x 3 | 126 | Wind - Onshore | Wind | SS | In Service
Snuggery | Synergen Power Pty Ltd | 3 x 21 | 63 | OCGT | Diesel | S | In Service
Torrens Island A | AGL Energy | 4 x 120 | 480 | Steam Sub Critical | Natural Gas Pipeline | S | Announced Withdrawal
Torrens Island B | AGL Energy | 4 x 200 | 800 | Steam Sub Critical | Natural Gas Pipeline | S | In Service
Waterloo | Waterloo Windfarm Pty Ltd | 37 x 3 | 111 | Wind - Onshore | Wind | SS | In Service
Committed Projects
Hornsdale Wind Farm Stage 1 | HWF 1 Pty Ltd | 102.4 | 102.4 | Wind - Onshore | Wind | SS | Committed
Total |  |  | 4665.6
*Pelican Point Power Station: Pelican Point Power Limited advised that the station capacity has been reduced to half from 1 April 2015 (to 239 MW), and will be reduced to 0 MW for winter 2016.

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – South Australia (MW)
Power Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | -25 | S
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Dry Creek GT | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | S
Hallett 4 North Brown Hill | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | SS
Hallett 5 The Bluff WF | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | SS
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Hallett Stage 1 Brown Hill | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | SS
Hallett Stage 2 Hallett Hill | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | SS
Ladbroke Grove | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Lake Bonney 2 Wind Farm | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | SS
Lake Bonney 3 Wind Farm | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | SS
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Northern | 546 | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Osborne | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | S
Pelican Point | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | S
Playford B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Port Lincoln GT | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | S
Portt Stanvac A | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Portt Stanvac B | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Quarantine | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | S
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 North | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Snuggery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Torrens Island A | 480 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Torrens Island B | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | S
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed Projects
Hornsdale Wind Farm | 0 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | SS
Total | 3996.7 | 4099.1 | 3073.1 | 3073.1 | 3073.1 | 3073.1 | 3073.1 | 3073.1 | 3073.1 | 3073.1
The table above lists the latest summer capacities for South Australian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2014–15 these figures are 9.9% of the installed capacity during summer, and 6.9% during winter, based on the contribution factors published by AEMO in the 2015 NEM Historical Market Information Report.
The two tables below have been included to better represent supply availability in South Australia, by taking into account the firm contribution by wind. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled wind generation for the summer period. The total refers to the maximum amount that the wind farms can generate at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation – South Australia (MW)
Power Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | -25 | S
Dry Creek GT | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | S
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Ladbroke Grove | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Northern | 546 | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Osborne | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | S
Pelican Point | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | S
Playford B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Port Lincoln GT | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | S
Portt Stanvac A | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Portt Stanvac B | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Quarantine | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 186 | S
Snuggery | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Torrens Island A | 480 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Torrens Island B | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | S
Firm Wind Capacity | 96.4656 | 106.6032 | 106.6032 | 106.6032 | 106.6032 | 106.6032 | 106.6032 | 106.6032 | 106.6032 | 106.6032 | SS
Total | 3118.7656 | 3128.9032 | 2102.9032 | 2102.9032 | 2102.9032 | 2102.9032 | 2102.9032 | 2102.9032 | 2102.9032 | 2102.9032
Summer aggregate available semi-scheduled generation
Power Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | -25 | S
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Hallett 4 North Brown Hill | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | 92.2 | SS
Hallett 5 The Bluff WF | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | 39.4 | SS
Hallett Stage 1 Brown Hill | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | 70.9 | SS
Hallett Stage 2 Hallett Hill | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | 53.5 | SS
Lake Bonney 2 Wind Farm | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | SS
Lake Bonney 3 Wind Farm | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | SS
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 North | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed Projects
Hornsdale Wind Farm | 0 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | SS
Total | 974.4 | 1076.8 | 1076.8 | 1076.8 | 1076.8 | 1076.8 | 1076.8 | 1076.8 | 1076.8 | 1076.8

## Winter Scheduled Capacities
Winter aggregate scheduled and semi-scheduled generation – South Australia (MW)
Project Station | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Dispatch Type
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Dry Creek GT | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | S
Hallett 4 North Brown Hill | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | SS
Hallett 5 The Bluff WF | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | SS
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Hallett Stage 1 Brown Hill | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | SS
Hallett Stage 2 Hallett Hill | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | SS
Ladbroke Grove | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Northern | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Osborne | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | S
Pelican Point | 0 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | S
Playford B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Port Lincoln GT | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | S
Portt Stanvac A | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Portt Stanvac B | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Quarantine | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | S
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 North | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Snuggery | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Torrens Island A | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Torrens Island B | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | S
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed Projects
Hornsdale Wind Farm | 0 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | SS
Total | 3503.4 | 3362.8 | 3362.8 | 3362.8 | 3362.8 | 3362.8 | 3362.8 | 3362.8 | 3362.8 | 3362.8
The table above lists the latest winter capacities for South Australian generation.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2014–15 these figures are 9.9% of the installed capacity during summer, and 6.9% during winter, based on the contribution factors published by AEMO in the 2015 NEM Historical Market Information Report.
The two tables below have been included to better represent supply availability in South Australia, by taking into account the firm contribution by wind. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled wind generation for the winter period. The total refers to the maximum amount that the wind farms can generate at the winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation – South Australia (MW)
Project Station | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Dispatch Type
Dry Creek GT | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | S
Hallett GT | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | S
Ladbroke Grove | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Lonsdale | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | 20.7 | S
Mintaro GT | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Northern | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Osborne | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | S
Pelican Point | 0 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | S
Playford B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Port Lincoln GT | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | S
Portt Stanvac A | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Portt Stanvac B | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | S
Quarantine | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | S
Snuggery | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | S
Torrens Island A | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Torrens Island B | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | S
Firm Wind Capacity | 74.8719 | 81.9375 | 81.9375 | 81.9375 | 81.9375 | 81.9375 | 81.9375 | 81.9375 | 81.9375 | 81.9375 | SS
Total | 2493.1719 | 2257.2375 | 2257.2375 | 2257.2375 | 2257.2375 | 2257.2375 | 2257.2375 | 2257.2375 | 2257.2375 | 2257.2375
Winter aggregate available semi-scheduled generation
Project Station | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Dispatch Type
Clements Gap | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | SS
Hallett 4 North Brown Hill | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | 132.3 | SS
Hallett 5 The Bluff WF | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | SS
Hallett Stage 1 Brown Hill | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | SS
Hallett Stage 2 Hallett Hill | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | SS
Lake Bonney 2 Wind Farm | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | SS
Lake Bonney 3 Wind Farm | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | SS
Snowtown | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | SS
Snowtown S2 North | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | SS
Snowtown S2 South | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | SS
Waterloo | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | SS
Committed Projects
Hornsdale Wind Farm | 0 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | SS
Total | 1085.1 | 1187.5 | 1187.5 | 1187.5 | 1187.5 | 1187.5 | 1187.5 | 1187.5 | 1187.5 | 1187.5

## Existing NS Generation
Existing non-scheduled generation – South Australia
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type | Service Status
Angaston 1 | Infratil Energy Australia Pty Ltd | 30 | Compression Reciprocating Engine | Diesel | In Service
Angaston 2 | Infratil Energy Australia Pty Ltd | 20 | Compression Reciprocating Engine | Diesel | In Service
Blue Lake Milling Power Plant | Vibe Energy Pty Ltd | 0.505 | Compression Reciprocating Engine | Diesel | In Service
Canunda | Canunda Power Pty Ltd | 46 | Wind - Onshore | Wind | In Service
Cathedral Rocks | JV Cathedral Rock Investments Pty Ltd and Acciona Energy Oceania Pty Ltd | 66 | Wind - Onshore | Wind | In Service
Highbury | EDL LFG SA Pty Ltd | 1.03 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In Service
Lake Bonney 1 Wind Farm | Lake Bonney Wind Power Pty Ltd | 80.5 | Wind - Onshore | Wind | In Service
Mt Millar | Mount Millar Windfarm Pty Ltd | 70 | Wind - Onshore | Wind | In Service
Pedler Creek | EDL LFG SA Pty Ltd | 3.09 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In Service
Starfish Hill | Ratch Australia | 34.5 | Wind - Onshore | Wind | In Service
Tatiara Meats | Vibe Energy Pty Ltd | 0.5 | Compression Reciprocating Engine | Diesel | In Service
Tea Tree Gully | EDL LFG SA Pty Ltd | 1.03 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In Service
Terminal Storage Mini Hydro | Lofty Ranges Power Pty Ltd | 2.5 | Hydro - Gravity | Water | In Service
Wattle Point | Infrastructure Capital Group | 90.75 | Wind - Onshore | Wind | In Service
Wingfield 1 | EDL LFG SA Pty Ltd | 4.1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In Service
Wingfield 2 | EDL LFG SA Pty Ltd | 4.1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas | In Service
Total |  | 454.605
*Port Stanvac and Lonsdale have been changed from non-scheduled to scheduled.

## New Developments
Projects under development – South Australia
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Full Commercial Use Date
Barn Hill | Barn HIll Wind Farm Pty Ltd | 1-62 | Wind | Wind - Onshore | [5 empty] | Pub An | 124-186 | SS | TAB
Carmodys Hill | Energy Pacific Vic Pty Ltd | 1-70 | Wind | Wind - Onshore | [5 empty] | Pub An | 140 | SS | TBA
Ceres Project | Senvion formely REpower | Senvion 3.4M | Wind | Wind - Onshore | [5 empty] | Pub An | up to 670 | SS | NULL
Cherokee Power Station | Tungkillo Powerco Pty Ltd | A | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 250 | S | 2016-10-01
Exmoor | Acciona Energy | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
Hornsdale Wind Farm | HWF 1 Pty Ltd | Stage 1 | Wind | Wind - Onshore | ü | ü | ü | ü | ü | Com | 102.4 | SS | 2016-11-01
|  | Next Stages | Wind | Wind - Onshore | [5 empty] | Pub An | 167.6 | SS | TBA
Innamincka | Geodynamics Limited / Origin Energy Geothermal Pty | 11 | Geological heat | Geoth. HDR-Binary cycle | [5 empty] | Pub An | 510 | S | TBA
Keyneton | Energy Pacific Vic Pty Ltd | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 105 | SS | TBA
Kongorong | Ratch Australia | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 100-240 | SS | 2020-06-01
Kulpara | Ratch Australia | 52 | Wind | Wind - Onshore | [5 empty] | Pub An | 60-150 | SS | 2022-03-01
Leigh Creek Energy Project | Leigh Creek Energy Limited | 200 MW | Natural Gas Pipeline | CCGT | [5 empty] | Pub An | 200 | S | 2019-07-01 | x
Lincoln Gap Wind Farm | Lincoln Gap Wind Farm Pty Ltd | 1-59 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 177 | SS | TBA
Mount Hill | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 80-180 | SS | TBA
Palmer Wind Farm | TrustPower Australia | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | Up to 342 | SS | 2018-11-01
Pelican Point S2 | Pelican Point Power Limited | 1-2 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 320 | S | TBA
Port Augusta Renewable Energy Park | DP Energy | 1-59 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 195 | SS | TBA
|  | All Units | Solar | PV panels | ü |  |  |  |  | Pub An | 180 | SS | TBA
Stony Gap | EnergyAustralia Renewables Pty Ltd | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
Waterloo | Waterloo Windfarm Pty Ltd | 38-43 | Wind | Wind - Onshore | [5 empty] | Pub An | 18 | SS | TBA
Willogoleche | Willogoleche Power Pty Ltd | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 95-125 | SS | TBA
Woakwine Wind Farm | Infigen Energy | Turbines 1-124 | Wind | Wind - Onshore | [5 empty] | Pub An | 400 | SS | TBA
Kingfisher solar storage project | Lyon Infrastructure Investments Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 17 | TBA | TBA | x
Roxby Downs Solar Farm | Lyon Infrastructure Investments Pty Ltd | TBA | Solar | Solar | [5 empty] | Pub An | 17 | TBA | TBA | x
Yorke Penninsula Biomass Energy | TBA | TBA | Biomass | Biomass | [5 empty] | Pub An |  | TBA | TBA | x
Infratech’s floating PV plant | TBA | TBA | Solar | Solar | [5 empty] | Pub An | 3.2 | TBA | TBA | x

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as semi-scheduled or non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more, unless AEMO approves its classification as scheduled or non-scheduled. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW, unless AEMO approves its classification as semi-scheduled or semi-scheduled.
Generating systems greater than 30 MW must be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating of less than 5 MW may be be exempted by AEMO if its generation is purchased entirely by the local retail or a customer at the generator's connection point or the generator is classified as a market generating unit by a market small generation aggregator. A generating unit with a nameplate rating is between 5 MW and 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.