## Summary
2015 Planning Studies - Additional Modelling Data and Assumptions Summary
This file presents tables of input data for the 2015 planning studies. It is a compilation of data from a number of sources, and represents the current set of technical data to be used in the 2015 NTNPD studies. Detailed technical data for generators can be found in Fuel and Technology Cost Review- Data (ACIL Allen)
This spreadsheet may be updated as the studies progress, if revisions are required, or if additional data becomes available.
Table Descriptions
Table Name | Description
Carbon Price | Contains information regarding projected carbon price assumtions
LRET | Provides information regarding the Large-scale Renewable Energy Target
GreenPower | Provides information regarding energy generated to satisfy GreenPower requirements
ACT Scheme | Provides information regarding the ACT 90% scheme
DSP | Lists commited demand side participation
Hydro Storage | Contains information regarding hydroelectric storage inflows
Interconnector Capability | Lists forward and backward interconnector capability
Proportioning Factors | Provides information regarding assumptions used in regard to location of interconnector losses
Augmentation Options | Lists augmentation options to be considered during the 2013 studies

## Carbon Price
Carbon Price Trajectories
Carbon Price Trajectories (Real 2014-15 $/t CO2-e)
| LCO5 | MCO5 | HCO5
2015/16 | 0 | 0 | 0
2016/17 | 0 | 0 | 0
2017/18 | 0 | 0 | 0
2018/19 | 8.2 | 0 | 0
2019/20 | 10.8 | 0 | 0
2020/21 | 11.1 | 0 | 0
2021/22 | 11.4 | 10.4693 | 1.6692
2022/23 | 11.8 | 10.7793 | 1.7182
2023/24 | 12.2 | 11.1027 | 1.7691
2024/25 | 12.6 | 11.4379 | 1.8221
2025/26 | 13.1 | 11.7873 | 1.8774
2026/27 | 13.5 | 12.1745 | 1.9388
2027/28 | 14 | 12.6141 | 2.0083
2028/29 | 14.5 | 13.0709 | 2.0806
2029/30 | 15.1 | 13.5392 | 2.1547
2030/31 | 15.6 | 14.0253 | 2.2317
2031/32 | 16.2 | 14.5334 | 2.3124
2032/33 | 16.8 | 15.067 | 2.3973
2033/34 | 17.5 | 15.6271 | 2.4865
2034/35 | 18.1 | 16.2144 | 2.5803
2035/36 | 18.8 | 16.8289 | 2.6786
2036/37 | 19.6 | 17.4706 | 2.7815
2037/38 | 20.2 | 18.1401 | 2.889
2038/39 | 20.8 | 18.8368 | 3.001
2039/40 | 21.4 | 19.562 | 3.1177

## LRET
Large-scale Renewable Energy Target
Source: http://ret.cleanenergyregulator.gov.au/About-the-Schemes/lret
Calendar year | Target (GWh, Australia) | Target (GWh, NEM) 1 | Financial year 3 | Target (GWh, NEM) 4
2014 | 16950 | 15085.5
2015 | 18850 | 16776.5 | 2014-15 | 15931
2016 | 21431 | 19073.59 | 2015-16 | 17925.045
2017 | 26031 | 23167.59 | 2016-17 | 21120.59
2018 | 28637 | 25486.93 | 2017-18 | 24327.26
2019 | 31224 | 27789.36 | 2018-19 | 26638.145
2020 | 33850 | 30126.5 | 2019-20 | 28957.93
2021 | 33000 | 29370 | 2020-21 | 29748.25
2022 | 33000 | 29370 | 2021-22 | 29370
2023 | 33000 | 29370 | 2022-23 | 29370
2024 | 33000 | 29370 | 2023-24 | 29370
2025 | 33000 | 29370 | 2024-25 | 29370
2026 | 33000 | 29370 | 2025-26 | 29370
2027 | 33000 | 29370 | 2026-27 | 29370
2028 | 33000 | 29370 | 2027-28 | 29370
2029 | 33000 | 29370 | 2028-29 | 29370
2030 2 | 33000 | 29370 | 2029-30 | 29370
1. Assumes NEM share of Australia-wide energy consumption of 89%.
2. The LRET target is undefined after 2030
3. LRET targets are defined on a calendar year basis, however modelling is performed on financial year basis
4. A baseline of 14425.98 GWh from existing hydro plants in the NEM is added to the Target (GWh, NEM).

## GreenPower
GreenPower
Energy generated to satisfy GreenPower requirements is additional to LRET targets 1,2,3
Calendar Year | Green Power | Financial year | Green Power
2014 | 1925.638
2015 | 1482.095 | 2014-15 | 1703.8665
2016 | 1374.731 | 2015-16 | 1428.413
2017 | 1150 | 2016-17 | 1262.3655
2018 | 950 | 2017-18 | 1050
2019 | 750 | 2018-19 | 850
2020 | 540 | 2019-20 | 645
2021 | 320 | 2020-21 | 430
2022 | 130 | 2021-22 | 225
2023 | 100 | 2022-23 | 115
2024 | 100 | 2023-24 | 100
2025 | 100 | 2024-25 | 100
2026 | 100 | 2025-26 | 100
2027 | 100 | 2026-27 | 100
2028 | 100 | 2027-28 | 100
2029 | 100 | 2028-29 | 100
2030 | 100 | 2029-30 | 100
1. The uptake of GreenPower has decline over time and the forecast of GreenPower energy is representative of this.
2. It is assumed that there will always be a few customers who choose GreenPower.
3. The trend is a decline to a floor value of 100 MW.

## ACT Scheme
ACT 90% Scheme
Energy generated to satisfy ACT 90% Scheme requirements is additional to LRET targets1,2,3
Calendar Year | ACT 90% Scheme | Financial year | ACT 90% Scheme
2014 | 20
2015 | 130 | 2014-15 | 75
2016 | 290 | 2015-16 | 210
2017 | 580 | 2016-17 | 435
2018 | 950 | 2017-18 | 765
2019 | 1420 | 2018-19 | 1185
2020 | 1900 | 2019-20 | 1660
2021 | 1900 | 2020-21 | 1900
2022 | 1900 | 2021-22 | 1900
2023 | 1900 | 2022-23 | 1900
2024 | 1900 | 2023-24 | 1900
2025 | 1900 | 2024-25 | 1900
2026 | 1900 | 2025-26 | 1900
2027 | 1900 | 2026-27 | 1900
2028 | 1900 | 2027-28 | 1900
2029 | 1900 | 2028-29 | 1900
2030 | 1900 | 2029-30 | 1900
1. The 90% total energy target for 2020 of 1,900 GWh came from Figure 30 of Action Plan 2: A new climate change strategy and action plan for the Australian Capital Territory
2. For years after 2020-21 it is assumed there is no change in energy. |  |  |  | link

## DSP
Estimated available DSP
| NSW | QLD | SA | TAS | VIC Summer | VIC Winter
Prices > $300/MWh | 23.9001 | 57.8828 | 36.9193 | 1.7893 | 74 | 74
Prices > $500/MWh | 31.6107 | 57.8828 | 39.5919 | 6.0605 | 79 | 79
Prices > $1000/MWh | 33.7719 | 59.1649 | 42.0302 | 6.0605 | 79 | 79
Prices > $7500/MWh | 164.4025 | 81.2345 | 122.5287 | 32.8712 | 168 | 108
Prices = MPC | 421.7349 | 156.2948 | 167.1593 | 72.5097 | 245 | 185
Estimated DSP for Queensland LNG from 2017-18 1
| Low uptake | Medium uptake | High uptake
Prices > $300/MWh | 0 | 0 | 0
Prices > $500/MWh | 0 | 0 | 0
Prices > $1000/MWh | 0 | 100 | 100
Prices > $7500/MWh | 0 | 100 | 100
Prices = MPC | 200 | 400 | 600
1. No DSP from LNG before 2017

## Hydro Storage
Hydroelectric Storage Inflows
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Blowering | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3376 | 24.5603 | 30.7075 | 34.3206
Eucumbene | 328 | 330 | 100 | 329 | 434 | 750 | 749 | 434 | 435 | 434 | 154 | 293
Fitzroy Falls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Guthega | 4.569 | 1.6356 | 0.31 | 0.844 | 4.031 | 7.259 | 9.3438 | 14.754 | 20.585 | 33.541 | 25.294 | 14.19
Koombooloomba Dam | 15.634 | 21.4781 | 22.5776 | 16.8359 | 22.4743 | 39.9951 | 35.9065 | 72.783 | 62.6867 | 50.6899 | 35.8876 | 44.4651
Kuranda Weir | 31.2125 | 25.2585 | 29.4399 | 16.956 | 28.7011 | 27.2822 | 17.4346 | 12.5394 | 30.0189 | 18.5019 | 16.35 | 12.6184
Split Yard Creek Dam | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eildon | 3.7565 | 1.8262 | 1.9238 | 3.3983 | 5.5076 | 18.8258 | 33.7134 | 45.6678 | 48.6122 | 33.3962 | 16.4894 | 6.4833
Dartmouth | 10.0982 | 7.6542 | 4.1385 | 5.0361 | 9.6919 | 20.9483 | 32.1252 | 42.6779 | 58.7651 | 50.7566 | 26.3713 | 16.7084
Derwent | 13.3004 | 11.5003 | 4.1301 | 43.9613 | 281.4386 | 263.688 | 297.509 | 254.9078 | 537.3463 | 541.2265 | 102.5531 | 118.6136
Anthony/Pieman Pond | 46.3214 | 35.5511 | 45.6914 | 66.262 | 324.1599 | 211.9164 | 246.7975 | 136.4141 | 323.8998 | 277.3484 | 54.5617 | 103.2031
Burbury | 9.3003 | 14.4104 | 15.0805 | 35.2711 | 131.984 | 65.872 | 65.062 | 35.0611 | 114.0935 | 86.5526 | 5.2902 | 42.4113
Lake Gordon | 23.9407 | 25.9908 | 34.331 | 69.4021 | 264.668 | 142.9943 | 156.3548 | 75.1023 | 242.0574 | 191.4958 | 11.8104 | 119.5136
Great Lake/Trevallyn pond | 3.7201 | 2.6901 | 3.7201 | 9.2703 | 197.166 | 133.9241 | 312.4895 | 143.9744 | 295.209 | 163.685 | 92.1628 | 5.2102
Mersey Forth Pond | 7.8902 | 8.7603 | 10.2703 | 26.4008 | 163.685 | 141.5443 | 260.2479 | 132.984 | 272.0783 | 237.6372 | 93.1128 | 60.6018
| Tasmanian inflows | [9 empty] | Victorian inflows
| Snowy inflows | [9 empty] | Queensland inflows

## Interconnector Capability
Interconnector Transfer Capability
Interconnector | Forward Direction | Forward capability: peak demand periodsa,b (MW) | Reverse Capability: peak demand periodsa,b (MW)
QNI | NSW to QLD | 540 | 1200
Terranora | NSW to QLD | 100 | 200
VIC-NSW | VIC to NSW | 500 | 150
Heywood (until 2016) | VIC to SA | 460 | 460
Heywood (from 2017) | VIC to SA | 650 | 650
Murraylinkc | VIC to SA | 0 | 170
Basslink | TAS to VIC | 594 | 478
Notes:
a. Iner-regional transfer capability is represented by a representative single number for long term modelling. In real time opertion transfer capability is determined by constraint equations.
b. Transfer capability represents with peak demand in the importing region
c. Forward capability limited by thermal limitations in Victoria 220kV tranmission network and reverse capbability limited by thermal limitations in 132kV transmission network in South Australia.

## Proportioning Factors
Proportioning Factors for Inter-Regional Losses
Notional Interconnector | Proportioning Factor | Region applied to
Queensland - New South Wales (QNI) | 0.55 | New South Wales
Queensland - New South Wales (Terranora) | 0.6 | New South Wales
Victoria - New South Wales | 0.39 | New South Wales
Victoria - South Australia (Heywood) | 0.77 | Victoria
Victoria - South Australia (Murraylink) | 0.82 | Victoria
Tasmania - Victoria (Basslink) 1 | 0.5 | Victoria
1. Basslink is not a regulated interconnector. A value of 0.5 has been assumed.

## Augmentation Options
Inteconnector Augmentation Options
Inter-connector | Augmentation Options | Projects | Forward Direction | Capacity increase in forward direction (MW) | Capacity increase in reverse direction (MW) | Cost Estimate ($ millions)
QNI | QNI-Option 1 | Uprating of the Northern NSW 330 kV lines and second Armidale SVC | NSW to QLD | 78 | 57 | 102
| QNI-Option 2 | Series compensation on the Bulli Creek-Dumaresq and Dumaresq-Armidale 330 kV lines (50% series compensation) | NSW to QLD | 230 | 245 | 183
| QNI-Option 3 | Series compensation on the Bulli Creek-Dumaresq 330 kV line only (30% series compensation). This option avoids series compensation of the Armidale - Dumaresq circuits making it lower cost for wind farms to connect to that double circuit line should they choose to do so in the future | NSW to QLD | 212 | 171 | 132
| QNI-Option 4 | New SVCs at Dumaresq and Tamworth and Switched Shunt Capacitors at Dumaresq, Armidale, and Tamworth substations | NSW to QLD | 230 | 194 | 179
| QNI-Option 5 | A second 330 kV HVAC QLD-NSW interconnector (Bayswater-Western Downs) | NSW to QLD | 807 | 841 | 1322
| QNI-Option 6 | A second 330 kV HVAC QLD-NSW interconnector (Armidale-Bulli Creek) | NSW to QLD | 230 | 393 | 570
| QNI-Option 7 | A 500 kV HVAC QLD-NSW interconnector (Bayswater-Western Downs) | NSW to QLD | 703 | 841 | 2339
VIC-NSW | VIC-NSW Option 1 | Second South Morang 500/330 kV transformer, a braking resister at Loy Yang and uprating of the South Morang-Dederang 330 kV circuits Uprate Upper Tumut-Canberra and Upper Tumut-Yass 330 kV lines | VIC-NSW | 170 | 0 | 80
| VIC-NSW Option 2 | Uprate South Morang-Dederang 330 kV lines and series capacitors Uprate Eildon-Thomastown 220 kV line A fourth 300/220 kV Dederang transformer Series compensation on Eildon-Thomastown 220 kV line Phase angle regulator on the Bendigo-Shepparton 220 kV line | VIC-NSW | 170 | 150 | 214
| VIC-NSW Option 3 | VIC-NSW Option 2 plus A third 330/220 kV South Morang transformer Connection of Rowville-Thomastown 220 kV line at South Morang Series compensation on Wodonga-Dederang 330 kV line Phase angle regulator on the Jindera-Wodonga 330 kV line | VIC-NSW | 170 | 400 | 353
| VIC-NSW Option 4 | A double circuit 500 kV line from South Morang to Bannaby | VIC-NSW | 3200 | 3200 | 3051
Heywood | VIC-SA Heywood Option 1 | Second 275 kV circuit from Tailem Bend and Tungkillo and Uprate Heywood and South East 275 kV circuits, and a SVC at Tailem Bend | VIC-SA | 190 (S) 270 (W) | 190 (S) 270 (W) | 90
| VIC-SA Heywood Option 2 | A 500 kV double circuit line from Krongart to Heywood initially operating at 275 kV Two additional 500/275 kV transformers at Heywood Additional reactive power compensation | VIC-SA | 1940 | 1940 | 915
Murraylink | VIC-SA Murraylink Option 1 | Two 15 MVAr shunt capacitor banks in Monash area | VIC - SA | 0 | 50 | 14
| VIC-SA Murraylink Option 2 | Upgrade of Murraylink to 400 MW and new 275kV double circuit line from Robertstown to Berri (200km line and two substations) | VIC-SA | 0 | 180 | 476
| VIC-SA Murraylink Option 3 | Option 2 + 220kV double circuit line from Shepparton-Kerang-Redcliffs (450km and 3 substations) | VIC-SA | 400 (S) 180 (W) | 0 | 851
SA-NSW | SA-NSW Option 1 | New interconnector between SA and NSW | NSW-SA | 2000 | 2000 | 3051
VIC-TAS | VIC-TAS Option 1 | A 400 kV mono-polar transmission system between Mortlake and West Montagu A 220 kV double circuit line between West Montagu and Burnie | TAS to VIC | 600 | 480 | 864