## Index
National Transmission Network Development Plan (NTNDP)
Electronic Material – Consolidated summary 2016 Transmission Annual Planning Report (TAPR) augmentations
This supplement provides:
* A consolidated summary of the augmentations proposed by each TNSP in their 2016 TAPRs and how the main grid augmentations relate to the NTNDP
Please note that the data format may need to be adjusted in order to view the data to the level of fidelity required. For example, you may need to format the cell to a more appropriate number of decimal places in some cases as desired.
Index Table
Tab Name | Content Description
Powerlink 2016 TAPR Projects | List of projects from the 2016 Powerlink TAPR1
TransGrid 2016 TAPR Projects | List of projects from the 2016 TransGrid TAPR2
AEMO 2016 TAPR Projects | List of projects from the 2016 AEMO Victorian TAPR3
ElectraNet 2016 TAPR Projects | List of projects from the 2016 ElectraNet TAPR4
TasNetworks 2016 TAPR Projects | List of projects from the 2016 TasNetworks TAPR5
1 | Powerlink. Available: https://www.powerlink.com.au/About_Powerlink/Publications/Transmission_Annual_Planning_Reports.aspx
2 | TransGrid. Available:https://www.transgrid.com.au/news-views/publications
3 | AEMO. Available: https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Victorian-transmission-network-service-provider-role/Victorian-Annual-Planning-Report
4 | ElectraNet. Available: https://www.electranet.com.au/electranet-publishes-2016-south-australian-transmission-annual-planning-report/
5 | TasNetworks. Available: http://www.tasnetworks.com.au/our-network/planning-and-development/annual-planning-program

## Powerlink 2016 TAPR Projects
2016 APR Reference |  | Transmission Development | Limitation Addressed | 2016 APR Project Status | 2016 APR Anticipated Timing | 2016 APR Indicative Cost ($ million) | 2015 APR Reference | AEMO categorisation | 2016 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Section 3.2 | Table 3.1 | Pioneer Valley feeder bays | Increase voltage stability in Mackay | Completed | 2015-11-01 | Not stated. | Section 3.2 Section 4.2.3 |  | Local supply need based on future loads - not within the 2016 NTNDP scope. | Local Network | Not applicable
| Table 3.2 | Moranbah area 132kV capacitor banks | Increase supply capability in the North zone | Committed | winter 2013 to summer 2017/18 | Not stated. | Section 3.2 Section 4.2.3 |  | Included in the 2016 NTNDP studies. | Local Network | Not applicable
| Table 3.3 | Aurizon 132 kV rail connection (Wotonga) | New connection to supply rail load in the Bowen Basin area | Completed | July 2015 | Not stated. | Section 3.2 |  | Included in the 2016 NTNDP studies. | Local Network | Not applicable
|  | APLNG / GLNG Wandoan South connections | New connection for CSM/LNG compression | Completed | 2015-12-01 | Not stated. | Section 3.2 |  | Included in the 2016 NTNDP studies. | Local Network | Not applicable
| Table 3.4 | Line refit works on 132kV transmission line between Woree and Kamerunga substations | Maintain supply reliability in the Far North zone | Completed | July 2015 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Ross 300kV 100MVAr bus reactor | Maintain supply reliability in the Ross zone | Completed | August 2015 | Not stated. | Section 3.2 |  | Included in the 2016 NTNDP studies. | Main Grid | Not applicable
|  | Collinsville Substation replacement (located at Collinsville North) | Maintain supply reliability in the North zone | Completed | October 2015 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Swanbank B Substation replacement (located at Blackstone) | Maintain supply reliability in the Moreton zone | Completed | November 2015 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission line between Sumner Tee and Richlands substations | Maintain supply reliability in the Moreton zone | Completed | October 2015 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
| Table 3.5 | Turkinje secondary systems replacement | Condition based Maintain supply reliability in the Far North zone | Committed | Summer 2018/19 | Not stated. | Section4.2.1 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Garbutt to Alan Sherriff 132kV line replacement | Condition based replacement. Maintain supply reliability in the Ross zone | Committed | 2018-06-01 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Nebo 275/132kV transformer replacements | Condition based replacement. Maintain supply reliability in the North zone | Committed | summer 2013/14 to summer 2017/18 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on the 132kV transmission line between Collinsville North and Proserpine substations | Condition based Maintain supply reliability to Proserpine | Committed | Summer 2018/19 | Not stated. | Section 4.2.3 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Proserpine Substation replacement | Condition based replacement. Maintain supply reliability in the North zone | Committed | Winter 2016 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Moranbah 132/66kV transformer replacement | Condition based replacement. Maintain supply reliability in the North zone | Committed | Summer 2016/17 | Not stated. | Section 3.2 |  | Included in the 2016 NTNDP studies. | Local Network | Not applicable
|  | Mackay Substation replacement | Condition based replacement. Maintain supply reliability in the North zone | Committed | Summer 2017/18 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Nebo primary plant and secondary systems replacement | Condition based. Maintain supply reliability in the North zone | Committed | Summer 2019/20 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Rockhampton Substation replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Committed | Winter 2016 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Blackwater Substation replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Committed | Summer 2016/17 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Baralaba secondary systems replacement | Condition based Maintain supply reliability in the Central West zone | Committed | Summer 2016/17 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Moura Substation replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Committed | Summer 2017/18 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Stanwell secondary systems replacement | Condition based Maintain supply reliability in the Central West zone | Committed | Summer 2018/19 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Calvale and Callide B secondary systems replacement | Condition based Maintain supply reliability in the Central West zone | Committed | Winter 2021 | Not stated. | Section 4.2.4 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Callide A Substation replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Committed | Summer 2017/18 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 132kV transmission lines between Calliope River to Boyne Island | Condition based Maintain supply reliability in the Central West zone | Committed | Summer 2017/18 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Tennyson secondary systems replacement | Condition based Maintain supply reliability in the Moreton zone | Committed | Summer 2017 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Upper Kedron secondary systems replacement | Condition based Maintain supply reliability in the Moreton zone | Committed | Summer 2016 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Rocklea secondary systems replacement | Condition based Maintain supply reliability in the Moreton zone | Committed | Summer 2017 | Not stated. | Section 3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Blackwall IPASS secondary systems Replacement | Condition based Maintain supply reliability in the Moreton zone | Committed | Winter 2017 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission lines between Runcorn to Algester | Condition based Maintain supply reliability in the Moreton zone | Committed | Summer 2016/17 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission lines between Belmont to Runcorn | Condition based Maintain supply reliability in the Moreton zone | Committed | Winter 2017 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Mudgeeraba 110kV Substation primary plant and secondary systems replacement | Condition based Maintain supply reliability in the Gold Coast zone | Committed | Summer 2017/18 | Not stated. | Section 4.2.8 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Mudgeeraba 275/110kV transformer replacement | Condition based replacement. Maintain supply reliability in the Gold Coast zone | Committed | Summer 2017/18 | Not stated. | Section 4.2.8 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
| Table 3.6 | Proserpine to Glenella 132kV transmission line retirement | Removal of assets at the end of technical life in the North zone | Committed retirement | Summer 2016/17 | Not stated. | NA |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.1 | Table 4.3 | Line refit works on the 132kV transmission line between Kareeya and Chalumbin substations | Condition based Maintain supply reliability to Kareeya | Proposed | Summer 2017/18 | 8 | Section 4.2.1 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Retirement of one 132/22kV Cairns transformer | Maintain supply reliability to the Far North zone | Proposed | Summer 2019/20 | 0.5 | NA | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Kamerunga Substation replacement | Condition based replacement. Maintain supply reliability to the Far North zone | Proposed | Summer 2019/20 | 25 | Section 4.2.1 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Woree secondary systems replacement | Condition based Maintain supply reliability to the Far North zone | Proposed | Summer 2020/21 | 10 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.2 | Table 4.4 | Line refit works on the coastal 132kV transmission line between Townsville South and Clare South substations | Condition based. Maintain supply reliability in the Ross zone | Proposed | Summer 2018/19 | 29 | Section 4.2.2 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Retirement of the inland 132kV transmission line between Townsville South and Clare South substations | Condition based. Maintain supply reliability in the Ross zone | Proposed | Summer 2019/20 | 10 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on one 132kV transmission line between Strathmore/Collinsville North and Clare South substations | Condition based. Maintain supply reliability in the Ross zone | Proposed | Summer 2021/22 | 55 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Ingham South 132/66kV transformers replacement | Condition based replacement. Maintain supply reliability in the Ross zone | Proposed | Summer 2019/20 | 7 | Section 4.2.2 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Garbutt 132/66kV transformers replacement | Condition based replacement. Maintain supply reliability in the Ross zone | Proposed | Summer 2018/19 | 11 | Section 4.2.2 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Dan Gleeson Secondary Systems replacement | Condition based. Maintain supply reliability in the Ross zone | Proposed | Summer 2019/20 | 7 | Section 4.2.2 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Townsville South primary plant and secondary system replacement | Condition based. Maintain supply reliability in the Ross zone | Proposed | Summer 2020/21 | 16 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.3 | Table 4.5 | Line refit works on the 132kV transmission line between Eton Tee and Alligator Creek Substation | Condition based Maintain supply reliability to Alligator Creek | Proposed | Summer 2018/19 | 10 | Section 4.2.3 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.4 | Table 4.6 | Line refit of the 132kV transmission line between Egans Hill and Rockhampton substations | Condition based Maintain supply reliability in the Central West zone | Proposed | Summer 2018/19 | 6 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line replacement of the 132kV transmission line between Callide A and Moura substations | Condition based Maintain supply reliability to Biloela and Moura in the Central West zone | Proposed | from 2020 | 68 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Retirement of the 132kV transmission line between Gladstone and Callide A | Maintain supply reliability to Biloela and Moura in the Central West zone | Proposed | Summer 2018/19 | 10 | Section 6.3.2 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Callide A Substation replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Summer 2018/2019 | 20 | Section 3.2 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Dysart Substation replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Summer 2019/20 | 12 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Dysart transformer replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Summer 2019/20 | 9 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Bouldercombe primary plant replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Summer 2019/20 | 26 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Bouldercombe transformer replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Summer 2019/20 | 7 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Wurdong secondary systems replacement | Condition based Maintain supply reliability in the Gladstone zone | Proposed | Summer 2018/19 | 10 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Lilyvale primary plant replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Summer 2020/21 | 8 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Lilyvale transformers replacement | Condition based replacement. Maintain supply reliability in the Central West zone | Proposed | Winter 2020 | 9 | Section 4.2.4 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.5 | Table 4.7 | Woolooga to Palmwoods Transmission Line refit | Condition based Maintain supply reliability in the Wide Bay zone | Proposed | Winter 2021 | 20 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Gin Gin Substation rebuild | Condition based Maintain supply reliability in the Wide Bay zone | Proposed | Summer 2018/19 | 27 | Section 4.2.5 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.6 | Table 4.8 | Tarong secondary systems replacement | Condition based Maintain supply reliability in the South West zone | Proposed | Summer 2021/22 | 11 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.7 | Table 4.9 | Line refit works on 110kV transmission lines between South Pine to Upper Kedron | Condition based. Maintain supply reliability in CBD and Moreton zone. | Proposed | Summer 2021/22 | 7 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission lines between Sumner to West Darra | Condition based. Maintain supply reliability in CBD and Moreton zone. | Proposed | Summer 2021/22 | 6 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission lines between Rocklea to Sumner | Condition based. Maintain supply reliability in CBD and Moreton zone. | Proposed | Summer 2021/22 | 9 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 110kV transmission lines between Blackstone to Redbank Plains to West Darra | Condition based. Maintain supply reliability in Moreton zone. | Proposed | Summer 2021/22 | 10 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 275kV transmission lines between Karana Tee to Bergins Hill to Goodna to Belmont | Condition based. Maintain supply reliability in Moreton zone. | Proposed | Summer 2021/22 | 36 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on 275kV transmission lines between South Pine to Karana Tee | Condition based. Maintain supply reliability in Moreton zone. | Proposed | Summer 2021/22 | 19 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Ashgrove West Substation replacement | Condition based. Maintain supply reliability in Moreton zone. | Proposed | Summer 2019 | 13 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Abermain secondary systems replacement | Condition based. Maintain supply reliability in Moreton zone. | Proposed | Winter 2020 | 7 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Belmont 275kV secondary system replacement | Condition based. Maintain supply reliability in CBD and Moreton zone. | Proposed | Winter 2021 | 9 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Palmwoods 275kV Substation primary and secondary replacement | Condition based. Maintain supply reliability in Moreton zone. | Proposed | Summer 2021/22 | 23 | Section 4.2.7 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.8 | Table 4.10 | Line refit works on the 110kV transmission line between Mudgeeraba and Terranora substations | Condition based Maintain reliable interconnection to New South Wales | Proposed | Summer 2019/20 | 5 | Section 4.2.8 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Line refit works on the 275kV transmission lines between Greenbank and Mudgeeraba substations | Condition based Maintain supply reliability to the Gold Coast zone | Proposed | Progressively from Summer 2020/21 | 69 | Section 4.2.8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Retirement of one Mudgeeraba 275/110kV transformer | Condition based Maintain supply reliability to the Gold Coast zone | Proposed | Summer 2019/20 | 0.5 | Section 4.2.8 | Committed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
|  | Mudgeeraba 275kV secondary systems replacement | Condition based Maintain supply reliability to the Gold Coast zone | Proposed | Summer 2021/22 | 11 | Section 4.2.8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 4.4.4 | Table 4.12 | Mt Emerald Windfarm | New windfarm near Atherton | Proposed | 2017/18 | NA | Section 4.4.4 |  | Connection point proposal | Connection | Not applicable
|  | Clare Solar PV | New solar arm near Clare | Proposed | Mid 2017 | NA | Section 4.4.4 |  | Connection point proposal | Connection | Not applicable
|  | Genex Kidston Hydro/Solar PV | New Hydro generator with Solar PV | Proposed | Mid 2019 | NA | NA |  | Connection point proposal | Connection | Not applicable
|  | Whitsunday Solar PV | New solar farm near Proserpine | Proposed | Mid 2019 | NA | NA |  | Connection point proposal | Connection | Not applicable
|  | Baralaba Solar PV | New solar farm near Baralaba | Proposed | Mid 2018 | NA | NA |  | Connection point proposal | Connection | Not applicable
|  | Multiple new coal mine 132kV connections | New industrial plant connections in the Galilee Basin area | Proposed | Progressively from summer 2018/19 | NA | Section 4.4.4 |  | Connection point proposal | Connection | Not applicable
|  | Bulli Creek Solar PV | New solar farm neat Bulli Creek | Proposed | Mid 2019 | NA | NA |  | Connection point proposal | Connection | Not applicable
Section 6.2.1 | NA | Supply to Bowen Basin coal mining area. Options include: • installation of a 132 kV capacitor bank at Proserpine Substation • installation of a second 275/132kV transformer at Strathmore Substation; and • turn-in to Strathmore substation the second 132 kV circuit between Collinsville North and Clare South substations • 132 kV phase shifting transformers to improve the sharing of power flow in the Bowen Basin within capability of existing transmission assts. | There have been several proposals for new coal mining, LNG and port expansion projects in the Bowen Basin area. These loads could cause voltage and thermal limitations impacting network reliability. | possible | Timing subject to commitment of additional load. | NA | Section 6.2.1 |  | Local supply need based on future loads - not within the 2016 NTNDP scope. | Local Network | Potential local generation support and demand side management initiatives.
Section 6.2.2 | NA | Supply to Bowen Industrial Estate: • installation of a second 132/66kV transformer at Bowen North Substation • connection of the second Strathmore to Bowen North 132kV circuit • second 275/132kV transformer at Strathmore Substation • turn-in to Strathmore Substation the second 132kV circuit between Collinsville North and Clare South substations. | There is no additional capacity forecasted to be required in Bowen industry estate in the medium economic outlook for the 2016 TAPR. However, Bowen North Substation supplys the forecasted electricity demand associated with infrastructure for new and expanded mining export and value adding facilities at 66kV via the Ergon Energy 66kV network from Proserpine and Strathmore substation. The outages of these connection could cause voltage and thermal limitation impacting network reliability. | possible | Timing subject to commitment of additional load. | NA | NA |  | Possible future project subject to customer commitment- not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.2.3 | NA | Supply to Galilee Basin coal mine area • installation of capacitor banks at Lilyvale Substation • installation of a third 275 kV circuit between Broadsound and Lilyvale substations • staged construction of a western 275 kV transmission corridor as part of a broader development strategy | There have been several proposals for new coal mining projects in the Galilee Basin that have not reached the required development status to be included in the medium economic outlook for the 2016 TAPR. These loads could cause voltage and thermal limitations impacting network reliability. | possible | Timing subject to commitment of additional load. | NA | Section 6.2.2 |  | Possible future project subject to customer commitment- not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.2.4 | NA | Central Queensland to North Queensland grid section transfer limit: 1. Following the string of the second circuit of a double circuit Stanwell–Broadsound 275 kV line, voltage and thermal limitations may reoccur. Options to address the emerging limitations could vary depending on the level of load commitment. • installation of capacitor banks and/or a SVC at existing central and northern Queensland substations. and/or • the construction of new transmission lines and/or series capacitors 2. An alternative is to establish a western 275kV corridor connecting Calvale and Lilyvale substations via Blackwater substation. | There have been several proposals for large mining and metal processing or other industrial loads in northern Queensland. These loads include large coal mine developments in Galilee Basin, expansion or development of coal mines and upstream liquefied natural gas (LNG) processing load in the Bowen Basin. The development status of these loads is not yet at the stage that they can be included (either wholly or in part) in the medium economic forecast of the APR. These loads could be up to 900MW. Thermal and voltage limitations will occur if even a portion of these new loads commit. | possible | Timing subject to customer commitment. Forecasted loads changed from 1500MW to 900MW | NA | Section 6.2.3 Appendix E |  | Possible future project subject to customer commitment- not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.2.5 | NA | Central West to Gladstone area reinforcement: A feasible network solution to facilitate efficient market operation may include transmission line augmentation between: • Calvale and Larcom Creek substations and • Larcom Creek and Calliope River substations. | Network limitation after decommissioning the 132 kV double circuit line between Callide and Gladstone South substations are not forecasted to impact reliability or efficient market outcomes occur in the medium economic outlook for the 2016 TAPR. However, there are several developments in the Queensland region that would change not only the power transfer requirements between the Central West and Gladstone zones but also on the intra-connectors to northern and southern Queensland. it may become economically viable to uprate its power transfer capacity to alleviate constraints. | possible | Beyond 5yr Outlook | NA | NA |  | Possible future project subject to customer commitment- not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.2.6 | NA | Supply to the Surat Basin north west area • Installation of SVCs at both Columboola and Wandoan South substations • additional circuits between Western Downs, Columboola and Wandoan South substations to increase fault level and transmission strength or • a combination of the above options. | There have been several proposals for additional LNG upstream processing facilities and new coal mining load in the Surat Basin north west area. These loads have not reached the required development status to be included in the medium economic forecast for the 2016 TAPR. The loads could be up to 350MW and cause voltage and thermal limitations impacting network reliability on the transmission system upstream of their connection points | possible | Beyond 5yr Outlook The loads changes from 400MW to 350MW | NA | Section 6.2.4 |  | Possible future project subject to customer commitment- not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 6.3.1 | NA | Ross zone: A potential reconfiguration option consists of: • a line refit of Collinsville North to King Creek substations • decommission the circuit section between King Creek to Clare South substations • install a second 275/132 kV transformer at Strathmore substation • establish 275 kV injection into Clare South substation | The network between Collinsville and Townsville comprises of a 132 kV network and a 275 kV network which operate in parallel. The 132 kV lines are approaching end of technical life within next five to 10 years, while the earliest end of technical life trigger for the 275 kV lines is beyond 10 years. | possible | Between 5 to 10 years | NA | Section 6.3.1 |  | Condition based renewals - not within the 2016 NTNDP scope. | Local Network/Main Grid | Not applicable
Section 6.3.2 | NA | Central West and Gladstone zones • Refitting or retirement of the 132 kV double circuit line between Callide and Gladstone South substations with possible network reconfiguration. | Condition based risks on the double circuit 132 kV line between Callide and Gladstone South substations. | possible | Between 5 to 10 years | NA | Section 6.3.2 |  | Condition based renewals - not within the 2016 NTNDP scope. | Local Network/Main Grid | Not applicable
Section 6.3.3 | NA | Central Queensland to South Queensland grid section: • Risks on the section between Calliope River and Wurdong may be managed through maintenance works, with minimal work required over the next five years. • maintenance or refurbishment on the South Pine to Woolooga 275kV transmission line in the next five to 10 years. • A transmission line refit project will also be required within the next five years to manage the risks of the 275kV single circuit transmission line between Palmwoods and Woolooga substations. | Three single circuit 275 kV transmission lines operate in parallel between Calliope River and South Pine substations and form the coastal corridor of the Central QLD to South QLD grid section. These single circuit 275 kV lines will reach end of technical life in 5 to 10 years. The 275 kV lines at the northern end of this corridor are currently tracking to a higher rate of corrosion and it's expected acceptable risk levels will be exceeded by 2021. The higher rate of corrosion is due to the proximity to the coast. Potential investment in renewable generation in central and north Queensland, coupled with the possible displacement and/or retirement of existing thermal plant may significantly increase the utilisation of the CQ-SQ grid section. | possible | Between 5 to 20 years | NA | Section 6.3.3 |  | Condition based renewals - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Section 6.5.2 | NA | The Queensland transmission network is interconnected to the New South Wales (NSW) transmission system through the Queensland/New South Wales Interconnector (QNI) transmission line and Terranora Interconnector transmission line. The most recent assessment did not recommend a preferred QNI upgrade option in light of uncertainties. However, Powerlink and TransGrid continue to monitor market developments to determine if any material changes could warrant reassessment. Relevant changes may include: • changes in generation and large-scale load developments in Queensland and the NEM (including LNG, coal developments, renewable generation, retirement of generation); and • NEM-wide reductions in forecast load and energy consumption. | The QNI maximum southerly capability is limited by thermal ratings, transient stability and oscillatory stability. The combined QNI plus Terranora Interconnector maximum northerly capability is limited by thermal ratings, voltage stability, transient stability and oscillatory stability. | Regulatory consultation concluded | Limiitation will be reviewed in 5-10 years | NA | Section 6.5.2 | Monitoring limitation > $6 million (equivalent to proposed) | Included in the 2016 NTNDP studies. | Main Grid | Not applicable
Note on I1: Matthew Armitage: New column in 2016

## 2016 TAS Projects
2016 APR Reference |  | Transmission Development | Limitation Addressed | 2016 APR Project Status | 2016 APR Anticipated Timing | 2016 APR Indicative Cost ($ million) | 2015 APR Reference | AEMO categorisation | 2016 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
6.2.2.1 |  | George Town Substation 110 kV redevelopment. | Condition based asset replacement of substation switchgears and associated equipment | Completed | 2015-08-01 | NA | 6.4.2.1 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.2.2.2 |  | Dynamic rating of supply transformers at Knights Road and Boyer substations | The maximum demand at Knights Road and Boyer substatios is approaching the continuous firm rating of the transformers | Completed | 2016-04-01 | NA | 6.8.2.1 |  | Local supply issue - not within the 2016 NTNDP scope. | NCIPAP | Not applicable
6.2.2.3 |  | Rosebery Substation transformer augmentation: Installation of cooling fans on the transformers to increase thermal capacity. | Thermal capacity of existing 110/44-22 kV transformers at Rosebery Substation. | Completed | 2016-04-01 | NA | 6.2.2.1 |  | Local supply issue - not within the 2016 NTNDP scope. | Local Network - distribution | Not applicable
6.2.11 |  | Sheffield Substation 220 kV K and L bay upgrades | Increase the rating of the Sheffield– George Town 220 kV transmission circuits, allowing more power to be transferred through this corridor | Committed | 2016-05-01 | NA | 6.3.2.1 | Committed augmentation < $6 million | NCIPAP project - not within the 2016 NTNDP scope. | NCIPAP | Not applicable
6.2.1.2 |  | Establishment of Rosny Park Zone Substation. | Strengthen the network on Hobart's eastern shore. | Committed | 2016-08-01 | NA | 6.6.2.1 | Committed augmentation > $6 million | Local supply issue - not within the 2016 NTNDP scope. | Local Network - distribution | Not applicable
6.2.1.3 |  | George Town to Comalco 220 kV line rating upgrade | Increase rating of dead-end assemblies (line connections) of George Town-Comalco 220 kV line | Committed | 2016-08-01 | NA | 6.4.2.1 | Committed augmentation < $6 million | NCIPAP project - not within the 2016 NTNDP scope. | NCIPAP | Not applicable
6.3.1.1 | Table 6-1 | Wesley Vale substation conversion from 11 kV to 22 kV | Convert supply voltage at Wesley Vale substation from 11 kV to 22 kV to increse supply diversity to local area. | Proposed | 2017-05-01 | 2.1 |  | Monitoring limitation < $6 million (equivalent to proposed) | Local supply issue - not within the 2016 NTNDP scope. | Local Network - distribution
6.3.2.1 | Table 6-2 | Dynamic rating of power tranformers at Farell, Sheffield, Hadspen and Palmerston substations | Allow dynamic rating of transforemrs to increase load transfer capability | Proposed | July 2016-Oct 2017 | 0.9 | 6.1.1.3/Table 6-3 |  | NCIPAP project - not within the 2016 NTNDP scope. | NCIPAP | Not applicable
6.3.2.1 | Table 6-2 | Liapootah-Chapel Street 220 kV and Hadspen-Norwood 110 kV transmission lines upgrade | Increase rating of dead-end assemblies (line connections) of Liapootah-Chael Street 220 kV and Hadspen-Norwood 110 kV transmission lines | Proposed | 2017-05-01 | 0.62 | 6.1.1.3/Table 6-3 |  | NCIPAP project - not within the 2016 NTNDP scope. | NCIPAP | Not applicable
6.3.2.1 | Table 6-2 | Chapel Street Substation - Install second 110 kV bus coupler circuit breaker | Reduce impact of bus coupler fault at Chapel Street Substation | Proposed | 2019-01-01 | 0.45 | 6.1.1.3/Table 6-3 |  | NCIPAP project - not within the 2016 NTNDP scope. | NCIPAP | Not applicable
6.3.3.1 | Table 6-1 | Decommission the Queenstown–Newton 110 kV transmission line; and connect Newton substation to the existing Farrell–Rosebery–Queenstown 110 kV transmission circuit. | Transmission line condition: Queenstown - Newton 110 kV line | Proposed | 2017-04-01 | 2.4 | 6.2.3.5 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
6.3.3.2 | Table 6-1 | Decommission the Waddamana - Bridgewater Junction 110 kV transmission line, and rearrange the existing 110 kV lines between Lindisfarne and Bridgewater to connect Bridgwater substation. | Condition of transmission line | Proposed | 2018-06-01 | 8 | 6.9.2.4/6.9.2.5 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
6.3.3.3 | Table 6-1 | Lindisfarne Substation - replace two 110/33 kV 45 MVA transformers with two 110/33 kV 60 MVA units | Condition of supply transformers. | Proposed | 2018-11-01 | 7.2 | 6.6.3.12 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
6.3.3.4 | Table 6-1 | North Hobart Substation - replace the 11 kV switchboards with new 12 kV air-insulated switchboards (operated at 11 kV) | Condition of 11 kV switchboards | Proposed | 2019-04-01 | 5.1 | 6.6.3.11 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.5 | Table 6-1 | Triabunna Spur transmission line - replace the 41 Kay poles on the Triabunna Spur transmission line with new steel poles. | Condition of transmission line support structure. | Proposed | 2019-06-01 | 3.7 | 6.7.3.7 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
6.3.3.6 | Table 6-1 | Palmerston Substation - asset renewal to replace the 23 type DR1 and DR2 disconnectors, the associated earth switches. | Condition of disconnectors and earth switches. | Proposed | 2020-04-01 | 5.9 | 6.4.3.6 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | Claremont Zone Substation - replace two 22.5 MVA transformers with two 25 MVA transformers. | Condition of supply transformers | Proposed | 2019-06-01 | 3 | 6.6.3.7 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | Gretna Zone Substation - replace two 1 MVA transformer with one 5 MVA unit. | Condition of supply transformers | Proposed | 2019-06-01 | 1 | 6.5.3.5 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | New Norfolk Zone Substation - replace four 2.5 MVA transformers with three 5 MVA transformers | Condition of supply transformers | Proposed | 2019-06-01 | 1.5 | 6.5.3.6 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | Richmond Zone Substation - replace two 2.5 MVA transformers with two 2.5 MVA trabsformers | Condition of supply transformers | Proposed | 2021-06-01 | 2.8 | 6.7.3.5 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | Derwent Park Zone Substation - replace two 22.5 MVA transformers with two 25 MVA transformers | Condition of supply transformers | Proposed | 2023-06-01 | 3 | 6.6.3.10 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | Geilston Bay Zone Substation - replace two 22.5 MVA transformers with two 25 MVA transformers | Condition of supply transformers | Proposed | 2024-06-01 | 4.2 | 6.6.3.14 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.3.7 | Table 6-3 | Bellerive Zone Substation - replace two 22.5 MVA transformers with two 25 MVA transformers | Condition of supply transformers | Proposed | 2026-06-01 | 4 | 6.6.3.13 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
6.3.4.1 |  | Transportable substation: 110/22/11 kV 25 MVA transformer and associated high voltage switchgears | Common spare 110/22/11 kV transformer to restore supply to communities and customers following an extended interruption to supply. | Proposed | 2019-05-01 | 8 | 6.9.2.6 | Monitoring limitation > $6 million (equivalent to proposed) | Local supply issue - not within the 2016 NTNDP scope. | Local Network | Not applicable
6.3.5.1 |  | Decommission the Butlers Gorge-Derwent Bridge 110 kV transmission line; and construct a new 22 kV distribution line from Butlers Gorge Power Station to supply the load. | Condition of assets | Deferred |  |  | 6.5.3.7 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement. | Not applicable
Note on I1: Matthew Armitage: New column in 2016

## AEMO 2016 APR Projects
2016 APR Reference |  | Transmission Development | Limitation Addressed | 2016 APR Project Status | 2016 APR Anticipated Timing | 2016 APR Indicative Cost ($ million) | 2015 APR Reference | 2016 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable) | 2015 APR Project Status | 2015 APR Anticipated Timing | 2015 APR Indicative Cost ($ million) | 2014 APR Reference | 2015 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Eastern Corridor | Appendix A.2 | A new 500/220 kV transformer at Hazelwood with an estimated cost of $36 million plus any fault level mitigation works. Upgrade the 220 kV Hazelwood–Rowville or Yallourn–Rowville lines. | Rowville - Yallourn loading when significant new generation is connected to the Latrobe Valley 220 kV transmission network and/or when there is significant capacity increase in the Hazelwood or Yallourn power stations. | Monitored | post 2025 | see "Transmission Development" column | "DSN Limitation Detail" Supplementary Information Workbook: South West Corridor | The NTNDP did not identify this limitation, as no scenario modelled significant capacity increases in either the Hazelwood or Yallourn power stations. | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | The NTNDP did not identify this limitation, as no scenario modelled significant capacity increases in either the Hazelwood or Yallourn power stations. | Main Grid | Not applicable.
|  | A new 500/220 kV transformer at Hazelwood with an estimated cost of $36 million plus any fault level mitigation works. Upgrade the 220 kV Hazelwood–Rowville or Yallourn–Rowville lines. | Hazelwood 500/220 kV transformer rating when significant new generation is connected to the Latrobe Valley 220 kV transmission network and/or when there is significant capacity increase in the Hazelwood or Yallourn power stations. | Monitored | post 2025 | see "Transmission Development" column | "DSN Limitation Detail" Supplementary Information Workbook: South West Corridor | The NTNDP did not identify this limitation, as no scenario modelled significant capacity increases in either the Hazelwood or Yallourn power stations. | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | The NTNDP did not identify this limitation, as no scenario modelled significant capacity increases in either the Hazelwood or Yallourn power stations. | Main Grid | Not applicable.
South West Corridor | Section 3.3.1 | South Australia–Victoria (Heywood) Interconnector Upgrade Installation of a third 500/275 kV transformer and 500 kV bus-tie at Heywood terminal station | Thermal capacity limitations of the Heywood transformers. | Completed (SA works expected complete March 2017) |  | NA | Section 2.3 | Included in the 2016 NTNDP studies. | Main Grid | Not applicable (network solution being implemented) | Committed | mid 2016 | NA | Section 3.2.2 | Included in the 2015 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
| Section 3.5 | Possible Dundonnell Wind Farm cut-in to the network. | Generation connection of Dundonell Wind Farm (312 MW) | Proposed | TBA | NA | Section 2.4 | NA | Main Grid | NA
| Section 3.5 | Possible Moorabool Wind Farm cut-in to the network. | Generation connection of Moorabool Wind Farm (321 MW) | Proposed | TBA | NA | NA | NA | Main Grid | NA
| Section 3.5 | Possible Mortlake South Wind Farm cut-in to the network. | Generation connection of Mortlake South Wind Farm (76.5 MW) | Proposed | TBA | NA | NA | NA | Local Network | NA
| Section 3.5 | Establish a new substation at Mt Gellibrand with possible line cut-in to Terang-Geelong 66 kV network. | Generation connection of Mt Gellibrand Wind Farm (132 MW) | Proposed | TBA | NA | Section 2.4 | NA | Local Network | NA
| Section 3.5 | Possible Salt Creek Wind Farm cut-in to the network. | Generation connection of Salt Creek Wind Farm (30 MW) | Proposed | TBA | NA | NA | NA | NA | NA
| Section 3.5 | Establish a new terminal station near Lismore, cut-in to Moorabool-Mortlake No.1 and and Moorabool-Tarrone No.2 500 kV circuits to connect Stockyard Hill Wind farm. | Generation connection of Stockyard Hill Wind Farm (534 MW) | Proposed | TBA | NA | Section 2.4 | NA | Main Grid | NA
| Appendix A.3 | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland with an estimated cost of $13.6 million. A static VAr compensator (SVC) or a synchronous static compensator (STATCOM) at an estimated cost of $31.6 million. Additional transposition towers along the Moorabool–Heywood–Alcoa Portland 500 kV line at an estimated cost of $35.9 million. | Moorabool - Heywood - Portland 500kV line voltage unbalance. Sectionalising the Moorabool–Heywood–Alcoa Portland 500 kV line to connect new generation potentially introduces voltage unbalance along the line when a line section is switched out. The impact of voltage unbalance levels increases in proportion to power flow magnitude and direction, new generation connection points, and output generated. | Monitored | post 2025 | see "Transmission Development" column | "DSN Limitation Detail" Supplementary Information Workbook: South West Corridor | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | A new Moorabool–Mortlake/Tarrone–Heywood 500 kV line with an estimated cost of $530.4 million. | Inadequate South-West Melbourne 500kV thermal capacity when significant wind generation and/or GPG (over 2,500 MW in addition to the existing generation from Mortlake) is connected to the transmission network. | Monitored | post 2025 | $530.4 million |  | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Installation of additional reactors or other type of reactive plant capable of absorbing reactive power. | Reduction in demand level during low load periods, particularly in the South-west corridor. Retirement of existing reactive plant in or close to the South-west corridor, such as the synchronous condenser at Brooklyn. | Monitored | post 2025 | NA | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
Northern Corridor | Appendix A.4 | Installing a new (third) 1,060 MVA 330 kV line between Murray and Dederang with an estimated cost of $176.5 million (excluding easement costs) or a new (second) 330 kV line from Dederang to Jindera at an estimated cost of $145.9 million (excluding easement costs). | Murray–Dederang 330 kV line rating with increased Murray generation and Vic import from NSW. | Monitored | post 2025 | see "Transmission Development" column | "DSN Limitation Detail" Supplementary Information Workbook: Northern Corridor | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Up–rating the two existing Dederang–South Morang 330 kV lines to 82 ºC (conductor temperature) operation and series compensation at an estimated cost of $16.2 million. Installing a new (third) 330 kV, 1,060 MVA single circuit line between Dederang and South Morang with 50% series compensation to match the existing lines, at an estimated cost of $234.6 million (excluding easement costs, and subject to obtaining the necessary easement) | Dederang–South Morang 330 kV line rating with increased Murray generation and Vic import from NSW. | Monitored | post 2025 | see "Transmission Development" column |  | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installing a wind monitoring scheme with an estimated cost of $524k or up-rating the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82 ºC, at an estimated cost of $11.9 million. | Dederang–Mount Beauty 220 kV line rating with increased Murray generation and Vic import from NSW. | Monitored | post 2025 | see "Transmission Development" column |  | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installing a wind monitoring scheme at an estimated cost of $524k or up-rating the Eildon–Thomastown 220 kV line, including terminations to 75 ºC operation, at an estimated cost of $42.8 million. | Eildon–Thomastown 220 kV line rating with increased Murray generation and Vic import from NSW, and increased NSW export. | Monitored | post 2025 | see "Transmission Development" column |  | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Installing a fourth 330/220 kV transformer at Dederang at an estimated cost of $20.8 million. | Dederang 330/220 kV transformer rating at times of over 2,500 MW of Vic import from NSW and Murray generation (with the DBUSS transformer control scheme being active). | Monitored | post 2025 | $20.8 million |  | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Installing additional capacitor banks and/or controlled series compensation at Dederang and Wodonga terminal stations. | Voltage collapse at South Morang, Dederang, Wodonga, and Jindera with Iincreased NSW import and export. | Monitored | post 2025 | NA |  | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
Greater Melbourne and Geelong | Section 3.2 & Appendix A.5 | Cut-in the Rowville-Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits at an estimated cost of $10.6 million. | Thermal capacity of the Rowville–Malvern 220 kV No.1 and 3 circuits limits load growth or additional loads connected to Malvern Terminal Station. | Monitored | post 2025 | $10.6 million | Section 2.1 and "DSN Limitation Detail" Supplementary Information Workbook: Greater Melbourne and Geelong | Existing control scheme for post-contingent load reduction and new wind monitoring scheme are modelled. | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | 1
|  | Connection of a Rowville–Springvale third circuit with an estimated cost of $53 million. | Thermal capacity of Rowville–Springvale and Springvale–Heatherton 220 kV circuits limits load growth or additional loads connected to Springvale or Heatherton Terminal Stations. | Monitored | post 2025 | $53 million |  | Existing control scheme for post-contingent load reduction and new wind monitoring scheme are modelled. | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | 2
|  | Implementing 5-minute ratings on the No 2 Keilor-Deer Park-Geelong 220 kV line. | Customer demand in surrounding areas to 2025 may need No 2 Keilor-Deer Park-Geelong 220 kV line five minute ratings to be enabled for up to four hours a year. | Complete | 2017 | NA | Section 2.3 | Included in the 2016 NTNDP studies. | Main Grid | Possible non-network solution applicable
| Appendix A.5 | Connection of a second 220kV line (Keilor – Geelong No.1) at Deer Park at an estimated cost of $12 million. | Customer demand in surrounding areas may exceed No 2 Keilor-Deer Park-Geelong 220 kV line five minute ratings post 2025. | Monitored | post 2025 | $12 million | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | 3
| Section 2.5, Section 3.3.2 Section 3.4.1 & Appendix A.3 | The Fishermans Bend synchronous condenser was fully decommissioned in September 2015. AusNet Services proposes decommissioning the Brooklyn and Templestowe synchronous condensers fully no later than 2017. | NA | Committed | 2015-2017 | NA | AusNet Services Asset Renewal Plan | Decreased minimum demand and synchronous condenser retirements may require operational limitation of South West corridor voltages during low demand periods. | Main Grid | Not applicable.
| Section 3.4.1 | Install three 220/66 kV 225 MVA transformers at Brunswick Terminal Station. | Thermal capacity of 220/66 kV transformers at Richmond and West Melbourne terminal stations. | Committed | late 2016 | NA | Section 2.3 | Included in the 2016 NTNDP studies. | Local Network | RIT-T completed.
| Section 3.4.1 & Section 3.5 | New 220 kV Deer Park terminal station with installation of two 225MVA 220/66 kV transformers and connection to Keilor-Geelong 220 kV No.2 circuit. | Thermal capacity limitations on Keilor 220/66 kV transformers. Offload Altona, Brooklyn, and Keilor terminal stations due to increased demand in the area. | Committed | late 2017 | NA | Section 2.3 & Section 2.4 | Included in the 2016 NTNDP studies. | Local Network | RIT-T completed.
| Appendix A.5 | Installation of a second 500/220 kV 1,000 MVA transformer at Cranbourne with an estimated cost of $38.8 million. | Rowville & Cranbourne A1 500/220 kV transformers rating limits increased demand in Eastern Metropolitan Melbourne. | Monitored | post 2025 | $38.8 million | "DSN Limitation Detail" Supplementary Information Workbook: Greater Melbourne and Geelong | This limitation was not identified in the NTNDP | Main Grid | Not applicable.
|  | Replacement of the existing (South Morang H1 330/220 kV) transformer with a higher rated unit in conjunction with AusNet Services’ asset replacement program. | South Morang H1 330/220 kV transformer rating limits increased demand in Metropolitan Melbourne and/or increased import from NSW. | Monitored | post 2025 (but condition expected to require replacement in 2018) | $34 million | Section 3 | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | 4
|  | Install an automatic load shedding control scheme to enable the use of five minute line rating. New (third) 500/220 kV transformer at Rowville, with an estimated cost of $39.8 million, plus any fault level mitigation works. | South Morang–Thomastown No.1 and No.2 220kV line rating limits load growth around the Melbourne Metropolitan area and/or increased export to NSW. | Monitored | post 2025 | $39.8 million | "DSN Limitation Detail" Supplementary Information Workbook: Greater Melbourne and Geelong | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | 5
| Section 3.4.4 & Appendix A.5 | New 500/330 kV transformer at South Morang, a Braking resistor at Loy Yang, and uprating of the South Morang–Dederang 330 kV lines. The total cost of these upgrades is expected to be approximately $72 million. The first two components are expected to be contestable. | The South Morang 500/330 kV F2 transformer rating, interconnected system transient stability performance, and the South Morang–Dederang thermal rating jointly limit the export capability from Victoria to New South Wales. | Monitored | post 2025 | $72 million | Section 2.3 & "DSN Limitation Detail" Supplementary Information Workbook: Greater Melbourne and Geelong | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Not applicable. | 6
Regional Victoria | Section 2.6 & Section 3.4.1 | Installation of a new Moorabool-Ballarat 220 kV circuit on the existing tower | Thermal capacity limitations on Moorabool–Ballarat 220 kV circuits | Committed | early 2017 | NA | Section 2.3 | Included in the 2016 NTNDP studies. | Main Grid | RIT-T completed.
| Section 2.6 & Section 3.4.1 | An automatic bus-splitting control scheme at Challicum Hills (Buangor) 66 kV substation | Constraints on the Ballarat - Horsham 66 kV (distribution) lines for outage of Horsham-Waubra-Ballarat or Horsham-Red Cliffs 220kV lines: • Assessed line ratings reduced in 2014. They have now been reassessed as higher than originally, however they still have a market impact. | Committed | Nov 2016 | NA | Section 2.3 & "DSN Limitation Detail" Supplementary Information Workbook: Regional Victoria | Included in the 2016 NTNDP studies. | Local Network | NA
| Section 3.4.3 & Section 4.2 | • Minor line upgrades – upgrading terminal station line droppers and installing wind monitoring at a total cost of approximately $1.5 million. • A new 420 MVA single circuit line between Ballarat and Waubra costing about $21 million. • A new 1,000 MVA double circuit line, replacing the existing Ballarat–Waubra 220 kV line, at a total cost of approximately $37 million. • Reactive compensation on the Ballarat–Waubra 220 kV lines, costing about $3 million. • A grid-connected battery to moderate peak generation (see Section 4.2.2 for more details). | North West Victoria transmission capability may restrict new renewable generation connection output. | Proposed | Staged as justified by new generation installations | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | NA
| Section 3.4.1 & Section 3.5 | Establish a new terminal station at Ararat cut-in to Ballarat - Waubra - Horsham 220 kV line. Approximately 85km from Horsham. | Generation connection of Ararat Wind Farm (241 MW). | Committed | 2016-07-01 | NA | Section 2.4 | Included in the 2015 NTNDP studies. | Main Grid | NA
| Section 3.5 | Possible Bulgana Wind Farm cut-in to the network. | Generation connection of Bulgana Wind Farm (189 MW) | Proposed | TBA | NA | Section 2.4 | NA | Main Grid | NA
| Section 3.5 | Establish a new terminal station at Crowlands with possible cut-in to Ballarat - Waubra - Horsham 220 kV line. | Generation connection of Crowlands Wind Farm (82 MW) | Proposed | TBA | NA | Section 2.4 | NA | Main Grid | NA
| Section 3.5 | Possible Gannawarra Solar Farm cut-in to the network. | Generation connection of Gannawarra Solar Farm (300 MW) | Proposed | TBA | NA | NA | NA | Main Grid | NA
| Section 3.5 | Possible Kiata Wind Farm cut-in to the network. | Generation connection of Kiata Wind Farm (39 MW) | Proposed | TBA | NA | NA | NA | Local Network | NA
| Section 3.5 | Possible Murra Warra Wind Farm cut-in to the network. | Generation connection of Murra Warra Wind Farm (386 MW) | Proposed | TBA | NA | NA | NA | Main Grid | NA
| Appendix A.6 | Staged installation of additional reactive power support in Regional Victoria. | Inadequate reactive power support due to increased demand and/or decrease in power factor in Regional Victoria. | Monitored | post 2025 | see "Transmission Development" column | "DSN Limitation Detail" Supplementary Information Workbook: Regional Victoria |  |  | Load reduction or new generation in Regional Victoria, such as Bendigo, Kerang, Fosterville, Red Cliffs and Wemen Terminal Station.
|  | • Install an automatic load shedding control scheme to enable the use of five minute rating of the Bendigo–Fosterville–Shepparton 220 kV line, • Install a phase angle regulating transformer on the Bendigo–Fosterville–Shepparton 220 kV line at an estimated cost of $45 million, or • Up-rate the existing conductor from 82 ºC to 90 ºC at an estimated cost of $58.7 million. | Bendigo–Fosterville–Shepparton 220 kV line rating may limit increased demand in Regional Victoria and/or increased import from NSW. | Monitored | post 2025 | see "Transmission Development" column |  | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | • Install an automatic load shedding control scheme to enable the use of five minute rating of the Bendigo–Fosterville–Shepparton 220 kV line, • Install a phase angle regulating transformer on the Bendigo–Fosterville–Shepparton 220 kV line at an estimated cost of $45 million, • Replace the existing Dederang–Glenrowan 220 kV lines with a new double circuit line, or • Replace the existing Dederang–Shepparton 220 kV line with a new double circuit line at an estimated cost of $258 million. | Dederang–Glenrowan & Dederang-Shepparton 220 kV line ratings may limit increased demand in Regional Victoria and/or increased import from NSW. | Monitored | post 2025 | see "Transmission Development" column |  | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | Uprating Ballarat-Bendigo 220 kV line at an estimated cost of $42.5 million. | Ballarat–Bendigo 220 kV line rating may limit increased demand in Regional Victoria. | Monitored | post 2025 | $42.5 million |  | This limitation was identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
|  | • Install an automatic load shedding control scheme to enable the use of five minute ratings. • Replace the existing Bendigo–Kerang–Wemen–Red Cliffs 220 kV line with a new double circuit 220 kV circuit line at an estimated cost of $581.4 million. | Kerang–Wemen–Red Cliffs 220 kV line rating may limit significant load growth at the Kerang Terminal Station. | Monitored | post 2025 | $581.4 million |  | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable | Monitored | post 2024 | see "Transmission Development" column | NA | This limitation was not identified in the NTNDP | Main Grid | Possible non-network solution applicable
| Section 4 & AusNet Services Asset Renewal Plan | Richmond Terminal Station - Replace existing infrastructure with three 225 MVA 220/66 kV transformers, three breaker-and-half 220 kV GIS switchbays, four 66 kV GIS busses, 22 kV switchboard and associated protection and control systems. | Condition based replacement. | Committed | 2018 | $175 million | Section 3 | Condition based renewals - no change to 2016 NTNDP outcome | Local Network | Not applicable (network solution being implemented) | Committed | 2018 | $175 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Not applicable (network solution being implemented)
|  | West Melbourne Terminal Station - Replace 220/66kV transformers, 220kV switch bays, 66kV switch bays and all protection and control systems. Retire the 22 kV supply from WMTS. |  | Committed | 2021 | $119 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Committed | 2021 | $119 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
|  | Springvale Terminal Station - Replace B1, B2 and B3 220/66 kV transformers, five 220 kV minimum oil CBs and selected 66 kV CBs. |  | Proposed | 2021 | $77 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Proposed | 2021 | $77 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
|  | Keilor Terminal Station - Replace A2 and A4 transformers with 750MVA 500/220kV transformers and retire A3 transformer (subject to further studies). Replace B4 transformer with a 150MVA 220/66kV transformer. Install new transformer protection. |  | Proposed | 2025 | $70 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid & Local Network | Not applicable.
|  | Heatherton Terminal Station - Replace all three 150MVA 220/66 kV transformers, two 220 kV minimum oil CBs, eleven 66 kV bulk old CBs and associated protection and control systems |  | Committed | 2017 | $59 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution need to be investigated | Committed | 2017 | $59 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution need to be investigated
|  | Fishermans Bend Terminal Station Stage 1- Replace one minimum oil 220 kV CB, six 66kV bulk oil and three 66kV minimum oil CBs. |  | Committed | 2018 | $17 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Committed | 2018 | $17 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
|  | Transmission Line Structure, Conductor and Insulator Replacement |  | Proposed | 2025 | $35 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2022 | $18 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| Section 3 | South Morang Terminal Station - Stage 1 - Replace the H2 transformer with a new 750 MVA 330/220 kV transformer and retain the existing H2 FERRANTI 330/220kV transformer as a cold spare transformer. |  | Committed | 2018 | $34 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2018 | $34 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| Section 3 | Fishermans Bend Terminal Station Stage 1- Replace one minimum oil 220 kV CB, six 66kV bulk oil and three 66kV minimum oil CBs. |  | Committed | 2018 | $17 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Committed | 2018 | $17 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 3 | Fishermans Bend Terminal Station Stage 2- Replace B1 and B3 transformers with two 150 MVA 220/66 kV transformers. Replace 220kV and 66kV circuit breakers. |  | Proposed | 2020 | $37 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Proposed | 2020 | $37 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 3 | Templestowe Terminal Station - Replace B2 220/66 kV transformer, two 66 kV minimum oil CBs and thirteen 66 kV bulk oil CBs, and install new protection and control systems. |  | Proposed | 2020 | $34 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Proposed | 2020 | $34 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| Section 4 & AusNet Services Asset Renewal Plan | West Melbourne Terminal Station - Replace three 150 MVA 220/66 kV transformers (B1, B2 & B3), seven 220 kV switch bays, 16 x 66 kV switch bays, 22 kV switch boards and all protection and control systems with GIS located in buildings. |  | Committed | 2021 | $119 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Committed | 2021 | $119 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
|  | Springvale Terminal Station - Replace B1, B2 and B3 220/66 kV transformers, five 220 kV minimum oil CBs and selected 66 kV CBs. |  | Proposed | 2021 | $77 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable | Proposed | 2021 | $77 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Local Network | Possible non-network solution applicable
| AusNet Services Asset Renewal Plan | DDTS - Replace the H1 ACEC 225/340MVA 330/220kV transformer |  | Committed | 2015 | $17 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2015 | $17 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | RWTS - Replace nine 220kV bulk oil CBs and provide new CB management system |  | Committed | 2015 | $21 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2015 | $21 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HWPS - Replace eleven bulk oil CBs |  | Committed | 2016 | $8 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2016 | $8 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | YPS - Replace seven minimum oil 220kV CBs and the associated oil CTs |  | Committed | 2016 | $21 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2016 | $21 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Transmission conductor replacement - 80km of ground-wire and conductor |  | Committed | 2017 | $7 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2017 | $7 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Transmission line insulator replacement on Priority 2 insulators (4385 strings from selected lines with 20mm pins and the rest of 16-mm pin insulators) |  | Committed | 2017 | $5 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Committed | 2017 | $5 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HWPS - Replace the remaining seven 220kV Bulk Oil CBs and install remote operated isolators |  | Proposed | 2018 | $24 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2018 | $24 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Replace glass and porcelain insulator strings and components with composite insulators. |  | Proposed | 2020 | $6 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2020 | $6 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | LYPS - Replace 500kV circuit breakers |  | Proposed | 2021 | $4 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2021 | $4 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HWTS - Replace 500kV circuit breakers |  | Proposed | 2021 | $6 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2021 | $6 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | HYTS - Replace two 500kV and two 275 kV CBs |  | Proposed | 2018 | $8 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2018 | $8 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | WBTS-HOTS Line - Install 141km of Optical Ground Wire (OPGW) on WBTS-HOTS Line |  | Proposed | 2022 | $14 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2022 | $14 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | Line - Replace ground wire on selected transmission lines |  | Proposed | 2022 | $18 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2022 | $18 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| AusNet Services Asset Renewal Plan | RCTS-HOTS Line - Install 277km of Optical Ground Wire (OPGW) on RCTS-HOTS Line |  | Proposed | 2024 | $28 million | AusNet Services Asset Renewal Plan | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2024 | $28 million | NA | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
| Section 3 | Moorabool Terminal Station - Replace 500kV and 220kV circuit breakers. |  | Proposed | 2020 | $8 million | Section 3 | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable. | Proposed | 2020 | $8 million | Appendix G | Condition based renewals - no change to 2015 NTNDP outcome | Main Grid | Not applicable.
Note on D11: [1] Voltage unbalance monitoring equipment is now installed in the area. The data from the equipment will be used to review the magnitude of the limitation and possibly calibrate the simulation model to review the existing constraints. AEMO expects to conduct this review in 2015.

## ElectraNet 2016 APR Projects
2016 APR Reference |  | Transmission Development | Limitation Addressed | 2016 APR Project Status | 2016 APR Anticipated Timing | 2016 APR Indicative Cost ($ million) | 2015 APR Reference | AEMO categorisation | 2016 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Section 4.3 | Table 4-3 | New Interconnector between South Australia and New South Wales or Victoria: Build a new single or double circuit 275 kV line from Robertstown to Monash, and establish a new interconnector to New South Wales or Victoria Alternative routes for a new interconnector could be from Tungkillo in South Australia to Horsham in Victoria, or a 500 kV high capacity interconnector from Davenport in South Australia to Mount Piper in New South Wale | Augmentation may reduce losses; support development of renewable generation; improve export/import capability; and enhance reliability to the Riverland in South Australia, and Western Victoria | Potential | Subject to market benefit assessment | 300-700 | Table 3-4 | Monitoring limitation > $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone. | Main Grid | Not applicable
Section 4.3 | Table 4-4 | Davenport - Brinkworth - Para 275 kV: Rebuild Davenport–Brinkworth–Para 275 kV as a high capacity 275 kV AC double circuit line with twin conductors. | Increase in renewable generation and loads in the Mid North or Eyre Peninsula. 1200 MW capacity increase. | Potential | Subject to market benefit analysis | 300-400 | Table 3-5 | Monitoring limitation > $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
Section 4.3 | Table 4-4 | Strengthen Mid North 275 kV network: Various line uprating and dynamic line ratings dependent on generator developments. | Increase in renewable generation in the Mid North or Eyre Peninsula. Capacity increase depending on the location of generation and local network capability. | Potential | Subject to market benefit assessment | <5 | Table 3-5 | Monitoring limitation < $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone. | Main Grid | Not applicable
Section 4.3 | Table 4-4 | Tie Davenport–Robertstown 275 kV at Belalie substation. | Increased renewable generation on the Mid North network. Capacity increase depending on the location of generation and local network capability. | Potential | Subject to market benefit assessment | 10-20 | Table 3-5 | Monitoring limitation > $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
Section 4.3 | Table 4-4 | Tie Robertstown–Para 275 kV at Tungkillo substation. | Increased renewable generation on the Mid North network. Capacity increase depending on the location of generation and local network capability. | Potential | Subject to market benefit assessment | 5-10 | Table 3-5 | Monitoring limitation > $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
Appendix G | Table G-1 | Install 50% series compensation on the South East – Tailem Bend 275 kV lines; remove rating restrictions from South East 275 kV and 132 kV lines; implement a run-back control scheme for Lake Bonney Wind Farm to manage light load and high wind condition; (AusNet Services)install a third 500/275 kV transformer at Heywood | Heywood Interconnector transfer limitations due to system stability and thermal constraints | Committed | July 2016 | 35-45 (ElectraNet's cost only) | Table 7-6 | Committed augmentation > $6 million | Included in the 2016 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
Appendix G | Table G-1 | Dalrymple Substation: Install a second 25 MVA 132/33 kVtransformer, extend and reconfigure 132 kV bus. | ETC reclassification to Category 2 required N-1 transformer redundancy at Dalrymple connection point from 1 December 2016. | Committed | Nov 2016 | 8-10 (ElectraNet costs only) | Table 7-6 | Committed augmentation > $6 million | Included in the 2016 NTNDP studies. | Local Network | Not applicable ( network solution being implemented)
Appendix G | Table G-1 | Weather Stations for Dynamic Line Rating Install modern weather stations at various monitoring locations to facilitate the future implementation of dynamic line ratings on critical circuits | Deterministic line ratings in various parts of the network can cause constraints at times of high demand or high wind generation. | Committed | 2016 | <5 | Table 7-6 | Committed augmentation < $6 million | Local supply/network need - not modelled in NTNDP studies. | Local Network | Not applicable ( network solution being implemented)
Appendix G | Table G-1 | Uprate the South East – Tailem Bend 275 kV lines to 120˚C line clearances | Congestion on the 275 kV network between South East and Tailem Bend restricts transfer capability between South Australia and Victoria across the Heywood Interconnector, following completion of the Heywood Interconnector Upgrade in 2016. | Committed | 2016 | <5 | NA | Committed augmentation < $6 million | Included in the 2016 NTNDP studies. | Main Grid | Potential local generation support and demand side management initiatives.
Appendix G | Table G-1 | Uprate the Tailem Bend – Tungkillo 275 kV line and the Tailem Bend – Mobilong 132 kV line to 100˚C line clearances | Congestion on the 275 kV and 132 kV networks north of Tailem Bend restricts transfer capability between South Australia and Victoria across the Heywood Interconnector, following completion of the Heywood Interconnector Upgrade in 2016. | Committed | 2017 | <5 | NA | Committed augmentation < $6 million | Included in the 2016 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
Appendix G | Table G-1 | Uprate the Robertstown – North West Bend #2 and the North West Bend – Monash #2 132 kV lines to 100˚C line clearances | Congestion on the 132 kV network between Robertstown and Monash restricts exports from South Australia to Victoria across the Murraylink Interconnector | Committed | 2017 | <5 | Table 7-6 | Committed augmentation < $6 million | Included in the 2016 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
Appendix G | Table G-1 | Uprate the Waterloo East – Robertstown 132 kV line to 100˚C line clearances | Congestion on the 132 kV network between Waterloo East and Robertstown restricts exports from South Australia to Victoria across the Murraylink Interconnector. | Committed | 2018 | <5 | NA | Committed augmentation < $6 million | Included in the 2016 NTNDP studies. | Main Grid | Not applicable ( network solution being implemented)
Appendix G | Table G-1 | Reactive Plant Control Systems Install a coordinated control scheme to better utilise existing reactive plant and voltage control facilities to minimise system constraints whilst managing system voltage levels | Difficulty with manually controlling the increasing number of reactive plant and voltage control facilities across the Main Grid effectively. | Proposed | 2018 | <5 | Table 7-6 | Monitoring limitation < $6 million (equivalent to proposed) | Reactive power support - not modelled in NTNDP studies. | Main Grid | Not applicable
Appendix G | Table G-1 | Design and build a grid-connected, utility scale energy storage system at Dalrymple that will help to manage frequency related system security issues, as well as improve the reliability of supply for customers at Dalrymple connection point and provide other market benefits | Large scale renewable energy sources connected to the transmission network are intermittent and do not contribute to frequency control to the same extent as conventional generation, causing potential frequency control issues that may threaten South Australian system security at times when few conventional generators are dispatched. | Proposed | 2019 (Subject to receipt of ARENA grant) | 10-20 | NA | Monitoring limitation > $6 million (equivalent to proposed) | Demonstration project - not modelled in NTNDP studies | Local Network | Not applicable
Appendix G | Table G-1 | Install dynamic 275 kV reactive support at Davenport substation | Potential network adequacy and security limitations resulting from the withdrawal of the network voltage control service provided by Northern Power Station at the Davenport 275 kV substation. | Proposed | 2019 | Up to 60 | NA | Monitoring limitation > $6 million (equivalent to proposed) | Reactive power support - not modelled in NTNDP studies. | Main Grid | Not applicable
Appendix G | Table G-1 | Establish a new 132 kV exit point on the Para – Roseworthy 132 kV line at Gawler East to provide supply to a 132/11 kV distribution substation that will be constructed and owned by SA Power Networks. | Significant residential developments near Gawler that cannot be supplied by SA Power Networks’ existing distribution network in the area. | Proposed | 2019 | 3-6 (ElectraNet costs only) | New | Monitoring limitation < $6 million (equivalent to proposed) | Project driven by distribution network limitation - not modelled in NTNDP studies | Main Grid | Not applicable
Appendix G | Table G-1 | Construct new double circuit 132 kV lines from Cultana to Yadnarie and from Yadnarie to Port Lincoln, and decommission the existing 132 kV lines | Significant lengths of conductor on the Whyalla to Yadnarie and the Yadnarie to Port Lincoln 132 kV lines are in poor condition and need to be replaced | Proposed | 2020 | 100-150 | New | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Main Grid | Potential local generation support and demand side management initiatives.
Appendix G | Table G-1 | Reinforce the Eyre Peninsula by constructing a double-circuit 275 kV line from Cultana to a location near Yadnarie, initially strung only on one side; establish a 275/132 kV substation near Yadnarie; provide supply to the new mining load(s) via 275 kV and 132 kV supplies from the new substation | Subject to connection of a new large mining load on the Eyre Peninsula, at high demand times the Middleback – Yadnarie 132 kV line will be overloaded under normal conditions and one Cultana 275/132 kV transformer will be overloaded for an outage of the other. | Potential (under SA Mining Growth Scenario) subject to load connection application. | Subject to step load connection | 150-300 | Table 7-6 | Monitoring limitation > $6 million (equivalent to proposed) | Possible future project subject to load connection - not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Appendix G | Table G-1 | Apply Dynamic Line Ratings to Davenport to Robertstown 275 kV Lines Increase the capacity of the 275 kV lines between Davenport and Robertstown by upgrading various items of plant (e.g. remove line traps, replace current transformers, change current transformer ratios) and apply dynamic line ratings to these lines. | Subject to connection of new wind farms to the 275 kV lines between Davenport and Robertstown, those 275 kV lines may be overloaded at times of high wind generation | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | <5 | Table 7-6 | Monitoring limitation < $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. | Main Grid | Not applicable
Appendix G | Table G-1 | Increase the capacity of the Robertstown 275/132 kV transformers by upgrading various items of plant and apply short term loading limits to the Robertstown 160 MVA 275/132 kV transformers. | Subject to connection of new wind farms to the 275 kV lines between Davenport and Robertstown, one of the Robertstown 160 MVA 275/132 kV transformers may be overloaded for an outage of the other transformer | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | <5 | Table 7-6 | Monitoring limitation < $6 million (equivalent to proposed) | Possible future project subject to wind farm development. Not captured in the 2016 NTNDP. | Main Grid | Not applicable
Appendix G | Table G-1 | Implement a control scheme that will reconfigure the Mid North 132 kV network at times of high wind farm generation by opening and closing 132 kV circuit breakers as required to target reduced congestion under various operating conditions | Subject to connection of new wind farms to the Mid North 132 kV lines or the 275 kV lines between Davenport and Para (the “East” and “West” circuits), the thermal rating of various 132 kV lines in the Mid North may constrain wind farm generation dispatch, based on the need to avoid overloading lines following a single credible contingency | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections | <5 | Table 7-6 | Proposed replacement < $6 million | Limitation may arise during times of high renewable generation in NSA zone. | Main Grid | Not applicable
Appendix G | Table G-1 | Increase the capacity of the 275 kV lines between Tungkillo and Heywood by upgrading various items of plant (e.g. remove line traps, replace current transformers, change current transformer ratios) and apply dynamic line ratings to these lines | Subject to the connection of new wind farms in South Australia, increased congestion on the 275 kV network between Tungkillo and Heywood is forecast to limit exports from South Australia to Victoria | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections / market benefit assessment | <5 | Table 7-6 | Monitoring limitation < $6 million (equivalent to proposed) | Possible future project subject to wind farm development. Not captured in the 2016 NTNDP. | Main Grid | Not applicable
Appendix G | Table G-1 | Increase the capacity of the Tungkillo to Tailem Bend 275 kV corridor by stringing the vacant 275 kV circuit between Tungkillo and Tailem Bend (and establish a third 275 kV circuit between Para and Tungkillo) | Subject to the connection of new wind farms in South Australia, increased congestion on the 275 kV network between Tungkillo and Tailem Bend is forecast to restrict exports from South Australia to Victoria across the Heywood interconnector | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections / market benefit assessment | 25-50 | Table 7-6 | Monitoring limitation > $6 million (equivalent to proposed) | Limitation may arise during times of high VIC-SA (Heywood) interconnector transfer.. | Main Grid | Not applicable
Appendix G | Table G-1 | Install two switched 15 Mvar 132 kV capacitor banks at Monash | Subject to the connection of new wind farms in South Australia, increased congestion on the 132 kV network between Robertstown and Monash is forecast to restrict exports from South Australia to Victoria across the Murraylink interconnector | Potential (under SA Renewable Generation Expansion Scenario) subject to generation connection application. | Subject to new wind farm connections / market benefit assessment | 5-10 | Table 7-6 | Monitoring limitation > $6 million (equivalent to proposed) | Limitation may arise during times of high renewable generation in NSA zone, depending on concentration level of future generation developments within the zone. Line uprating is modellled in 2016 NTNDP, but not the capactors. | Main Grid | Not applicable
Appendix G | Table G-2 | Tailem Bend Substation Upgrade Extend the Tailem Bend substation to accommodate an additional 275 kV diameter, with two circuit breakers, associated plant, secondary systems and rearrange 275 kV line exits. | Substandard circuit breaker arrangement at South East substation constrains the Heywood Interconnector and places network security and reliability at risk. | Committed | 2016 | 8-12 | Table 7-7 | Committed augmentation > $6 million | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Upper North Voltage Control Scheme Install automated regional voltage control schemes for Eyre Peninsula and Upper North regions. | Changing generation patterns have resulted in complex voltage interactions on the Eyre Peninsula and Upper North regions leading to potential violations of voltage limits stipulated in the Rules and connection agreements. | Committed | 2016 | <5 | Table 7-13 | Committed augmentation < $6 million | For security and compliance - not within the 2016 NTNDP scope. | Local Network | Not applicable
Appendix G | Table G-2 | Install, upgrade or replace transformer oil containment systems and associated equipment at various sites, where assessment indicates a clear need. | Transformer oil containment systems need refurbishment to maintain compliance with environment protection regulations. | Committed | 2018 | 5-10 | Table 7-7 | Committed replacement > $6 million | For security and compliance - not within the 2016 NTNDP scope. | Asset Replacement
Appendix G | Table G-2 | Install Eyre Peninsula islanding control scheme to minimise interruptions to customers | Shutdown of regionally important substations required during outages of Cultana to Yadnarie 132 kV transmission line | Proposed | 2018 | <5 | Table 7-7 | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Redesign and replace the Murraylink Control Scheme | Outages and constraints on the Murraylink Interconnector | Proposed | 2018 | <5 | Table 7-7 | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Construct a new Backup Control and Data Centre to meet current physical and electronic security requirements | Existing backups for ElectraNet’s control centre and data centre requirements require improvement to address emerging security threats | Proposed | 2018 | 4-8 | NA | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-2 | Create a high voltage switching training facility to improve training standards across all aspects of high voltage switching | High voltage switching training conducted on live network results in network and asset performance impacts and training limitations | Proposed | 2018 | 4-8 | NA | Proposed replacement > $6 million | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Install status indication on isolators and earth switches where there currently is none | High voltage hazard due to lack of remote visibility of manually operated isolator and earth switch status | Porposed | 2018 | <5 | NA | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Replace or refurbish mechanical and electrical isolation lock-off points on all motorised air insulated isolators | High voltage hazard due to risk of failure of mechanical or electrical lock-off points on motorised air insulated high voltage isolators | Proposed | 2019 | 10-15 | NA | Proposed replacement > $6 million | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Install a switched 50 Mvar 275 kV reactor at Templers West | Following a single contingency of an in-service generator, steady-state voltage levels on the South Australian transmission system may breach 110% at minimum demand times from 2023-24 | Proposed | 2023 | <5 | NA | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Install an additional 132 kV circuit breaker and associated equipment at Blanche substation | Generation constraints and/or loss of load during plant outages at Blanche substation | Proposed | 2018-2023 | <5 | Table 7-7 | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Local Network | Not applicable
Appendix G | Table G-2 | Install a single 275 kV circuit breaker and associated equipment between the 275 kV busses at Robertstown substation | Either Murraylink interconnection or generation north of Robertstown must be constrained during scheduled maintenance of centre breakers or associated plant at Robertstown substation | Proposed | 2018-2023 | 5-10 | Table 7-7 | Monitoring limitation > $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Install a monitoring and protection scheme for the neutral earthing reactors and resistor installations across the network | Risk of thermal damage to neutral earthing reactors and resistors, and consequent unsafe operating conditions and risk of damage to larger plant | Proposed | 2018-2023 | <5 | NA | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Appendix G | Table G-2 | Implement full single pole reclosing capability on the 132 kV circuits in the Mid North region | Both Mintaro and Angaston generators are constrained off during 132 kV outages that result in these generators being radialised | Potential | 2018-2023 | <5 | Table 7-7 | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Local Network | Not applicable
Appendix G | Table G-2 | Implement full single pole reclosing capability on the 132 kV circuits in the South East region | Both Ladbroke Grove and Snuggery generators are constrained off during 132 kV outages that result in these generators being radialised | Potential | 2018-2023 | <5 | Table 7-7 | Monitoring limitation < $6 million (equivalent to proposed) | For security and compliance - not within the 2016 NTNDP scope. | Local Network | Not applicable
Appendix G | Table G-3 | Brinkworth to Mintaro Line Refurbishment Replace all porcelain disc insulators on Brinkworth to Mintaro 132 kV line, achieving a 15-year life extension. Alternative option: assess and replace insulators on sample-based testing results. | Porcelain disc insulators on Brinkworth to Mintaro 132 kV line at end of life, leading to high failure rate and fire start risk | Committed | 2016 | 6-8 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Tailem Bend to Keith No.2 Line Refurbishment Replace all porcelain disc insulators on Tailem Bend to Keith #2 132 kV line, achieving a 15-year life extension. Alternative option: assess and replace insulators on sample-based testing results. | Porcelain disc insulators on Tailem Bend to Keith #2 132 kV line at end of life, leading to high failure rate and fire start risk | Committed | 2016 | 5-8 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace the existing SVC thyristor valves and thyristor valve cooling, protection and control systems for both SVCs at Para substation with modern-day equipment. Install circuit breakers and associated plant to connect both SVCs to east and west busbars. Install a 50 Mvar reactor at Para substation to provide reactive support during SVC outages. | Condition of the existing Para SVCs secondary systems and the lack of spare parts make maintenance impossible and manufacturer support is largely withdrawn. Failure would severely constrain interconnector transfer capacity | Committed | 2016 | 20-25 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Morgan to Whyalla pumping station #2 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Morgan to Whyalla pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2016 | 10-15 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Morgan to Whyalla pumping station #1 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Morgan to Whyalla pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2016 | 10-14 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Morgan to Whyalla pumping station #3 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Morgan to Whyalla pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2016 | 10-13 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Morgan to Whyalla pumping station #4 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Morgan to Whyalla pumping station #4 primary plant at end of technical life; site not aligned with current environmental practices and company practices | Committed | 2016 | 10-13 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Mannum to Adelaide pumping station #2 supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Mannum to Adelaide pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2017 | 10-14 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Mannum to Adelaide pumping station #3 supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Mannum to Adelaide pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2017 | 10-14 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Rebuild the Mannum to Adelaide pumping station #1 supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Mannum to Adelaide pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2017 | 15-20 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Millbrook Pump Station Rebuild the Millbrook supply site to modern-day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Millbrook pumping station primary plant at end of technical life; site not aligned with current environmental practices and company policies | Committed | 2017 | 12-16 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Para to Davenport Line Hazard Mitigation Replace load releasing cross arms and all porcelain disc insulators on Para-Brinkworth-Davenport 275 kV line, achieving a 15-year life extension. Alternative options: rebuild 275 kV line in an adjacent easement and retire old line; or replace load releasing cross arms with standard cross arms (and also strengthen the towers) and assess and replace insulators on samplebased testing results. | Load releasing cross arms on Para-Brinkworth-Davenport 275 kV line are a safety risk and inadequate for access and maintenance. Porcelain disc insulators at end of life, leading to high failure rate and fire start risk | Committed | 2018 | 40-60 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Program of unit asset replacements at multiple substations | Substation assets have been identified with high failure rates, safety risks or assessed to be at the end of their technical and economic lives. | Committed | 2013-2018 | 45-55 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Baroota Substation Upgrade Replace plant in poor condition at Baroota substation and implement flood mitigation measures. Retain only the existing single 10 MVA 132/33 kV transformer. | The majority of the primary equipment at Baroota substation is in poor condition | Proposed | 2017 | 5-10 (ElectraNet costs only) | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace substation lighting and associated infrastructure at sites where hazards exist. | Review of substation lighting identified compliance issues and safety hazards with some existing lighting systems. Cost and risks assessments were undertaken for the various lighting functions to determine the optimal solution to meet the requirements under the WHS Act and Australian Standards | Proposed | 2018 | 4-8 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace AC auxiliary supply equipment, switchboards and cabling at 13 substations. | AC auxiliary supplies at older substations are not compliant with current Australian standards and have some safety hazards and operational deficiencies | Proposed | 2018 | <5 | Table 7-8 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Impement a planned replacement program to remove battery chargers from service and replace with modern, fit-for-purpose equipment. Alternative option: replace battery chargers on failure | A number of substation battery charger units have reached the end of their practical life. Also, spare parts are not available | Proposed | 2018 | <5 | Table 7-8 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace obsolete online asset condition monitoring equipment. | Many items of online condition monitoring equipment are nearing the end of their usable lives (12-20 years old) and are exhibiting high failure rates | Proposed | 2018-2023 | 8-12 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Implement a program of transmission line support system refurbishment to renew line asset components and extend line life | Transmission line support systems (towers, poles) components at end-of-life, leading to a high failure rate, and safety and network availability risk | Proposed | 2018-23 | 8-10 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Implement a program of transmission line insulator system refurbishment to renew line asset components and extend line life | Transmission line insulator systems at end-of-life, leading to a high failure rate, and safety and network availability risk Implement a program of transmission line insulator system refurbishment to renew | Proposed | 2018-24 | 50-70 | Table 7-8 | Committed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Implement a program of transmission line conductor and earthwire refurbishment to renew line asset components and extend line life | Transmission line conductor and earthwire components at end-of-life, leading to a high failure rate, and safety and network availability risk | Proposed | 2018-25 | 10-20 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Program of unit asset replacements at various substations. | Substation assets have been identified with high failure rates, safety risks or assessed to be at the end of their technical and economic lives | Proposed | 2018-2023 | 30-45 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace 400-500 protection scheme relay assets. Alternative option: replace assets on failure. | Various individual substation protection systems have been assessed to be at the end of their technical and economic lives. Increased risk of failure could cause safety and reliability issues | Proposed | 2018-2023 | 30-40 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace obsolete online asset condition monitoring equipment. | Many items of online condition monitoring equipment are nearing the end of their usable lives (12-20 years old) and are exhibiting high failure rates | Proposed | 2018-2023 | 10-15 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace the existing transformers with two new 132/33 kV transformers at Mannum substation. Alternative option: replace assets on failure. | Mannum transformers 1 and 2 have been assessed to be at the end of their technical lives and at high risk of failure | Proposed | 2018-2023 | <5 | Table 7-8 | Proposed replacement < $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Replace the existing 50 MVA transformer with a new 25 MVA 132/33/11 kV transformer at Mount Gambier substation. Alternative option: replace assets on failure. | Mount Gambier transformer 1 has been assessed to be at the end of its technical life and at high risk of failure | Proposed | 2018-2023 | 4-8 | Table 7-8 | Proposed replacement > $6 million | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Appendix G | Table G-3 | Reinforce the Yorke Peninsula by constructing a single circuit 275 kV line from Blyth West to Hummocks and install a single 200 MVA 275/132 kV transformer at Hummocks substation | Subject to connection of a new large mining load on the Yorke Peninsula, at high demand times when either the Bungama – Hummocks or the Waterloo – Hummocks 132 kV line is out of service, the other line may be overloaded and it may not be possible to maintain adequate voltage levels on Yorke Peninsula. | Potential (under SA Mining Growth Scenario) subject to load connection application. | Subject to step load connection | 40-55 | Table 7-12 | Monitoring limitation > $6 million (equivalent to proposed) | Possible future project subject to load connection - not captured in the 2016 NTNDP. | Main Grid | Potential local generation support and demand side management initiatives.
Section 7.1.1 | Table 7-1 | Munno Para 275 kV Injection: Establish Munno Para substation and install a single 225 MVA 275/66 kV transformer supplying into the Northern Suburbs. | Load growth in the Northern Suburbs overloads SA Power Networks’ 66 kV network. | Completed | August 2015 | Not stated | Table 7-6 |  | Included in the 2016 NTNDP studies. | Local Network | Not applicable (this project has been completed)
Section 7.1.1 | Table 7-1 | Uprate the Robertstown – North West Bend #1 132 kV line to 100 ˚C line clearances and implement dynamic ratings on these lines. | Robertstown-North West Bend #1 132 kV line overloaded for loss of Robertstown-MWP3-MWP2-MWP1 - North West Bend #2 132 kV line at high demand times, as Western Victorian 220 kV network is unable to support Murraylink transfer into South Australia at times of high Victorian demand | Completed | October 2015 | Not stated | Table 7-6 |  | Included in the 2016 NTNDP studies. | Main Grid | Not applicable (network solution being implemented)
Section 7.1.1 | Table 7-1 | South East circuit breaker (CB) upgrade Install additional circuit breakers and associated switchgear, metering and protection at South East substation. | Substandard circuit breaker arrangement at South East substation constrains the Heywood Interconnector and places network security and reliability at risk. | Completed | December 2015 | Not stated | Table 7-7 |  | For security and compliance - not within the 2016 NTNDP scope. | Main Grid | Not applicable
Section 7.1.1 | Table 7-1 | Mt Gunson 132/33 kV connection point Replacement: Replace selected end-of-life plant at Mt Gunson substation with modern-day equipment and install a new 10 MVA 132/33 kV transformer. Alternative option: rebuild entire substation adjacent to existing substation. | Mount Gunson substation plant at end of technical life; 132/33 kV transformer condition assessment indicates replacement is required. | Completed | June 2015 | Not stated | Table 7-8 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 7.1.1 | Table 7-1 | Neuroodla 132/33 kV Connection Point Replacement: Rebuild Neuroodla substation within the existing substation site, installing a new 10 MVA 132/33 kV transformer and modern-day equipment. Alternative options: replace selected substation plant based on condition or rebuild entire substation adjacent to existing substation. | Neuroodla substation at end of technical life; 132/33 kV transformer condition assessment indicates replacement is required. | Completed | July 2015 | Not stated | Table 7-8 |  | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 7.1.1 | Table 7-1 | Para Unit Asset Replacements: Replace the 275 kV, 132 kV and 66 kV secondary systems, associated telecommunications systems, control buildings and selected primary plant at Para substation. The project scope and schedule have been extended to include unit asset replacements required in the 2014-2018 period. Alternative options: refurbish individual assets, replace assets on failure, or rebuild substation. | Some primary plant and most secondary systems at Para substation are in poor condition, not to modern-day standards and are a security and reliability risk. The structural integrity of the existing control building is of concern. | Completed | March 2016 | Not stated | Table 7-8 |  | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 7.1.1 | Table 7-1 | Rebuild the Morgan to Whyalla pumping station #2 supply site to current day standards and replace the 132/3.3 kV transformers. Employ a standardised approach across all pumping station sites to realise design and operational efficiencies. | Morgan to Whyalla pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies | Completed | May 2016 | Not stated | Table 7-8 |  | Condition based renewals - not within the 2016 NTNDP scope. | Asset Replacement | Not applicable
Section 7.1.1 | Table 7-1 | Davenport Under-voltage Load Shedding scheme: An under-voltage load shedding scheme was implemented on the Olympic Dam exit at Davenport substation to mitigate risk of voltage collapse following closure of Northern Power Station | Risk of voltage collapse following closure of Northern Power Station | Completed | April 2016 | Not stated | NA |  | For security and compliance - not within the 2016 NTNDP scope. | Local Network | Not applicable
Note: Some projects with '2016 APR project status' of 'committed' may have been completed since publication of 2016 TAPR.
Note on I1: Matthew Armitage: New column in 2016

## Transgrid 2016 APR Projects
2016 APR Reference | Transmission Development | Limitation Addressed | 2016 APR Project Status | 2016 APR Anticipated Timing/Completion | AEMO categorisation | 2016 APR Indicative Cost ($ million) | 2016 NTNDP | Augmentation / Investment Type | Potential Non-Network Options (if applicable)
Section 3.3.1 | Redevelopment of Orange 132/66 kV Substation | Condition based replacement of Orange 132/66 kV Substation with additinoal 66 kV Capacitor | Committed | 2019 | Committed Asset Replacement > $6 million | 34.578 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.1 | Strategic Land Acquisition at Riley Street | For replacement of Haymarket substation around 2041 | Completed | 2016 | Completed Asset Replacement > $6 million | 20.8485 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.1 | Upper Tumut Switching Station Rehabilitation | Replacement of the secondary systems is programmed for completion progressively through to January 2015 | Completed | 2016 | Completed Asset Replacement > $6 million | 46.782 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.1 | Cooma Substation Replacement | A new Cooma 132/66 kV Substation will be established in close proximity to the existing substation. The existing Cooma Substation will be transferred to Essential Energy and converted to a 66/11 kV substation. | Completed | 2015-11-01 | Completed Asset Replacement > $6 million | 40.68 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.1 | Yanco Substation Refurbishment | The majority of the substation’s equipment is nearing the end of its serviceable life and will be replaced to maintain reliability of supply. | Completed | 2015-09-01 | Completed Asset Replacement > $6 million | 19.323 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.1 | Implement dynamic line ratings based on information obtained from weather stations | This is a market driven project which aims to capture market benefits arising from increased line ratings should favourable weather conditions occur. | Committed | Spring 2016 | Committed Augmentation > $6 million | 6.102 | No impact on 2016 NTNDP studies | Main Grid | Not applicable
Section 3.3.1 | Quality of Supply Monitoring | This project is so that they can measure, record and analyse aspects of the quality of supply at these customer connection points. | Committed | 2017-06-01 | Committed Augmentation > $6 million | NA | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 3.3.1 | Replace circuit breakers of shunt capacitor banks with point-on-wave closing control. | This project is needed to avoid the mal-operation or failure of customer equipment | Committed | 2018-01-01 | Committed Asset Replacement < $6 million | 5.085 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 3.2.2 | Provision of a 66 kV Line Switch bay at Beryl 132/66 kV Substation | Essential Energy plans to reinforce its network supplying Dunedoo and Coonabarabran. | Completed | 2015-09-01 | Completed Augmentation < $6 million | 1.017 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 3.2.2 | Provision of a 66 kV Transformer switch bay at Molong 132/66 kV Substation | The old Molong 66/11 kV substation needs to be retired due to its condition. | Completed | 2016-03-01 | Completed Asset Replacement < $6 million | 1.017 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 3.2.2 | Provision of a new 132 kV Line switch bay at Vineyard 330/132 kV Substation | The new precinct at Marsden Park does not have an existing electricity supply. Endeavour Energy has determined that a new 132 kV feeder from Vineyard is the preferred option to provide supply to a new area. | Completed | 2016-02-01 | Completed Augmentation < $6 million | 2.034 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 3.2.2 | Replacement of equipment at Sydney West 330/132 kV substation to ensure that the 132 kV fault rating is at least 38 kA | The existing fault level at Sydney West 132 kV switchyard is approaching the design fault level rating. | Completed | 2016-02-01 | Completed Asset Replacement < $6 million | 5.085 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Beaconsfield Transformer No 1 & No 2 replacement | Condition based replacement of one transformer, the other will not be replaced | Committed | Expected completion 2018 | Committed Asset Replacement > $6 million | 37.629 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 3.2.2 | Buronga 220 kV Substation - Replacement of X2 220 kV Reactor | Condition based replacement | Completed | 2015-07-01 | Completed Asset Replacement < $6 million | 5.085 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.2 | Broken Hill 220/22 kV Substation - Replacement of No 1 and No 2 Reactors | Condition based replacement | Completed | Winter 2016 | Completed Asset Replacement > $6 million | 9.153 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Orange 132/66 kV Substation Capacitors - Additional 66 kV capacitor bank | To be provided as part of condition based replacement works. | Committed | 2019 | Committed Augmentation > $6 million | NA | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 3.2.2 | Armidale 330/132 kV substation: SVC control system replacement | Condition based replacement | Completed | Sept 2015 | Completed Asset Replacement > $6 million | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Tamworth 132/66 kV substation: substation rebuild | Condition based replacement; the new substation is to be constructed on an adjacent site with two 120 MVA 132/66 kV transformers and with no 132 kV busbar initially | Committed | Early 2017 | Committed Asset Replacement > $6 million | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.2 | Kangaroo Valley 330 kV substation: Secondary System Replacement | Condition based replacement | Completed | 2016-02-01 | Completed Asset Replacement > $6 million | 6.102 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Sydney West 330/132 kV substation | Condition based replacement; replacement of the secondary systems | Committed | Mid 2016 | Committed Asset Replacement > $6 million | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Sydney North Secondary System Replacement | Condition based replacement | Committed | late 2018 | Committed Asset Replacement > $6 million | 42.714 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.2 | Sydney South 330 kV Substation - Replacement of all 415 V AC auxiliary supply systems | Condition based replacement | Completed | 2016-02-01 | Completed Asset Replacement > $6 million | 6.102 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Haymarket 330 kV substation - removal of SICAM (control and monitoring system) from GIS | Condition based removal | Committed | Mid 2016 | Committed Asset Replacement > $6 million | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Albury 132/22 kV substation: Secondary Systems Replacement | Condition based replacement | Committed | late 2016 | Committed Asset Replacement > $6 million | 11.187 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Burrinjuck to Yass 132 kV Transmission Line 970 Pole Replacements & installation of OPGW) | Condition based replacement | Committed | 2017 | Committed Asset Replacement > $6 million | 13.221 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Replacement of the Vales Point 330/132 kV substation | The replacement of Vales Point Substation is driven by the condition of the substation and its assets. The asset condition is based on assessments and testing carried out on the physical assets. A reduction in load would not defer the retirement dates. | Proposed | Expected completion: 2018 | Proposed Asset Replacement > $6 million | 44.748 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 3.4.1 | Development of southern supply to the ACT: - Condition of licence is to provide two geographically separate 330 kV supplies to the ACT - The first of which is the existing Canberra 330/132 kV substation - Establishment of a switching station at a suitable site together with associated 330 kV line connections - After review by the ACT gov, a site near Stockdill Drive is preferred | Jurisdictional reliability requirement | Proposed | Required by 2020 | Proposed Augmentation > $6 million | Not Available | Local Area Limitation - Not within scope of NTNDP | Main Grid | Not applicable
Section 3.3.1 | Wagga 132/66 kV substation: - replacement of No 1 and 3 132/66 kV 60 MVA transformers with 132/66 kV 120 MVA transformers - remove existing No 2 transformer - replace equipment identified as nearing end of serviceable life | Asset Condition – Condition assessments of Wagga 132 kV Substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed. This includes the No 2 and No 3 132/66/11 kV transformers. | Proposed | 2019-06-01 | Proposed Asset Replacement > $6 million | 52.884 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 3.4.1 | Supply to Beryl/Mudgee area: The provision of additional reactive support at Beryl substation by the addition of a 66 kV capacitor | voltage stability limitation in the network supplying Beryl is expected to emerge by summer 2015/16 | Proposed | Indicative date: summer 2016/17 | Proposed Augmentation < $6 million | 2.034 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 3.3.2 | Taree Substation 33 kV Switchyard Condition | Condition based replacement | Committed | 2017-09-01 | Committed Asset Replacement > $6 million | 9.153 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.2 | Taree 132/66/33 kV Substation: Secondary Systems Condition | Condition based replacement | Committed | 2017-09-01 | Committed Asset Replacement > $6 million | 26.442 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.2.2 | Haymarket 330 kV Substation Secondary Systems Replacement | Condition based replacement | Completed | 2015-08-01 | Completed Asset Replacement > $6 million | 9.153 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.5 | Cooma – Munyang 132 kV Line 97K Rehabilitation | Condition based replacement | Proposed | 2018 | Proposed Asset Replacement > $6 million | 15.255 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Coffs Harbour – Koolkhan 132 kV transmission line: pole replacements - Line 96H | Condition based replacement | Committed | 2018 | Committed Asset Replacement > $6 million | 14.238 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.1 | Installation of a Phase Shifting Transformer in the Tamworth-Gunnedah line 969 | Thermal constraints on 969 line when there is an outage of 968 line | Proposed | possible within 5 years | Proposed Augmentation > $6 million | 15 | Local Area Limitation - Not within scope of NTNDP | Local Network | Potential local generation support and demand side management initiatives.
Section 4.2.2 | Replacement of the Tamworth No 2 330/132 kV transformer with a 375 MVA unit (reduce Tamworth Tx from 3 to 2)` | Condition based replacement; No 2 330/132 kV 150 MVA transformer is nearing the end of its serviceable life. | Proposed | Indicative date: 2019 | Proposed Asset Replacement > $6 million | 11 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 4.1.1 | Sydney South - Beaconsfield capacity: - preferred option is to perform a detailed assessment of the cable installation by testing oil samples at a large number of points along the entire cable route, installing soil property and condition monitors. | Recent investigations into the condition of cable 41 have found that the cable backfill has degraded, reducing the thermal performance of the cable | Proposed* RIT-T PSCR | Within 5 Years | Proposed* RIT-T PSCR Augmentation > $6 million | 0.5 - 3 (Montoring System only) | Due to the noted cable degradation issues, it is likely that there is a need to monitor cable performance to secure supply to the Sydney metropolitan area. | Main Grid | It is not expected that the required levels of demand management would be available to cover the loss of cable 41 capacity, particularly as this would be required in addition to demand management being sought to compensate for the expected 132 kV cable retirements.
Section 3.4.1 | Connection of Ausgrid’s new sub transmission substation in the Munmorah/Doyalson area | Supply to Munmorah/Doyalson once the present 33 kV supply from Munmorah power station is no longer available | Proposed | Indicative date: 2017 | Proposed Augmentation > $6 million | NA | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 4.4 | Replacement of the Munmorah 330/132 kV substation in piecemeal fashion | Condition assessment of Munmorah Substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed. | Proposed | Monitored and replaced as required | Proposed Asset Replacement > $6 million | 9 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 3.4.1 | Replacement of Canberra 330/132 kV substation in piecemeal fashion | Asset Condition – Condition assessments of Canberra Substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed | Proposed | Indicative date: 2019 | Proposed Asset Replacement > $6 million | 30 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 4.4 | Condition of Burrinjuck 132/11 kV substation: - connect line 970, line 992 and the Burrinjuck power station in a tee-connection, and decommission the portion of the Burrinjuck substation owned by TransGrid | Asset Condition – Condition assessments of Burrinjuck substation and its assets identified numerous items of equipment reaching the end of their serviceable life and substation issues which are required to be addressed. | Proposed | Under review | Proposed Asset Replacement > $6 million | 7 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 4.4 | Complete the communication link works and commission the NSW-Muraylink runback scheme | Reliability issues in northern Victoria and South Australia | Proposed | Completed | Proposed Augmentation > $6 million | NA | No impact on 2015 NTNDP studies | Main Grid | Not applicable
Section 4.4 | Implement a combination of SCADA and protection optimised multiple contingency schemes to protect the NSW power system from potential cascading failure | This is a regulatory obligation driven project. This project mitigates the impact of multiple contingency events which result in voltage instability. | Committed | The program is to be delivered in a piecemeal fashion focusing on the highest priority parts of the network. | Committed Augmentation > $6 million | 9.3 | No impact on 2016 NTNDP studies | Main Grid | Not applicable
Section 4.2.3 | Provision of a New 132 kV switch bay at Williamsdale 330/132 kV Substation | When the Googong town load grows sufficiently, it will require a second 132 kV supply | Proposed | Indicative date: 2018 | Proposed Augmentation < $6 million | 1.017 | Local Area Limitation - Not within scope of NTNDP | Local Network | Not applicable
Section 4.3.4 | Sydney North – Tuggerah Line 21 Tower Life Extension | Condition based replacement | Proposed | Indicative: 2021 | Proposed Asset Replacement < $6 million | 5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.1 | 959/92Z Sydney North – Sydney East 132 kV transmission line : tower life extension | Condition based replacement | Proposed | Anticipated between 1 and 10 years | Proposed Asset Replacement > $6 million | 8.5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.3.4 | Deniliquin 132/66 kV substation: Secondary Systems Replacement | Condition based replacement | Proposed | Indicative date: 2023 | Proposed Asset Replacement > $6 million | 10 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.4 | ANM 132 kV substation: Secondary System Replacement | Condition based replacement | Proposed | On Hold | Proposed Asset Replacement < $6 million | 6 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.4 | 1 and 2 Snowy – Yass/Canberra 330 kV transmission lines remediation | Condition based replacement | Proposed | On Hold | Proposed Asset Replacement > $6 million | 29 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.4 | Low Span Northern Tower Lines Remediation - Central Coast Hunter Valley Northern NSW | Remedial works to restore conductor clearances on 137 spans across 12 330 kV transmission lines in the northern region | Proposed | Indicative date: 2018 | Proposed Asset Replacement < $6 million | 4 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.3.2 | Low Span Northern Pole Lines Remediation - Central Coast Hunter Valley Northern NSW | Remedial works to restore conductor clearances on 263 spans across 14 132 kV transmission lines in the northern region | Comitted | Late 2017 | Comitted Asset Replacement > $6 million | 8 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 3.5 | Low Span Central Tower Lines Remediation - NSW metropolitan area | Remedial works to restore conductor clearances on 151 spans across 13 330 kV transmission lines in the central region | Proposed | Indicative date: 2017 | Proposed Asset Replacement < $6 million | 2 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.4 | Low Span Central Pole Lines Remediation - Central West NSW | Remedial works to restore conductor clearances on 152 spans across 10 132 kV transmission lines in the central region | Proposed | Indicative date: 2019 | Proposed Asset Replacement < $6 million | 3.7 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.4 | Low Span Southern Tower Lines Remediation - Southern NSW | Remedial works to restore conductor clearances on 45 spans across 11 330 kV transmission lines in the southern region | Proposed | Indicative date: 2019 | Proposed Asset Replacement < $6 million | 3 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.2.4 | Low Span Southern Pole Lines Remediation - Southern NSW | Remedial works to restore conductor clearances on 150 spans across 14 132 kV transmission lines in the southern region | Proposed | Indicative date: 2019 | Proposed Asset Replacement < $6 million | 5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.3.4 | Sydney North to Vales Point 330 kV Transmission Line Tower Life Extension | Condition based replacement | Proposed | Indicative date: 2023 | Proposed Asset Replacement > $6 million | 9 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.3.4 | Murrumburrah 132 kV Substation Secondary Systems Replacement | Condition based replacement | Proposed | Indicative date: 2022 | Proposed Asset Replacement < $6 million | 5 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.4 | Hume 132 kV substation secondary systems replacement in Southern NSW | Replacement of the secondary systems | Proposed | Currently not proceeding | Proposed Asset Replacement > $6 million | 7 | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Not applicable
Section 4.1.2 | Upgrade Queensland – NSW Interconnector (QNI) Transmission Capacity | This is a market benefit driven project | Regulatory consultation completed | Limiitation will be reviewed in 5-10 years | Regulatory consultation completed Augmentation > $6 million | 72.207 | The least cost modelling does not identify the need to increase the NSW-QLD transfer capability. | Main Grid | Not applicable
Section 4.1.2 | Develop new breaker and a half switch yards for Tamworth and Armidale 330/132 kV substations | This project is market benefit driven and is contingent on QNI being upgraded | Proposed | Between 5 to 10 years | Proposed Augmentation > $6 million | NA | No impact on 2015 NTNDP studies | Main Grid | Not applicable
Section 4.1.2 | Hunter Valley - Tamworth - Armidale 330 kV system: Upgrade the capacity of the 330 KV transmission lines between Liddell and Tamworth through uprating lines or building new 330 kV transmission lines | This project is market benefit driven and is contingent on QNI being upgraded and new generation being connected in northern NSW. | Proposed | Between 5 to 10 years | Proposed Augmentation > $6 million | NA | The need to increase the capacity of the Hunter Valley – Tamworth – Armidale 330 kV lines does not arise during the NTNDP outlook period. | Main Grid | Not applicable
Section 4.1.2 | Install new capacitors in northern NSW at Dumaresq, Armidale, and Tamworth or an SVC in the area. | This project is market benefit driven and is contingent on QNI being upgraded | Proposed | Between 5 to 10 years | Proposed Augmentation > $6 million | NA | The least cost modelling does not identify the need to increase the NSW-QLD transfer capability. | Main Grid | Not applicable
Section 4.1.1 | Powering Sydney's Future: preferred option is to establish two new 330 kV cables between Rookwood Road and Beaconsfield West connected and operated at 132 kV, in conjunction with Ausgrid’s replacement of the 132 kV cables supplying the Surry Hills area | Limitations in supplying the inner Sydney area : - Retirement of Ausgrid 132 kV cables - De-rating of 330 kV cable 41 - De-rating of 132 kV cables - Sydney Load growth | Proposed | Within 5 Years* PSCR with Ausgridgrid | Proposed Augmentation > $6 million | 500 | Limitation was identified within first 5 years of NTNDP study. The limitation is sensitive to changes in local demand and network capability. The timing of the limitation will change if there is a material change to local demand and network capability. | Main Grid | demand management to defer or, if possible, avoid one or both of these cables would be implemented if practical and cost-effective.
Section 4.4 | Rebuild Newcastle Substation: The preferred network option is to rebuild Newcastle substation in a piecemeal fashion. | Condition of Newcastle Substation. The need date to address the condition issues at Newcastle is 2020. The substation is required to meet the present and future demand in the area, and provide a focal point for seven 330 kV connections. | Proposed | Deferred to 2021 | Proposed Asset Replacement > $6 million | NA | Condition based renewals - not within the 2015 NTNDP scope. | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 4.3.1/4.4.1 | Capacity of the Snowy to Sydney network: Increasing line ratings of line 01, 39, 4 and 5 to 100°C Installing a phase shifting transformer on line 39 Replacing terminal equipment on line 11 at Dapto and Sydney South | Development of new generation in Southern NSW may lead to the 330 kV network between the Canberra/Yass area and Sydney becoming congested | Proposed | Timing based on future generation/load. Currently Monitoring | Proposed Augmentation > $6 million | 81.36 | The need to increase capacity of the network to import power from the Snowy region, or Uranquinty, or from Victoria does not arise in the NTNDP outlook period. | Main Grid | Potential local generation support and demand side management initiatives.
Section 4.3.1/4.4.1 | Capacity of the Marulan – Avon, Marulan – Dapto and Kangaroo Valley – Dapto lines: Increasing line ratings of line 18 to 100°C operating temperature | Development of new generation in Southern NSW may lead to the 330 kV network between the Canberra/Yass area and Sydney becoming congested | Proposed | Timing based on future generation/load. Currently Monitoring | Proposed Augmentation > $6 million | NA | The need to increase rating of Marulan – Avon, Marulan – Dapto and Kangaroo Valley – Dapto Lines does not arise during the NTNDP outlook period. | Main Grid | Implementing a special protection scheme (SPS) - generation runback scheme
Section 4.3.3 | Provision of capacitor banks at Panorama and Orange 132/66 kV Substations and Orange North 132 kV Switching Station; • Provision of a 132 kV series reactor on the 94X Wallerawang – Panorama 132 kV line and later on the 949 Mt Piper – Orange North 132 kV; and • replacement of 944 line | Condition of Wallerawang-Orange line 944 | Proposed | 2019-2026 | Proposed Asset Replacement < $6 million | 0.5 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 4.2.4 | Beryl 132/66 kV substation: secondary systems replacement | Condition based replacement | Proposed | Indicative date: 2020 | Proposed Asset Replacement < $6 million | 6 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 4.2.4 | Armidale Secondary System Replacement | Condition based replacement | Proposed | Deferred to 2021 | Proposed Asset Replacement < $6 million | 1 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 4.3.4 | Forbes No 1 and No 2 132/66 kV transformer replacement | Condition based replacement | Proposed | Indicative date: 2021 | Proposed Asset Replacement > $6 million | 8 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 4.4 | Yanco – Griffith 132 kV Line 99J Rebuild | Condition based replacement | Proposed | Indicative date: 2022 | Proposed Asset Replacement > $6 million | 18 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 4.3.3 | No.1 transformer replacement | Sydney East 330/132 kV substation | Proposed | 1905-07-12 | Proposed Asset Replacement > $6 million | 16 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Potential local generation support and demand side management initiatives.
Section 3.3.1 | Installation of fibre networks | OPGW installation in Southern and Central West area | Comitted | Mid 2018 | Comitted Asset Replacement > $6 million | NA | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 3.4.2 | Avon Swithcing station | Repalcment of secondary sustems | Planned | End 2017 | Planned Asset Replacement > $6 million | NA | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 4.1.3 | Interconnection between SA and NSW (SANI) | This project is drive by market benefit, as well as relabliity benefits | Proposed | Presntly an option for RIT-T | Proposed Augmentation > $6 million | NA | Considered in NTNDP | Main Grid | Some benefits to relability/security can be provieded locally
Section 4.2.2 | Wood Pole Repalcement | Replace wooden pole structures in poor condition along the following lines: 94X, 948, 966, 993, 995, 9U3, 976/2, 97B, 97A, 99P , 97L, 97G/3 and 96L | Proposed |  | Proposed Asset Replacement > $6 million | NA | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 4.4.4 | Wellington Reactor replacement | Condition based replacement | Proposed | 2022 | Proposed Asset Replacement < $6 million | 4.5 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable
Section 4.4.4 | Marulan Transformer renewal | Condition based replacement | Proposed | 2023 | Proposed Asset Replacement < $6 million | 2 | Replacement Project - Not within scope of NTNDP | Asset Replacement | Not applicable

## Reference
AEMO categorisation
Committed augmentation > $6 million
Committed replacement > $6 million
Monitoring limitation > $6 million (equivalent to proposed)
Proposed replacement > $6 million
Committed augmentation < $6 million
Committed replacement < $6 million
Monitoring limitation < $6 million (equivalent to proposed)
Proposed replacement < $6 million