## Index
The National Electricity Market Constraint Report 2021
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Ad-Hoc | 0 | 1 | 1 | 0 | 0 | 0
Constraint Automation - Real Time | 22603 | 29805 | 37744 | 32817 | 53504 | 40710
Constraint Automation | 64 | 20 | 48 | 49 | 39 | 23
DATASNAP | 115 | 44 | 92 | 90 | 62 | 60
FCAS | 257 | 267 | 486 | 1192 | 730 | 418
NSW | 1973 | 2455 | 8206 | 5092 | 7926 | 6562
Negative Residue | 0 | 0 | 0 | 0 | 12 | 0
Non-Conformance | 5 | 52 | 35 | 29 | 31 | 40
Other | 0 | 0 | 3 | 1 | 0 | 16
Outage Ramping | 20484 | 16928 | 19368 | 25718 | 23622 | 33118
PASA | 0 | 0 | 0 | 0 | 0 | 1
Qld | 206 | 246 | 1716 | 582 | 937 | 1305
Quick | 359 | 386 | 1032 | 865 | 1072 | 862
SA | 3197 | 1775 | 3239 | 7132 | 2309 | 6564
Tas | 1050 | 134 | 193 | 629 | 25 | 351
Vic | 3251 | 1376 | 6280 | 5656 | 1418 | 2312
Total constraint eqns | 11660 | 11578 | 11467 | 12348 | 13127 | 14297
Total changes without outage ramping and CA-RT | 10477 | 6756 | 21331 | 21317 | 14561 | 18514
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578 | 11467 | 12348 | 13127 | 14297
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917 | 4036 | 4390 | 4603 | 4973
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387 | 505 | 585 | 588 | 641
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82 | -111 | 881 | 779 | 1170

## Binding
Constraint Equation ID | 2021 Hours | 2020 Hours | Description | Type | Limit Type | Region
#TORRB2_D_E | 2726.0833 | 1078 | STSB2.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
#PPCCGT_D_E | 2479.75 | 2074.0833 | SPPT.ENERGY * 1 = 166 (Wt = 755) | Other | DEFAULT | Direction
#TORRB3_D_E | 1939.75 | 819.5 | STSB3.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
S>NIL_MHNW1_MHNW2 | 1723.9167 | 144 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
#TORRB4_D_E | 1622.4167 | 465.25 | STSB4.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
#COHUNSF1_E | 1530.3333 | 228.9167 | VKGS2C.ENERGY * 1 <= 13 (Wt = 360) | Other | DEFAULT | Quick
#WARWSF2_E | 1509.3333 | 63.1667 | QMRY4W.ENERGY * 1 <= 16 (Wt = 360) | Other | DEFAULT | Quick
#TORRB1_D_E | 1439.0833 | 463.9167 | STSB1.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
T::T_NIL_1 | 1427.5 | 315.75 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
T_MRWF_FOS | 1251.1667 | 1187.8333 | Limit Musselroe wind farm due to upper limit on Tasmanian generator events. Limit is 153 MW (effective 144 MW at the connection point at Derby) | NIL | Other | Tas
N^^N_NIL_3 | 1245.9167 | 104.4167 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL | Voltage Stability | NSW
N^^N_NIL_2 | 1028.4167 | 165.25 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
SVML_ZERO | 1008.3333 | 947 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
#MAPS2PV1_E | 928.4167 | 0 | SMA21M.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
#MWPS1PV1_E | 910 | 0 | SMW11M.ENERGY * 1 <= 0 (Wt = 360) | Other | DEFAULT | Quick
V^^N_NIL_1 | 875 | 585.1667 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
#MWPS2PV1_E | 845.4167 | 0 | SMW21M.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
N>>N-NIL_94T | 843.9167 | 0 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | NIL | Thermal | NSW
#VIC1_E_20200811 | 745.0833 | 884.1667 | Multiple VIC1 LHS <= 300 (Wt = 360) | Other | DEFAULT | Quick
S_NIL_STRENGTH_1 | 648.75 | 942.3333 | Out= NIL, Upper limit (2500 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements | NIL | System Strength | SA
#MWPS4PV1_E | 633 | 0 | SMW41M.ENERGY * 1 <= 0 (Wt = 360) | Other | DEFAULT | Quick
#OSB-AG_D_E | 575.9167 | 47.8333 | SNBN1.ENERGY * 1 = 145 (Wt = 755) | Other | DEFAULT | Direction
#DEVILS_G_E | 566.5833 | 226.0833 | TDG11.ENERGY * 1 <= 64 (Wt = 360) | Other | DEFAULT | Quick
Q>NIL_YLMR | 562.25 | 63.6667 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
Q>NIL_EMCM_6056 | 475.5833 | 0 | Out= NIL, avoid thermal overload on Emerald to Comet (6056) 66 kV Feeder | NIL | Thermal | Qld
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 411.5 | 139.75 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | Voltage Stability | NSW
N>>N-NIL_94T_947 | 407 | 129.6667 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | NIL | Thermal | NSW
N>N-NIL_PK_TX1 or N>N-NIL_PK_TX2 | 394.4167 | 0 | Out= Nil, avoid O/L Parkes TX1 or TX2 132/66kV transformer on trip of Nil, Feedback | NIL | Thermal | NSW
#WARWSF1_E | 383.4167 | 371.4167 | QMRY3W.ENERGY * 1 <= 16 (Wt = 360) | Other | DEFAULT | Quick
#BULBESG1_E | 377.75 | 0 | VBGT2B.ENERGY * 1 <= 0 (Wt = 360) | Other | DEFAULT | Quick
V^^V_NIL_KGTS V^^V_NIL_KGTS_2 | 349.5833 | 0 | Out= Nil, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | NIL | Voltage Stability | Vic
SV_420_DYN | 335.4167 | 120.6667 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
V_S_NIL_ROCOF | 326.9167 | 11.25 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
N_X_MBTE_3A & N_X_MBTE_3B | 321.5833 | 797.5 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
#WAGGNSF1_E | 318.1667 | 0 | NWGG1W.ENERGY * 1 <= 22 (Wt = 360) | Other | DEFAULT | Quick
V>V_NIL_17 | 283.8333 | 235.5833 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
SVML^NIL_MH-CAP_ON | 283 | 0 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL | Voltage Stability | SA
#WELLSF1_E | 280.9167 | 0.83333 | NWLS4W.ENERGY * 1 <= 170 (Wt = 360) | Other | DEFAULT | Quick
S^SETX_GEN_CAP | 273.4167 | 79.4167 | Out= One South East 275/132kV transformer O/S, avoid local voltage collapse on trip of remaining South East transformer, | Outage | Thermal | SA
N>N-NIL_LSDU | 270.3333 | 101.25 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
#JEMALNG1_E | 255.3333 | 0 | NFBS1J.ENERGY * 1 <= 36 (Wt = 360) | Other | DEFAULT | Quick
#WEMENSF1_E | 255 | 0 | VWES2W.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
V_T_NIL_FCSPS | 238.1667 | 347.9167 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
N>N-NIL_997_99A | 234.8333 | 0 | Out= Nil, avoid O/L Corowa to Albury 132kV line (997/1) on trip of Finley to Uranquinty 132kV line (99A), Feedback | NIL | Thermal | NSW
V>>V_NIL_18 | 228.1667 | 35.6667 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
#WINTSF1_E | 226.3333 | 0 | VGNS2W.ENERGY * 1 <= 30 (Wt = 360) | Other | DEFAULT | Quick
V^^V_MLNK_KGTS | 221.9167 | 0 | Out= Murraylink, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | Outage | Voltage Stability | Vic
S>NIL_HUWT_STBG2 | 217.0833 | 42.25 | Out = Nil; avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=60 MW && when Dalymple Battery (i.e. both Gen and Load component) is I/S].[Note:Swamped when WTTPT<80 && DALR OFF OR DalrB OFF] | NIL | Thermal | SA
V_YATPSF_FLT_25 | 216.4167 | 0 | Limit Yatpool solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_NIL_STRGTH_HAUSF | 216.25 | 995.0833 | Out = Nil, limit Haughton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
V_KIAMSF_FLT_50 | 211.8333 | 0.83333 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KARADSF_FLT_25 | 209.0833 | 63.5833 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S-X_2DV+2RB_STRGHT_1 | 200.5833 | 0 | Out = 2 x Davenport + 2 x Robertstown synchronous condensers O/S, Upper limit (1300 to 1750 MW) for SA ASG for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | Outage | System Strength | SA
V_BANSF_BBD_60 | 199.9167 | 277 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
N>>N-NIL_969 | 183.5 | 0 | Out= Nil, avoid O/L Gunnedah to Tamworth (969) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
V^^N_MSUT_1 | 183.3333 | 0 | Out = Murray to Upper Tumut (65), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S:V_PA_SVC_420 | 176.5 | 363.75 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
N_MBTE1_B | 175.75 | 119.6667 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
#YATSF1_E | 165.8333 | 166.5 | VRCS2Y.ENERGY * 1 <= 50 (Wt = 360) | Other | DEFAULT | Quick
V_MURRAWRWF_FLT_90 | 164.9167 | 130.5833 | Limit Murra Warra Wind Farm upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
#ADPPV1_E | 160.3333 | 0 | SMVE6D.ENERGY * 1 <= 9 (Wt = 360) | Other | DEFAULT | Quick
#ADPBA1G_E | 159.8333 | 0 | SMVE4D.ENERGY * 1 <= 0.001 (Wt = 360) | Other | DEFAULT | Quick
#ADPBA1L_E | 159.8333 | 0 | SMVE5D.ENERGY * 1 <= 0.001 (Wt = 360) | Other | DEFAULT | Quick
#GNNDHSF1_E | 144.9167 | 0 | NGNE1G.ENERGY * 1 <= 110 (Wt = 360) | Other | DEFAULT | Quick
N_COLEASF1_FLT_45 | 137.1667 | 5.4167 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_LIMOSF1_FLT_60 | 136.1667 | 0 | Limit Limondale 1 solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_BROKENH1_ZERO | 135.5 | 39.8333 | Broken Hill Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
N^N_CHLS_1 | 134 | 15.6667 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
Q^^NIL_QNI_SRAR | 134 | 397.1667 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
N_BROKENHSF_FLT_25 | 133.25 | 46.25 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V::N_DDSM_xxx | 132.25 | 11.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_VS_LB_CAN_50 | 128.0833 | 4.75 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage | System Strength | SA
#STOCKYD1_E | 126.8333 | 0 | VHGT1S.ENERGY * 1 <= 286 (Wt = 360) | Other | DEFAULT | Quick
Q>NIL_BI_xxx | 121.5 | 0.5 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines | NIL | Thermal | Qld
V_KARADSF_FLT_20 | 120.3333 | 0.083333 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KIATAWF_FLT_0 | 115.9167 | 45.1667 | Limit Kiata Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
SA_ISLE_STRENGTH_BU | 115.8333 | 17.5833 | Out= 2x Davenport syn cons + 2 x Robertstown syn cons O/S when SA in Island mode, Maximum limit (130 MW) for Bungala Solar Farm for system strength requirements when SA is at risk of separation or when islanded.(Note:Swamped when all 4/any syncons I/S) | Outage | System Strength | SA
V_MLMO_VS_LB_CAN_50 | 115.4167 | 147.5 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS generating. | Outage | System Strength | SA
V_YATPSF_FLT_20 | 115.4167 | 0 | Limit Yatpool solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>Q-NIL_757_758 | 115.25 | 0 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL | Thermal | NSW
N^^V_NIL_1 | 114.8333 | 535.5 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
#TORRA3_D_E | 114.4167 | 28 | STSA3.ENERGY * 1 = 40 (Wt = 755) | Other | DEFAULT | Direction
N^^V_CNCW_1 | 113.5833 | 19.25 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V_MURRAWRWF_FLT_0 | 111.8333 | 68.5833 | Limit Murra Warra Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V_S_HEYWOOD_UFLS | 110 | 7.8333 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC.Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
V_STOCKYH_ZERO | 105.75 | 0 | Stockyard Hill wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
#CRURWF1_E | 105.6667 | 1.8333 | NCDS1C.ENERGY * 1 <= 138 (Wt = 360) | Other | DEFAULT | Quick
#GULLRWF2_E | 103.4167 | 146.75 | NGUR3G.ENERGY * 1 <= 67 (Wt = 360) | Other | DEFAULT | Quick
V>>N-NIL_HA | 103.3333 | 18.1667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
SVML_ROC_80 | 102.3333 | 72.8333 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
#BULGANA1_E | 102.1667 | 302.9167 | VBGT1B.ENERGY * 1 <= 150 (Wt = 360) | Other | DEFAULT | Quick
N_SUNRSF_FLT_60 | 101.9167 | 0 | Limit Sunraysia solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>>CPST_CLWU_RGLC | 101.9167 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
V_BANNERTSF_FLT_25 | 101.8333 | 63.9167 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_FINLYSF_FLT_45 | 101.0833 | 46.4167 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
NRM_QLD1_NSW1 | 100.0833 | 5.9167 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
V^^N_LTYS_1 | 98 | 0 | Out = Lower Tumut - Yass (3) 330kV line , avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_BANNERTSF_FLT_45 | 98 | 40.0833 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_OAKEY1SF_ZERO | 96.0833 | 0 | Oakey 1 Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N_LIMOSF2_FLT_15 | 94.5833 | 0 | Limit Limondale 2 solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V::N_HWSM_xxx | 94.5833 | 125 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
#QLD1_E_20210706 | 94.25 | 0 | Multiple QLD1 LHS <= 0 (Wt = 360) | Other | DEFAULT | Quick
V::N_SMF2_xxx | 93 | 4.0833 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V^^N_CNCW_1 | 93 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V>>V_DDSM_1 | 91.5 | 0 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Thermal | Vic
Q_STR_HASF_ZERO | 90.0833 | 0 | Limit 0MW to Haughton Solar farm for system strength requirement | Outage | System Strength | Qld
Q_STR_MEWF_ZERO | 90.0833 | 0 | Limit 0MW to Mt Emerald Wind farm for system strength requirement | Outage | System Strength | Qld
Q_STR_SMSF_ZERO | 90.0833 | 0 | Limit 0MW to Sun Metals Solar farm for system strength requirement | Outage | System Strength | Qld
Q>>BCST_BCST_CLWU | 89.3333 | 0 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line, avoid O/L the remaining Stanwell to Bouldercombe 848 or 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
V_ARARATWF_FLT_0 | 89.0833 | 15.75 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V^SML_BUDP_3 | 88.8333 | 27.0833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
N>>N-NIL_94B_9ML | 88.6667 | 0 | Out= Nil, avoid O/L Bodangora to Wellington (94B/1) on trip of Crudine Ridge to Ilford Tee (9ML) line, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
V_NUMURKAH_ZERO | 88 | 52.0833 | Numurkah Solar Farm upper limit of 0 MW | NIL | Unit Zero | Vic
V_BANSF_BBD_80 | 86.0833 | 38.8333 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
S>SETX_NIL_SETX | 84.5833 | 0 | Out= One South East 275/132kV transformer O/S, avoid O/L of other South East 132/275kV TX on Nil trip, | NIL | Thermal | SA
VSML_ROC_80 | 84.1667 | 77.4167 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
#WANDBG1_E | 83.1667 | 0 | QWSB1W.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
N_SUNRSF1_ZERO | 81.75 | 0 | Sunraysia 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
#WANDBL1_E | 81.5 | 0 | QWSB2W.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
V>>V_NIL_7 | 81.5 | 17.9167 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
V_GANWRSF_FLT_30 | 79.9167 | 7.4167 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_CWWF_FLT_0 | 79.8333 | 17.5833 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>N-PKWL_94K_2 | 79.4167 | 0 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
V_MURRAWRWF_FLT_80 | 77 | 0 | Limit Murra Warra Wind Farm upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
#YARANSF1_E | 76.5833 | 1403.5833 | QMRY1Y.ENERGY * 1 <= 82 (Wt = 360) | Other | DEFAULT | Quick
V>>V_NIL_9 | 75.75 | 147.9167 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
V_KIATAWF_FLT_15 | 75 | 7.6667 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
V^^N_DPWG_X5_1 | 73.3333 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N^^V_DDSM1 | 72.5833 | 74 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
V_MACWF_FLT_0 | 72.4167 | 0 | Limit Macarthur Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>N-NIL_9R4_99A | 71.75 | 44.0833 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) on trip of Finley to Uranquinty (99A) line, Feedback | NIL | Thermal | NSW
S>SE6161_SETX2_SGBL | 71.5833 | 0 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | Thermal | SA
VT_ZERO | 71.25 | 60.5833 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Interconnector Zero | Vic
N_BROKENHSF_FLT_30 | 69.75 | 8.6667 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N^N-LS_SVC | 69.5 | 638.75 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | Voltage Stability | NSW
T>T_NIL_BL_110_4 | 68.8333 | 3.3333 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
#LGAPWF2_E | 68.6667 | 0 | SLGW4L.ENERGY * 1 <= 43 (Wt = 360) | Other | DEFAULT | Quick
Q>>CPWO1_CPWO2_WUGG | 67.5 | 0 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Woolooga (814) on trip of Wurdong to Teebar Creek (819) line, Feedback | Outage | Thermal | Qld
S>>RBTX_WEWT_RBTX | 66.75 | 0 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
N_COLEASF1_ZERO | 66.6667 | 8.8333 | Coleambally solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_SILVERTWF_FLT_100 | 66.6667 | 8.75 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
V_CWWF_FLT_55 | 64.75 | 0 | Limit Crowlands Wind Farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NQTE_ROC | 63.4167 | 37.6667 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
V^^N_HWSM_1 | 63.3333 | 155.1667 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^N_CNUT_1 | 61.3333 | 1 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S:V_XPAVC_310 | 60.25 | 27.9167 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
QNTE_ROC | 60.0833 | 30 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
Q>NIL_COLNVSF1 | 59.9167 | 305.5 | Out = Nil, Limit Collinsville Solar Farm to thermal rating of Powerlink's RMU | NIL | Thermal | Qld
#MIDDLSF1_E | 59.6667 | 23.6667 | QLIS2M.ENERGY * 1 <= 26 (Wt = 360) | Other | DEFAULT | Quick
V^^SML_NSWRB_2 | 59.3333 | 50.8333 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
T_MRWF_QLIM_xx | 58.0833 | 66.6667 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
#KEPSF1_E | 57.8333 | 0 | QROW2K.ENERGY * 1 <= 7.5 (Wt = 360) | Other | DEFAULT | Quick
N>N-NIL_MBDU | 56.8333 | 8.8333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
S>>PARB_RBTU_WEWT | 56.3333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S-SNWWF_0 | 54 | 8.0833 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | Unit Zero | SA
N>>N-MPWW_ONE_8 | 53.8333 | 0 | Out= Mt. Piper to Wallerawang(70 or 71), avoid O/L Molong to Orange North (94T) on trip of the remaining Mt Piper to Wallerawang (71 or 70) , Feedback | Outage | Thermal | NSW
N^N-89_LSTX_SVC | 52.5833 | 0 | Out= Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage | Voltage Stability | NSW
N::N_NIL_63 | 52.25 | 0 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
V_WEMENSF_FLT_25 | 52.0833 | 53.5 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_DARLSF_FLT_80 | 48.4167 | 27.9167 | Limit Darlington Pt Solar Farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_NIL_STRGTH_SMSF | 47.9167 | 504.75 | Out = Nil, limit Sun metals solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_OKYOKYSF | 47.8333 | 0 | De-rating of 33kV Cable from Oakey(T189) substation to Oakey solar farms, limit total output of Oakey SF 1 and SF2 to 40MW | Outage | Thermal | Qld
Q_STR_32282_HASF | 47.5 | 0 | Limit 75% to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
V:S_600_HY_TEST | 46.9167 | 17.5833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
#MOORAWF1_E | 46.4167 | 148.5833 | VELT2M.ENERGY * 1 <= 75 (Wt = 360) | Other | DEFAULT | Quick
Q-CLRSF_MVAR | 46 | 0 | Constraint to violate if Reactive power output of Clare Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-HAMSF_MVAR | 46 | 0 | Constraint to violate if Reactive power output of Hamilton Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-WHTSF_MVAR | 46 | 0 | Constraint to violate if Reactive power output of Whitsundays Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
Q-COLSF_MVAR | 45.9167 | 0 | Constraint to violate if Reactive power output of Collinsville Solar farm is greater than +/10Mvar when it is limited at 0MW output, Swamp if MW >0 (DS only) | Outage | Unit Zero | Qld
N^^Q_AR_VC_B1 | 45.8333 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
S:V_PA_SVC_270 | 45.5 | 1.5833 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
#DARLSF1_E | 45.0833 | 59.8333 | NDNS1D.ENERGY * 1 <= 275 (Wt = 360) | Other | DEFAULT | Quick
V::N_NIL_xxx | 44.9167 | 37.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Transient Stability | Vic
#CRWASF1_E | 44.5 | 0 | NAL11C.ENERGY * 1 <= 22 (Wt = 360) | Other | DEFAULT | Quick
V::N_MLTR_xxx | 44.0833 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
S:V_550_HY_TEST_DYN | 43.9167 | 52.5 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
N_LIMOSF2_FLT_25 | 43.5 | 52.8333 | Limit Limondale 2 solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_NIL_STRGTH_MEWF | 43.1667 | 1572.1667 | Out = Nil, limit Mt Emerald wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N_WRWSF_055 | 43.0833 | 16.4167 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | Other | NSW
N::N_SDUT_2 | 42.75 | 0.41667 | Out = Upper Tumut -Stockdill(1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
V:S_600_HY_TEST_DYN | 42.5 | 23.5 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
N_LIMOSF11_ZERO | 42.1667 | 0.33333 | Limondale 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
T>T_NIL_110_1 | 41.9167 | 32.6667 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
N::N_LTYS_2 | 41 | 0 | Out = Lower Tumut -Yass(3), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
V_BULGANAWF_FLT_40 | 40.9167 | 0 | Limit Bulgana Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^^Q_ARTW_B1 | 40.8333 | 17.3333 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
#KEPWF1_E | 40.75 | 0 | QROW1K.ENERGY * 1 <= 10 (Wt = 360) | Other | DEFAULT | Quick
S>DVTX_NIL_DVTX | 40.75 | 23.25 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | NIL | Thermal | SA
N_COLEASF1_FLT_30 | 40.6667 | 18.6667 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>V_NIL_14 | 39.75 | 4.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
N^^Q_NIL_A | 39.25 | 8.8333 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | Voltage Stability | NSW
S_SECB_LG-1 | 39.25 | 6.4167 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | Thermal | SA
#CPP_3_E | 39.1667 | 13.8333 | QCAC3.ENERGY * 1 <= 0 (Wt = 360) | Other | DEFAULT | Quick
N_SUNRSF_FLT_50 | 38 | 0 | Limit Sunraysia solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N^^Q_MUTW_1_B1 | 37.6667 | 3.75 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
V>>N-X_MSUT_99P_1 | 36.0833 | 0 | Out= Murray to Upper Tumut(65) and either 993 or 99P,avoid Murray to Lower Tumut(66) O/L on trip of Wagga to Lower Tumut(051) and With subsequent operation of Wagga-Yass trip scheme that will open Yass?Wagga parallel(Trip 990+991),Feedback.OM607 and OM527 | Outage | Thermal | Vic
N^^Q_TW_330_BUS1_B1 | 35.9167 | 0 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
#COOPGWF1_E | 35.6667 | 339.8333 | QCPG1C.ENERGY * 1 <= 440 (Wt = 360) | Other | DEFAULT | Quick
SVML_FLT_125 | 35 | 4.0833 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
N_FINLYSF_FLT_30 | 34.4167 | 14.5 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 34.25 | 12.4167 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Thermal | Qld
Q>>CPST_CLWU_BCST | 33.8333 | 0 | Out = 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Stanwell to Bouldercombe 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
T::T_HA_GT_PM_4 | 33.5833 | 4.5 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
V^^N_UTYS_1 | 33.0833 | 76.75 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_NIL_STRGTH_KIDSF | 32.1667 | 50.6667 | Out = Nil, limit Kidston solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N^^Q_TW_330_BUS3_B1 | 31.5833 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 31.5833 | 155.25 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Transient Stability | Qld
S>>PARB_RBTU_WTTP | 31.5833 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V_GANWRSF_FLT_25 | 31.5833 | 47.6667 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>N-PKWL_94K_1 | 31.25 | 11 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
Q_STR_7C8C_HASF | 31.1667 | 0 | Limit Haughton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 31.0833 | 47.1667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Thermal | Vic
V::S_SETB_TBSE_2 | 30.8333 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Transient Stability | SA
Q_YARANSF1_RB | 30.5 | 0 | Yarrranlea Run Back limit | NIL | Discretionary | Qld
T^V_NIL_11 | 30.1667 | 0.083333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink harmonic filter, swamped if TVCC in service | NIL | Voltage Stability | Tas
S:V_550_HY_TEST | 30 | 33.5 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
V_KIATA_ISL_0 | 29.5833 | 83.0833 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
Q_OAKEY2SF_ZERO | 29.3333 | 0 | Oakey 2 Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
T_T_TI_GH_RC12_250 | 29.3333 | 4.1667 | Discretionary 250 MW upper limit on Tribute, Granville Harbour, Reece 1 and 2 generation | Outage | Discretionary | Tas
Q_NIL_STRGTH_HAMSF | 29.1667 | 22.3333 | Out = Nil, limit Hamilton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_RRSF | 29.0833 | 17.4167 | Out = Nil, limit Ross River solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N_COLEASF1_FLT_60 | 28.9167 | 0 | Limit Coleambally solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V^^N_SDUT_1 | 28.75 | 0 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q>>WOPW_WOSP_WOGP_2 | 28.5 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
Q_NIL_STRGTH_HAYSF | 27.9167 | 0.91667 | Out = Nil, limit Hayman solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_COLSF | 27.5 | 28.9167 | Out = Nil, limit Collinsville solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
V_CWWF_ISL_0 | 27.25 | 37.3333 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N_NIL_TE_B | 26.8333 | 0.33333 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
N>>N-NIL_9ML | 26.75 | 0 | Out= Nil, avoid O/L Crudine Ridge to Ilford Tee (9ML) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
Q_STR_7C8C_RRSF | 26.6667 | 0 | Limit Ross River SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_MARYRSF1_RB | 26.5833 | 0 | Maryrorough Run Back limit | NIL | Discretionary | Qld
Q_STR_7C8C_KIDSF | 26.1667 | 0 | Limit Kidston SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_NIL_STRGTH_WHTSF | 26.0833 | 21.9167 | Out = Nil, limit Whitsunday solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N_LIMOSF1_FLT_50 | 26 | 18.0833 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_NIL_STRGTH_CLRSF | 25.75 | 34.75 | Out = Nil, limit Clare solar farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Kareeya generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N>V_MSSGG_TX | 25.5833 | 0 | Out = one Murray to Guthega 330/132kV Tx, Avoid another parallel Tx overload by limiting Guthega generation | Outage | Thermal | NSW
N_STWF1_ZERO | 25.3333 | 65.5 | Silverton wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_MTMERCER_ZERO | 25.3333 | 13.4167 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
V_KIAMSF_0 | 25.25 | 4.0833 | Out = Kiamal Syncon, limit Kiamal solar farm to 0 MW | Outage | Discretionary | Vic
Q_NIL_STRGTH_DAYSF | 25.0833 | 6.0833 | Out = Nil, limit Daydream solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
S_SECB_LG3 | 25.0833 | 3.9167 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | Thermal | SA
V_WEMENSF_FLT_45 | 25 | 28.5 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q>NIL_TV66 | 24.5 | 0 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Thermal | Qld
V_BANNERTSF_FLT_20 | 24.4167 | 0 | Limit Bannerton Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V>>N-MSUT_1 | 24.3333 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Wagga to Lower Tumut(051) trip; Feedback | Outage | Thermal | Vic
N_TARALGAWF_ZERO | 23.9167 | 11.9167 | Taralga WF upper limit of 0 MW | Outage | Unit Zero | NSW
NRM_NSW1_VIC1 | 23.75 | 22 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
NSA_Q_BARCALDN | 23.25 | 14.25 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
V_ARARATWF_FLT_160 | 23.25 | 0 | Limit Ararat Wind Farm upper limit to 160 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_311393_MEWF | 22.8333 | 16.75 | Limit Mt Emerald SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
S>>CGTB1_TBTU_TBMO | 22.75 | 1.5 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T_FASH_MAXGEN_1 | 22.75 | 0 | Upper limit on Mackintosh + Bastyan + John Butters with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Other | Tas
N_FINLYSF_FLT_55 | 22.6667 | 0 | Limit Finley solar farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
TVBL_ROC | 22.6667 | 16.1667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
#QPS5_D_E | 22.4167 | 9.1667 | SQPS5Q.ENERGY * 1 = 0 (Wt = 755) | Other | DEFAULT | Direction
Q_NIL_STRGTH_RGBSF | 22.1667 | 49.4167 | Out = Nil, limit Rugby Run SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
N^^V_NIL_ARWBBA | 22 | 39.6667 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
Q^^N_AR_SVC_1 | 22 | 8.9167 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
V>V_NIL_8 | 21.9167 | 66.4167 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
Q>>NIL_BCCP_RGLC | 21.3333 | 23.5 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
V_MURRAWRWF_FLT_60 | 21.1667 | 0 | Limit Murra Warra Wind Farm upper limit to 60 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
Q::N_AR_CP2_AR_2L-G | 21.0833 | 9.4167 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
VSML_ZERO | 21 | 41.4167 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
Q_LILYSF1_ZERO | 20.4167 | 43.9167 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
T_T_FASH2_1 | 19.9167 | 0 | Out = Farrell to Sheffield no.2 220kV line, Farrell bus split, limit John Butters, Bastyan and Mackintosh to less than 110% West Coast load | Outage | Other | Tas
N_DARLSF_FLT_110 | 19.5833 | 0 | Limit Darlington Pt Solar Farm upper limit to 110 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
#BOWWBA1G_E | 19.5833 | 0 | SPGW3B.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
#BOWWBA1L_E | 19.5833 | 0 | SPGW4B.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
#BOWWPV1_E | 19.5833 | 0 | SPGW2B.ENERGY * 1 <= 0.0001 (Wt = 360) | Other | DEFAULT | Quick
Q>CMTX | 19.4167 | 26.75 | Out = Clermont T1 or T2 132/66 kV transformer, limit to Clermont Solar Farm to 30MW to prevent overload on remaining transformer | Outage | Thermal | Qld
SVML_FLT_130 | 19.1667 | 0 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
N_LIMOSF1_FLT_85 | 19.0833 | 0 | Limit Limondale 1 solar farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
NSA_Q_GSTONE34_xxx | 18.9167 | 91.5833 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
V::S_NIL_MAXG_xxx | 18.3333 | 2.0833 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
N_DARLSF_FLT_85 | 18 | 0 | Limit Darlington Pt Solar Farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C8C_HAMSF | 17.75 | 0 | Limit Hamilton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
SVML^NIL_160 | 17.6667 | 52 | Out=NIL, SA to Vic on ML upper transfer limit of 160 MW to manage voltage collapse at Monash | NIL | Discretionary | SA
N^^Q_CPP_N-2 | 17.5 | 0 | Out= Nil, loss of all Callide C units declared credible, to prevent Voltage Collapse on loss of all Callide C units | Outage | Voltage Stability | NSW
N::N_CNCW_2 | 17.4167 | 0 | Out= Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | Transient Stability | NSW
N_SUNRSF_FLT_80 | 17.1667 | 0 | Limit Sunraysia solar farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C8C_CLRSF | 16.6667 | 0 | Limit Clare SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
T_CTHLWF_ZERO | 16.6667 | 0 | Wild Cattle Hill Wind Farm upper limit of 0 MW | Outage | Unit Zero | Tas
VTBL_ROC | 16.6667 | 9.0833 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
V_GANWRSF_FLT_15 | 16.6667 | 0 | Limit Gannawarra solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#SUNRSF1_E | 16.3333 | 0 | NBSF2S.ENERGY * 1 <= 200 (Wt = 360) | Other | DEFAULT | Quick
#TORRB1_E | 16.25 | 1.3333 | STSB1.ENERGY * 1 = 40 (Wt = 360) | Other | DEFAULT | Quick
Q_KSP1_ZERO | 16.25 | 0 | Kidston solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
T::T_NIL_3 | 16.25 | 20.4167 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
S>NIL_HUWT_STBG3 | 16 | 0 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Constraint Swamped when Wattle PT when generating >=60 MW) | NIL | Thermal | SA
V>SMLMHNW1 | 15.9167 | 1.9167 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | Vic
V::N_MLSY_xxx | 15.8333 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q_STR_7C8C_HAYSF | 15.6667 | 0 | Limit Hayman SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
#NSW1-QLD1_RAMP_I_F | 15.5 | 29.6667 | NSW1-QLD1 >= MIN(-165, InitialFlow + 200) (Wt=35) | Other | Ramping | Quick
V::N_KGRC_xxx | 15.3333 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_LTWG_xxx | 15.3333 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N>N-NIL_CO_TX | 14.8333 | 0 | Out= Nil, avoid O/L either Corowa 22kV/132kV Transformer on NIL trip, Feedback. NOTE: System normal is only one transformer in service. 90% of Rating and no operating margin is used as per Essential Energy advice. | NIL | Thermal | NSW
S>>X_RBPA+CB_03 | 14.8333 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | Thermal | SA
N^N_KKLS_1 | 14.5 | 2.0833 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
Q_STR_7C8C_COLSF | 14.5 | 0 | Limit Collinsville SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>NIL_NIL_SETX12 | 14.5 | 0 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | Thermal | SA
N^^V_CTMN_1 | 14.3333 | 0 | Out = Collector - Marulan (4) or Collector - Yass (3L) or Marulan - Yass (5), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V^^N_MNYS_1 | 14.0833 | 20.6667 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_ARARATWF_ISL_0 | 14.0833 | 30.25 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
S-MWPS4-PV_0 | 14 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW | Outage | Unit Zero | SA
V>>N-DDWO_RADIAL_2 | 13.8333 | 0 | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Thermal | Vic
SA_ISLE_STRENGTH | 13.6667 | 8.6667 | Maximum limit (1900 MW) for SA non-synchronous generation for system strength requirements when SA is at risk of separation or when islanded. | Outage | System Strength | SA
Q_STR_311393_HASF | 13.3333 | 41.5833 | Limit Haughton SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
Q::N_DM_CB_AR_2L-G | 13.1667 | 0.083333 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
Q_STR_7C8C_DAYSF | 13.1667 | 0 | Limit Daydream SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>X_RBPA+CB_01 | 13.0833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), | Outage | Thermal | SA
T_T_FASH_1_N-2 | 12.9167 | 13.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Other | Tas
Q_STR_7C8C_RUGSF | 12.8333 | 0 | Limit Rugby Run SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
T>T_TUMBNN2_110_3 | 12.8333 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.2 110kV lines, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, Feedback | Outage | Thermal | Tas
VS_050_DYN | 12.75 | 0 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
N^^Q_LDTW_1_B1 | 12.6667 | 0 | Out = Liddell to Tamworth (84), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
N_SILVERTWF_FLT_80 | 12.5 | 0 | Limit Silverton Wind Farm upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
V>V_RCTS_TX1B_1 | 12.5 | 0 | Out= Red Cliffs 1B 220/66kV transformer, avoid O/L Red Cliffs 2B 66/220kV transformer on trip of Red Cliffs 3A transformer, Feedback | Outage | Thermal | Vic
S:VS_PA_SVC_570 | 12.4167 | 31.25 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | Oscillatory Stability | SA
S::V_TBSE_TBSE_2 | 12.3333 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
V::N_BYPASS_HW_SY_xxx | 12.0833 | 27.9167 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Transient Stability | Vic
V_T_NIL_BL1 | 12.0833 | 13 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Other | Vic
N>N-NIL_DC | 11.75 | 4 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | Thermal | NSW
V_GANWR_SF_BAT_50 | 11.75 | 6.1667 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
#LGAPWF1_E | 11.6667 | 38.4167 | SLGW1L.ENERGY * 1 <= 126 (Wt = 360) | Other | DEFAULT | Quick
Q>NIL_EMBW_EMLV_DS | 11.5833 | 36.1667 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
V>X_NWCB6225+6021_T1 | 11.5833 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1132kV line.(Note: swamped when ML Sever scheme is I/S) | Outage | Thermal | Vic
V^^S_MLSY_2 | 11.4167 | 0.33333 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
V::N_MLMO_xxx | 11.3333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_SMF2_SD2 | 11.3333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Transient Stability | Vic
VSML_FLT_150 | 11.3333 | 0 | Vic to SA on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N_X_MBTE2_A & N_X_MBTE2_B | 11.1667 | 801.6667 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
Q_OKYTX3 | 11.0833 | 0 | Out = Oakey 3T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 67.3MW | Outage | Thermal | Qld
V_BULGANAWF_FLT_60 | 11.0833 | 0 | Limit Bulgana Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_FINLYSF_FLT_50 | 11 | 2.4167 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N^^Q_AR_330_BS1_1_B1 | 10.9167 | 0 | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
V>>V_NIL_23 | 10.5 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
V_WEMENSF_FLT_20 | 10.3333 | 0 | Limit Wemen Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q>NIL_SRMB_M020/1 | 10.25 | 17.3333 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
Q_STR_8C10C_HASF75 | 10.25 | 0 | Limit Haughton SF to 75% if Stan>=3+CalB+C>=2+Glad>=2+ (Stan+Cal+Glad) >=8+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG) 25% if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG). Zero otherwise | Outage | System Strength | Qld
V^SML_KGRC_4 | 10.1667 | 4.1667 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Voltage Stability | Vic
T_T_FASH_2_N-2 | 9.9167 | 5.9167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Other | Tas
V_OWF_TGTSNRBHTN_30 | 9.9167 | 10.6667 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
S-MWPS3-PV_0 | 9.9167 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW | Outage | Unit Zero | SA
SVML_FLT_150 | 9.9167 | 4.4167 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
V::S_TBCP1_SETB_2 | 9.75 | 0 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
S_NBH_0 | 9.5833 | 0 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | Unit Zero | SA
N^^Q_ARDM_B1 | 9.5 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
N^^Q_LS_VC_B1 | 9.4167 | 1.9167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
N^^V_LTYS_1 | 9.3333 | 0 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
#LYA3_E | 9.25 | 0 | VLYP3.ENERGY * 1 <= 430 (Wt = 360) | Other | DEFAULT | Quick
T^V_NIL_9 | 9.1667 | 36.3333 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
V::N_SMF2_SD1 | 9.1667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Transient Stability | Vic
Q_STR_32282_MEWF | 9.0833 | 0 | Limit 75% to Mt Emerald WF during day or no limit during night if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),. Zero otherwise. . | Outage | System Strength | Qld
V_MURRAWRWF_FLT_15 | 8.9167 | 21.6667 | Limit Murra Warra Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_STR_7C9C_MEWF | 8.8333 | 0 | Mt Emerald WF to 100% of Max capacity if Stan>=3+CalB+C>=2+Glad>=3+ (Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG).80% if Stan>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>2 or if Stan>=3+Glad>=2+(Stan+Cal+Glad)>=6+Kar>2 .Zero otherwise | Outage | System Strength | Qld
#VIC1-NSW1_E_E | 8.75 | 0 | VIC1-NSW1. * 1 <= 700 (Wt = 35) | Other | DEFAULT | Quick
T^T_LIPM_1 | 8.75 | 0 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Voltage Stability | Tas
V::N_MLTX_xxx | 8.75 | 22.5833 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>V_WETS_BTX_1 | 8.75 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr, prevent pre-contingent overload the remaining Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback. | Outage | Thermal | Vic
S-BUPV2_0 | 8.6667 | 2.9167 | Discretionary upper limit for Bungala Stage 2 PV generation of 0 MW | Outage | Unit Zero | SA
VS_250_DYN | 8.5833 | 13.0833 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
S>X_RBPA+CB_06 | 8.5833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage | Thermal | SA
S-BUPV1_0 | 8.5 | 2.9167 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
V^SML_BEKG_4 | 8.3333 | 7 | Out = Bendigo to Kerang 220kV line, avoid voltage collapse for loss of Ballarat to Waubra to Ararat 220kV line | Outage | Voltage Stability | Vic
Q_STR_32282_SMSF | 8.25 | 0 | Limit 75% to Sun Metals SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_7C8C_WHTSF | 8.25 | 0 | Limit Whitsunday SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V::S_SETB_MAXG_2 | 8.25 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with both Black Range series capacitors O/S). | Outage | Transient Stability | SA
V_GANWRSF_ISL_0 | 8.1667 | 0 | Gannawarra Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_BANNERTON_ZERO | 8.0833 | 0.16667 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V>>N-MSUT_2 | 8 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage | Thermal | Vic
S>NIL_BWMP_HUWT | 8 | 10.6667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
S_DVRB2_270 | 7.9167 | 5.4167 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
S>>NIL_TWPA_TPRS | 7.8333 | 0.58333 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
VS_250 | 7.8333 | 1.5 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
V^^N_BADP_1 | 7.8333 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S>>NIL_BWMP_TWPA | 7.75 | 1.1667 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
N^^Q_BCDM_B1 | 7.6667 | 0.25 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
V_ARARATWF_FLT_60 | 7.6667 | 0 | Limit Ararat Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>NIL_SGBN_SGSE-T2 | 7.5833 | 28 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | Thermal | SA
N_LIMOSF21_ZERO | 7.5 | 0 | Limondale 2 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_9C3_10C21_HASF | 7.1667 | 29.4167 | Limit Haughton70% Max capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
N_DARLSF_FLT_100 | 7.0833 | 0 | Limit Darlington Pt Solar Farm upper limit to 100 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_CPSA_44 | 7.0833 | 0 | Discretionary, Condamine PS =< 44MW | Outage | Discretionary | Qld
V>SMLBAHO1 | 7.0833 | 0 | Out = Bendigo to Kerang line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of any 220kV line section between Ballarat and Horsham | Outage | Thermal | Vic
Q_STR_7C2K_KIDSF_3 | 6.9167 | 0 | Limit 80% to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
T_V_NIL_BL1 | 6.9167 | 3.5 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Other | Tas
Q_STR_8C7C1S_CLRSF | 6.8333 | 0 | No limit Clare SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_COLSF | 6.8333 | 0 | No limit Collinsville SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_DAYSF | 6.8333 | 0 | No limit Daydream SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_HAMSF | 6.8333 | 0 | No limit Hamilton SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_HAYSF | 6.8333 | 0 | No limit Hayman SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_KIDSF | 6.8333 | 0 | No limit Kidston SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_MEWF | 6.8333 | 0 | No limit Mt Emerald WF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_RGBSF | 6.8333 | 0 | No limit Rugby Run SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_RRSF | 6.8333 | 0 | No limit Ross River SF if Stan>=2+Cal>=2+Glad>=2+(Stan+Cal+Glad)>=8+Kar>=2,NQLD>350&370(AVG),Ross_FN>250&,470(AVG),(NQLD>450&470(AVG),Ross_FN>250&270(AVG),Stan>=3+Kar=0),50% if Stan>=2+Kar=0) ,80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. 0 otherwise | Outage | System Strength | Qld
Q_STR_8C7C1S_SMSF | 6.8333 | 0 | No limit Sun Metals SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_WHTSF | 6.8333 | 0 | No limit Whitsunday SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),Ross_FN>250&270(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
S_HALWF_0 | 6.8333 | 0 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW | Outage | Unit Zero | SA
#SMCSF1_E | 6.75 | 0 | QTZS1S.ENERGY * 1 <= 79 (Wt = 360) | Other | DEFAULT | Quick
CA_BRIS_4F1FE461_1 | 6.75 | 0 | Constraint Automation, O/L MOBTAB_1:LMOB:Z:132@T_BEND@SA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
S_WATERLWF_RB | 6.75 | 7 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
#DRYCGT2_D_E | 6.6667 | 3.1667 | SDCA2.ENERGY * 1 = 0 (Wt = 755) | Other | DEFAULT | Direction
Q_STR_7C2K_CLRSF_3 | 6.6667 | 0 | Limit 80% to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_HASF | 6.6667 | 0 | No limit Haughton SF if Stan>=2+Cal>=2+Glad>=2+(Stan+Cal+Glad)>=8+Kar>=2,NQLD>350&370(AVG),Ross_FN>250&,470(AVG),(NQLD>450&470(AVG),Ross_FN>250&270(AVG),Stan>=3+Kar=0),50% if Stan>=2+Kar=0),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. 0 otherwise. | Outage | System Strength | Qld
NC_N_VP6 | 6.5833 | 1.9167 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_WHTSF_3 | 6.5833 | 0 | Limit 80% to Whitsunday Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
S>>RBTX2_RBTX1_WEWT | 6.5833 | 4.9167 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage | Thermal | SA
S>>V_MWP3RB_RBNW1 | 6.5833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L Roberstown-North West Bend 132kV line on trip of Nil trip, Feedback | Outage | Thermal | SA
S>VMLMHNW1 | 6.5833 | 22.0833 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
T>>T_NIL_BL_EXP_7C | 6.5833 | 3.9167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
T>T_GTSH_IMP_4K | 6.5833 | 37.6667 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
NC_Q_MPP_2 | 6.5 | 2.9167 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_HAMSF_3 | 6.5 | 0 | Limit 80% to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
V>>N-NIL_HH | 6.5 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL | Thermal | Vic
Q_STR_7C2K_HAYSF_3 | 6.4167 | 0 | Limit 80% to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
Q_STR_32282_CLRSF | 6.3333 | 0 | No upper limit to Clare SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_COLSF | 6.3333 | 0 | No upper limit to Collinsville SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_DAYSF | 6.3333 | 0 | No upper limit to Daydream SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_HAMSF | 6.3333 | 0 | No upper limit to Hamilton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_HAYSF | 6.3333 | 0 | No upper limit to Hayman SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_KIDSF | 6.3333 | 0 | No upper limit to Kidston SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_RGBSF | 6.3333 | 0 | No upper limit to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_RRSF | 6.3333 | 0 | No upper limit to Ross River SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_32282_WHTSF | 6.3333 | 0 | No upper limit to Whitsunday SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_STR_9C10C_CMSF | 6.3333 | 0 | Limit Clermont SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10 +Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG) or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG) . Zero otherwise | Outage | System Strength | Qld
V^T_NIL_9 | 6.3333 | 0 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL | Voltage Stability | Vic
V_DUNDWF1_ZERO | 6.3333 | 34.3333 | Dundonnell wind farm 1 upper limit of 0 MW | Outage | Unit Zero | Vic
SVML^MH-CAP_OFF | 6.25 | 0 | Out= One or both Capacitor banks (i.e. 61 or 62) at Monash O/S or not available for switching, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash. | Outage | Voltage Stability | SA
V>>V_NIL_24 | 6.25 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
V_DUNDWF2_ZERO | 6.25 | 31.9167 | Dundonnell wind farm 2 upper limit of 0 MW | Outage | Unit Zero | Vic
Q_9C3_10C21_MEWF | 6.1667 | 34 | Limit Mt_Emerald 70% capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
Q_STR_9C10C_RGBSF | 6.1667 | 0 | Limit Rugby Run SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG)or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
Q>>CPST_BCRG_CLWU | 6.0833 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
Q_MB_66_CB_E352 | 6.0833 | 0 | Out = Maryborough(T59) 66kV CB E352, limit Susan River to 33.20MW to prevent instability | Outage | System Strength | Qld
N_MBTE1_A | 6 | 29.5833 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
T>T_TUMBNN1_110_3 | 6 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line, avoid O/L Tungatinah to New Norfolk 110kV line on trip of Tungatinah to Meadowbank to New Norfolk No.2 110kV line, Feedback | Outage | Thermal | Tas
Q_STR_7C2K_KIDSF_2 | 5.9167 | 0 | Limit 80% to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_RRSF_3 | 5.9167 | 0 | Limit 80% to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
V_COHUNASF_0INV | 5.9167 | 0 | Constraint to violate if Cohuna Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
Q_9C3_10C21_SMSF | 5.8333 | 0 | Limit Sun_Metals 70% Capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
S>>NIL_RBTU_WEWT | 5.8333 | 0.16667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S>BRDV_BWPA_RHBR | 5.8333 | 9.6667 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S^DVBR_SA_NTH | 5.8333 | 2.3333 | Out = Davenport-Brinkworth 275kV line, Manage voltage collapse in northern SA for the trip of Davenport-Belalie 275kV line(NOTE: ARCHIVE POST COMMISSIONING OF DAVENPORT SYN CONS) | Outage | Voltage Stability | SA
V:S_PA_SVC_550 | 5.8333 | 0 | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage | Oscillatory Stability | Vic
Q_STR_7C2K_DAYSF_3 | 5.75 | 0 | Limit 80% to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HASF_3 | 5.75 | 0 | Limit 80% to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
N>>V_SMDD6 | 5.6667 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
N_SILVERTWF_FLT_50 | 5.6667 | 0 | Limit Silverton Wind Farm upper limit to 50 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
V>>N-NIL_HG | 5.6667 | 0.083333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
VSML_080 | 5.6667 | 3.6667 | Vic to SA on ML upper transfer limit of 80 MW | Outage | Discretionary | Vic
Q_STR_7C2K_COLSF_3 | 5.5833 | 0 | Limit 80% to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
T_T_FASH_10_N-2 | 5.5833 | 10.75 | Out = NIL, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain John Butters and Bastyan to 0 MW as per TAS Networks advice | Outage | Discretionary | Tas
V>>V_NIL_13 | 5.5833 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
Q:N_TW330_CB5102_OSC | 5.5 | 6.8333 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage | Oscillatory Stability | Qld
S-TBSF1_0 | 5.5 | 2.9167 | Discretionary upper limit for Tailem Bend (Coorong) Solar PV of 0 MW | Outage | Unit Zero | SA
V::N_EPMB_xxx | 5.5 | 21.1667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_GANWR_BAT_G_ISL_0 | 5.5 | 0.41667 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
N>>N-NIL_94B | 5.4167 | 0 | Out= Nil, avoid O/L Beryl to Wellington 132 kV (94B) on nil trip, Feedback. Metering at Wellington is used | NIL | Thermal | NSW
N^^V_MSUT_1 | 5.4167 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>>PATW_BWPA_TPRS | 5.4167 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>V_NIL_NIL_RBNW1 | 5.3333 | 0.91667 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | Thermal | SA
T_GRANVH_ZERO | 5.3333 | 10.8333 | Granville Harbour wind farm upper limit of 0 MW | Outage | Unit Zero | Tas
N_BROKENH1_0INV | 5.25 | 0 | Constraint to violate if Broken Hill Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q_STR_9C10C_EMSF | 5.25 | 0 | Limit Emerald SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG) or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
V^^N_DTMN_1 | 5.25 | 0 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
T^V_NIL_8 | 5.1667 | 12.8333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
T_T_FASH_7_N-2 | 5.1667 | 6.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation <= 110% of West Coast load | Outage | Other | Tas
NSA_V_NPSD_100 | 5.0833 | 12 | Newport unit >= 100 MW for Network Support Agreement | Outage | Network Support | Vic
#N-Q-MNSP1_E_E | 5 | 0 | N-Q-MNSP1.ENERGY * 1 <= 125 (Wt = 35) | Other | DEFAULT | Quick
T:T_LIPM_1 | 5 | 0 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Transient Stability | Tas
V>>N-JNWO_RADIAL_2 | 5 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Thermal | Vic
NC_V_KARSF1 | 4.9167 | 0 | Non Conformance Constraint for KARADOC SOLAR FARM | Other | Non-Conformance | Non-Conformance
T>T_PMWA_IMP_4D | 4.9167 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V_OWF_NRB_0 | 4.9167 | 2.8333 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Discretionary | Vic
Q^N_AR_330_BS3_1 | 4.8333 | 0 | Out= Armidale No.3 330kV bus, QLD to NSW voltage stability limit for trip of a Dumaresq to Armidale 330kV line 8E | Outage | Voltage Stability | Qld
Q_DAYDSF1_ZERO | 4.8333 | 2.5833 | Daydream solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
V^SML_HORC_3 | 4.8333 | 0.83333 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
Q_MARYRSF1_10 | 4.6667 | 0 | Maryrorough Solar Farm upper limit of 10 MW | Outage | Discretionary | Qld
Q_EMERASF1_ZERO | 4.5833 | 0.16667 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>RBMW4+TX_NIL_RBTX1 | 4.5833 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, avoid O/L of remaining Robertstown 275/132kV TX on Nil trip, Feedback | NIL | Thermal | SA
V::S_XPAVC_MAXG | 4.5833 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
#SA1_E_20210130 | 4.5 | 0 | Multiple SA1 LHS <= 150 (Wt = 360) | Other | DEFAULT | Quick
I_CTRL_ISSUE_ML | 4.5 | 28.25 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
V_GANWR_BAT_L_ISL_0 | 4.4167 | 26.9167 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
Q_STR_7C2K_RUGSF_3 | 4.3333 | 0 | Limit 80% to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
S>>X_PARB+RB_SBUS_10 | 4.3333 | 0 | Out= Robertstown South 275kV Bus(275kV CBs ONLY O/S with associated 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Para 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N::N_BYCR_2 | 4.25 | 0 | Out = Bannaby to Crookwell (61), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
N::N_UTRV_2 | 4.25 | 0 | Out = Upper Tumut -Ravine (6X), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
N^^Q_AR_330_BS5_1_B1 | 4.25 | 0 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
Q_STR_7C0K9C_HASF | 4.25 | 0 | No limit to Haughton Solar Farm if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=9+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG) or 50% if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,Zero otherwise. | Outage | System Strength | Qld
S>>X_CNRB+CB_01 | 4.25 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
T_BLINK_TV_NGZ | 4.25 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | Outage | Other | Tas
V::N_HYMO_xxx | 4.25 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
#BANGOWF1_E | 4.1667 | 0 | NBA21B.ENERGY * 1 <= 105 (Wt = 360) | Other | DEFAULT | Quick
#V-SA_RAMP_I_F | 4.1667 | 2.0833 | V-SA >= MIN(-78, InitialFlow + 50) (Wt=35) | Other | Ramping | Quick
NC_V_GLRWNSF1 | 4.1667 | 0 | Non Conformance Constraint for GLENROWAN WEST SF1 | Other | Non-Conformance | Non-Conformance
N_FINLYSF1_ZERO | 4.1667 | 3.8333 | Finley solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
T_MRWF_GCS | 4.1667 | 0 | Musselroe wind farm Generator Control Scheme (GCS) constraint to maintain TAS FOS for a Tasmania generator event. Limit Musselroe wind farm based on load available/armed by Musselroe GCS | NIL | Other | Tas
#MINTARO_D_E | 4.0833 | 3.25 | SMPS.ENERGY * 1 = 30 (Wt = 755) | Other | DEFAULT | Direction
N>>Q-LDTW_2 | 4.0833 | 0.083333 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage | Thermal | NSW
N^^V_DPWG_X5_1 | 4.0833 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>>PATW_RBTU_TPRS | 4.0833 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V>>S_MWP3RB_NWRB1 | 4.0833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L North West Bend-Roberstown #1 132kV line on Nil trip, Feedback | Outage | Thermal | SA
V>S_460 | 4.0833 | 0 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage | Thermal | Vic
#VIC1_E_20210319 | 4 | 0 | Multiple VIC1 LHS <= 65 (Wt = 35) | Other | DEFAULT | Quick
T::T_HA_GT_PM_6 | 4 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
S>RBTX1_RBTX2_WEMWP4 | 3.8333 | 31.8333 | Out= Robertstown 275/132kV TX1, avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, | Outage | Thermal | SA
V::N_BABE_xxx | 3.8333 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N^^V_LTWG_1 | 3.75 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_30272_HASF | 3.75 | 0 | Haughton SF to100% if Stan>=3+Glad>=2+ (Stan+Cal+Glad)>=7+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),80% if Stan>=3+Glad>=2+(Stan+Cal+Glad)>=6+Kar>2 .0 otherwise | Outage | System Strength | Qld
Q_STR_30272_SMSF | 3.75 | 0 | Sun Metals SF to100%if Stan>=3+Glad>=2+ (Stan+Cal+Glad)>=7+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),80% if Stan>=3+Glad>=2+(Stan+Cal+Glad)>=6+Kar>2 .0 otherwise | Outage | System Strength | Qld
V::N_DDMB_xxx | 3.75 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_BULGANAWF_FLT_0 | 3.75 | 52.9167 | Limit Bulgana Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
N^^V_LTMS_1 | 3.6667 | 0 | Out = Murray to Lower Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_DARLSF_FLT_60 | 3.6667 | 0 | Limit Darlington Pt Solar Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_BULGANAWF_FLT_50 | 3.6667 | 0 | Limit Bulgana Wind Farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NC_N_CRWASF1 | 3.5833 | 0 | Non Conformance Constraint for COROWA SOLAR FARM | Other | Non-Conformance | Non-Conformance
N^^V_GRYS_1 | 3.5833 | 0 | Out = Gullen Range to Yass (3J), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_COLEASF1_FLT_40 | 3.5833 | 0 | Limit Coleambally solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
S>>X_PARB+RB_SBUS_11 | 3.5833 | 0 | Out= Robertstown South 275kV Bus(275kV CBs ONLY O/S with associated 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Para 275kV line O/S, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>X_RBPA+CB_02 | 3.5833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | Thermal | SA
V^^N_BURC_1 | 3.5833 | 0 | Out = Buronga to Red Cliffs (0X1) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_MACARTHUR_ZERO | 3.5833 | 79 | Macarthur upper limit of 0 MW | Outage | Unit Zero | Vic
Q::N_ARSVC_AR_2L-G | 3.5 | 1.5833 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
S>RBTX2_RBTX1_WEMWP4 | 3.5 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage | Thermal | SA
T>T_FASH_1_N-2 | 3.5 | 3.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Thermal | Tas
CA_BRIS_50737673_1 | 3.4167 | 0 | Constraint Automation, O/L 66:LSM3:Z:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORVM2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
Q>>NIL_CLWU_RGLC | 3.4167 | 23.6667 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL | Thermal | Qld
Q_STR_7C2K_RUGSF_2 | 3.4167 | 0 | Limit 80% to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
T>T_PMWA_110_7 | 3.4167 | 0 | Out= Palmerston to Waddamana 110 kV line, avoid overloading the New Norfolk to Chapel St 110 kV line (flow to South) on trip of New Norfolk to Creek Road 110 kV line, feedback | Outage | Thermal | Tas
V::N_HYSE_xxx | 3.4167 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
QNTE_OSCILLATE | 3.3333 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Discretionary | Qld
Q_STR_8C_7C2K_CMSF | 3.3333 | 0 | No limit to Clermont SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_EMSF | 3.3333 | 0 | No limit to Emerald SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_RGBSF | 3.3333 | 0 | No limit to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
S:V_XPAVC_230 | 3.3333 | 0 | Out = Para SVC 1 and 2 (Note: with both or one Black Range series caps O/S), SA to VIC on Heywood upper transfer limit of 230 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
S_BRBG_CMWF_0 | 3.3333 | 0.16667 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | Unit Zero | SA
V_SHWF_FLT_286 | 3.3333 | 0 | Limit Stockyard Hill wind farm to 286 MW if Heywood flow is above 400 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
#MTGELWF1_E | 3.25 | 2.8333 | VGTW1M.ENERGY * 1 <= 66 (Wt = 360) | Other | DEFAULT | Quick
Q:N_1078 | 3.25 | 2.3333 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
Q_STR_7C2K_CLRSF_2 | 3.25 | 0 | Limit 80% to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S>>BRTX3_BWMP_WTTP | 3.25 | 0 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>RBTU_RBPA_WEWT | 3.25 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
N>N-GITN_TE_C1 | 3.1667 | 0.083333 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
T^^V_GTSH_1 | 3.1667 | 18.5 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Voltage Stability | Tas
Q_STR_7C8C_MEWF | 3.0833 | 0 | Limit Mt Emerald WF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>NIL_CGTB_TUTB_1 | 3.0833 | 0.41667 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL | Thermal | SA
N_FINLYSF_FLT_40 | 3 | 0 | Limit Finley solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>>CPST_CLWU_LCCP | 3 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q_STR_7C2K_COLSF_2 | 3 | 0 | Limit 80% to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S>>TBTU_TBCG_TBMO | 3 | 4.1667 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
V::N_ROSM_xxx | 3 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::S_RBPA_SETB | 3 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Transient Stability | SA
V_MOORBWF_ZERO | 3 | 0 | Moorabool Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
S>X-WTTP+CB_1 | 2.9167 | 0 | Out= Waterloo-Templers 132kV line + associated line CBs O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Mintaro-Waterloo 132kV line(this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
VSML_030 | 2.9167 | 0 | Vic to SA on ML upper transfer limit of 30 MW | Outage | Discretionary | Vic
Q::N_30+38_AR_2L-G | 2.8333 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
Q_STR_7C2K_HASF_2 | 2.8333 | 0 | Limit 80% to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_9C10C_LYSF | 2.8333 | 0 | Limit Lilyvale SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG)or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
Q_YARANSF1_37 | 2.8333 | 0 | Yarranlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
S>>BWMP_TWPA_TPRS | 2.8333 | 0.33333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S>>CGTB1_TUTB_MOTB | 2.8333 | 9.6667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_TBTU_TBMO_1 | 2.8333 | 0.16667 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S>V_RBNW_RBMWP3 | 2.8333 | 0 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage | Thermal | SA
V::N_BEKG_xxx | 2.8333 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_S_ROCOF | 2.8333 | 0 | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | ROC Frequency | Vic
N>N-BAMB_132_OPEN_A | 2.75 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | Thermal | NSW
T>T_TUNN3_110_2 | 2.75 | 0 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
#HILLSTN1_E | 2.6667 | 0 | NDNH1H.ENERGY * 1 <= 30 (Wt = 360) | Other | DEFAULT | Quick
#TAS1_E_20210420 | 2.6667 | 0 | Multiple TAS1 LHS >= 198 (Wt = 360) | Other | DEFAULT | Quick
Q_RGBYRSF1_ZERO | 2.6667 | 0.083333 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>BRDV_RBTU_WEWT | 2.6667 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S_HALWF2_0 | 2.6667 | 0 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
V_KIATAWF_FLT_18 | 2.6667 | 0 | Limit Kiata Wind Farm upper limit to 18 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
S>>RBTU_RBPA_WTTP | 2.5833 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
#TORRB3_E | 2.5833 | 0.083333 | STSB3.ENERGY * 1 = 40 (Wt = 360) | Other | DEFAULT | Quick
N::Q_NIL_KC | 2.5833 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | Transient Stability | NSW
N>>N-NIL_998 | 2.5833 | 0 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
N>>N-NIL__H_15M | 2.5 | 0.083333 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | Thermal | NSW
N_LIMOSF2_FLT_10 | 2.5 | 0 | Limit Limondale 2 solar farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C8C0K_COLSF | 2.5 | 0 | No limit to Collinsville SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_DAYSF | 2.5 | 0 | No limit to Daydream SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_RGBSF | 2.5 | 0 | No limit to Rugby Run SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_RRSF | 2.5 | 0 | No limit to Ross River SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_RGBSF | 2.5 | 0 | Limit Rugby Run SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Strathmore SVC OS if Kar=0),60% if (Stan+Cal+Glad) >=7, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C_SMSF | 2.5 | 0 | Limit Sun Metals SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V::N_DDWO_xxx | 2.5 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N::Q_MUTW_1 | 2.4167 | 0.083333 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
N_BODWF1_ZERO | 2.4167 | 1.5 | Bodangora wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_STR_7C8C_50_HASF | 2.4167 | 0 | No limit to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(50% if Kar=0),40% if (Stan+Cal+Glad) >=7+Kar>2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
I_CTRL_ISSUE_TE | 2.3333 | 1.6667 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
N_COLWF01_ZERO | 2.3333 | 0 | Collector wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q>>CPST_LCCP_CLWU | 2.3333 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage | Thermal | Qld
Q_STR_7C8C0K_HAMSF | 2.3333 | 0 | No limit to Hamilton SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_SMSF | 2.3333 | 0 | No limit to Sun Metals SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S:VS_PA_SVC_420 | 2.3333 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
S>>V_NWRB2_RBNW1 | 2.3333 | 0 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage | Thermal | SA
S>>X_RBTU+CB_7 | 2.3333 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, avoid O/L Robertstown 275/132kV #1 transformer on trip of Robertstown - Para line (this offloads Robertstown TX#2 132/275kV ) | Outage | Thermal | SA
#TORRB4_E | 2.25 | 0 | STSB4.ENERGY * 1 = 40 (Wt = 360) | Other | DEFAULT | Quick
NC_N_GULLRSF1 | 2.25 | 0 | Non Conformance Constraint for Gullen Range Solar Farm | Other | Non-Conformance | Non-Conformance
NC_N_MANSLR1 | 2.25 | 0 | Non Conformance Constraint for MANILDRA SOLAR FARM | Other | Non-Conformance | Non-Conformance
Q_STR_7C8C0K_HAYSF | 2.25 | 0 | No limit to Hayman SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
S>>NIL_BWMP_BRTW | 2.25 | 3.1667 | Out= Nil, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
S_TIPSB_270 | 2.25 | 0 | Out = NIL, Loss of Torrens Island A Power Station declared credible as a single credible contingency, discretionary upper limit for TIPSB1+TIPSB2+TIPSB3+TIPSB4 <= 270 MW | Outage | Discretionary | SA
V::N_HORC_xxx | 2.25 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_DUNDWF3_ZERO | 2.25 | 34 | Dundonnell wind farm 3 upper limit of 0 MW | Outage | Unit Zero | Vic
V_ELAINEWF_ZERO | 2.25 | 3.25 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
#WALGRVL1_E | 2.1667 | 0 | NSWB2W.ENERGY * 1 <= 47 (Wt = 360) | Other | DEFAULT | Quick
NC_Q_OAKEY1SF | 2.1667 | 1.25 | Non Conformance Constraint for OAKEY 1 SOLAR FARM | Other | Non-Conformance | Non-Conformance
NSA_V_BDL0xxx | 2.1667 | 5.5833 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Network Support | Vic
Q_STR_7C2K_HAMSF_2 | 2.1667 | 0 | Limit 80% to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
V::S_BLKRG_TBSE_2 | 2.1667 | 0 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
Q::N_AR_CP1_AR_2L-G | 2.0833 | 0 | Out = Armidale capacitor bank (80MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
#V-SA_RAMP_E_F | 2.0833 | 0.58333 | V-SA <= MAX(30, InitialFlow - 30) (Wt=35) | Other | Ramping | Quick
N>>N-NIL_67 | 2.0833 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL | Thermal | NSW
N^^Q_LDMU_1_B1 | 2.0833 | 1.3333 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
Q_STR_211383_9_CLRSF | 2.0833 | 3.3333 | Limit Clare SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_COLSF | 2.0833 | 3.3333 | Limit Collinsville SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_DAYSF | 2.0833 | 3.3333 | Limit Daydream SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_HAMSF | 2.0833 | 3.3333 | Limit Hamilton SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_HAYSF | 2.0833 | 3.3333 | Limit Hayman SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_KIDSF | 2.0833 | 3.3333 | Limit Kidston SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_RGBSF | 2.0833 | 3.3333 | Limit Rugby Run SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_RRSF | 2.0833 | 3.3333 | Limit Ross River SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_WHTSF | 2.0833 | 3.3333 | Limit Whitsunday SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_311393_SMSF | 2.0833 | 17.1667 | Limit Sun Metals SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
S_NIL_STRENGTH_2 | 2.0833 | 0 | Maximum limit (1870 MW + Vic to SA on Heywood) for South Australian non-synchronous generation for higher number synchronous generators online for system strength requirements | NIL | System Strength | SA
T>T_SH_TX | 2.0833 | 0 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Thermal | Tas
V>>N-LTMS_1 | 2.0833 | 0 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage | Thermal | Vic
V^^S_SETB_TBSE_2 | 2.0833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Voltage Stability | SA
NC_N_DARLSF1 | 2 | 0.33333 | Non Conformance Constraint for DARLINGTON POINT SF | Other | Non-Conformance | Non-Conformance
NC_N_VP5 | 2 | 2.3333 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_RRSF_2 | 2 | 0 | Limit 80% to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S>>BRTW_BWPA_WTTP | 2 | 0.25 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>X_CNRB+CB_04 | 2 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 132/275kV TX2 on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
V:T_SHGT_BL_1 | 2 | 0.33333 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
N_COLEASF1_FLT_50 | 1.9167 | 2.1667 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
T>T_NIL_BL_3C | 1.9167 | 7.75 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
V>>V-LTWG_RADIAL_1 | 1.9167 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, 15 min ratings; Feedback. Swamp if VBB/SIPS available | Outage | Thermal | Vic
N>>N-NIL_DPTX_2 | 1.8333 | 4.6667 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
NC_N_MP1 | 1.8333 | 0.25 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_BULBESG1 | 1.8333 | 0 | Non Conformance Constraint for BULGANA BESS | Other | Non-Conformance | Non-Conformance
QNI_SOUTH_1000_DYN | 1.8333 | 0 | QLD to NSW on QNI upper transfer limit of 1000 MW, dynamic headroom, DS formulation only. | Outage | Transient Stability | Qld
Q_STR_7C8C0K_KIDSF | 1.8333 | 0 | No limit to Kidston SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
T>T_NIL_BL_110_5 | 1.8333 | 0 | Out = Nil, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | NIL | Thermal | Tas
T>T_NIL_BL_IMP_7CC | 1.8333 | 1 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
V>S_460_DYN | 1.8333 | 0 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | Vic
#LIMOSF11_E | 1.75 | 214.9167 | NBSF1L.ENERGY * 1 <= 220 (Wt = 360) | Other | DEFAULT | Quick
S>>BRBG_BGTX_HUWT | 1.75 | 0.25 | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | Thermal | SA
S>>X_RBPA+CB_04 | 1.75 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Templers West-Para 275kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | Thermal | SA
V::S_BLKRG_MAXG_2 | 1.75 | 0 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | Transient Stability | SA
V_DDWF_MOPS_600 | 1.75 | 0 | Limit Dundonnell wind farm and Mortlake GT combined upper limit to 600 MW | Outage | Discretionary | Vic
NC_V_GANNSF1 | 1.6667 | 0 | Non Conformance Constraint for GANNAWARRA SOLAR | Other | Non-Conformance | Non-Conformance
N_WELLSF1_ZERO | 1.6667 | 0 | Wellington solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
QNI_SOUTH_1150_DYN | 1.6667 | 8.3333 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Transient Stability | Qld
T>T_PMWA_110_6 | 1.6667 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
V_GANWRSF_0INV | 1.5833 | 0.16667 | Constraint to violate if Gannawarra Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
CA_BRIS_50B292E2_1 | 1.5833 | 0 | Constraint Automation, O/L 64:LSM2:I:330@TUMUT3@NSW for CTG LXPD on trip of LOWER TUMUT-CANBERRA 07 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N::N_CTYS_2 | 1.5833 | 0 | Out= Collector -Yass (3L), stability limit (Snowy-NSW) for loss of Yass-Marulan (5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | Transient Stability | NSW
N>N-ARCH_87_TE_C1 | 1.5833 | 1.5833 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
NC_N_LIMOSF11 | 1.5833 | 0 | Non Conformance Constraint for LIMONDALE SF 1 | Other | Non-Conformance | Non-Conformance
NC_Q_SWAN_E | 1.5833 | 0.91667 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance | Non-Conformance
Q_STR_7C2K_HAYSF_2 | 1.5833 | 0 | Limit 80% to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S^NIL_PL_MAX | 1.5833 | 0.33333 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
V>>N-JNWO_RADIAL_1 | 1.5833 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
VSML_105 | 1.5833 | 0 | Vic to SA on ML upper transfer limit of 105 MW | Outage | Discretionary | Vic
VSML_160 | 1.5833 | 0 | Vic to SA on ML upper transfer limit of 160 MW | Outage | Discretionary | Vic
N:V_WA_BUSA_BWRG | 1.5 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage | Transient Stability | NSW
Q>>NIL_STCP_RGLC | 1.5 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Stanwell to Calliope River (848+812) line, Feedback | NIL | Thermal | Qld
#N-Q-MNSP1_RAMP_I_F | 1.4167 | 0 | N-Q-MNSP1 >= MIN(-17, InitialFlow + 80) (Wt=35) | Other | Ramping | Quick
N::N_CNSD_2 | 1.4167 | 0.5 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
NC_N_HUMENSW | 1.4167 | 0.5 | Non Conformance Constraint for Hume Hydro Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YENDWF1 | 1.4167 | 0.41667 | Non Conformance Constraint for YENDON WIND FARM 1 | Other | Non-Conformance | Non-Conformance
NC_V_YWPS3 | 1.4167 | 1.4167 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance | Non-Conformance
S>>V_NIL_NIL_RBMW3 | 1.4167 | 3.25 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
S>>X_RBTU+CB_2 | 1.4167 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) | Outage | Thermal | SA
V::S_XSEVC_MAXG | 1.4167 | 0 | Out= Both South East SVC1 & SVC 2 O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V^^N_UTRV_1 | 1.4167 | 0 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>N_LSDU_9U6_1 | 1.3333 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | Thermal | NSW
NRM_VIC1_SA1 | 1.3333 | 0 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue | Negative Residue
N^^V_BUDP_1 | 1.3333 | 15.5 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_BKHSF_44INV | 1.3333 | 0.33333 | Limit Broken Hill Solar Farm upper limit to 0 MW if number of inverter available exceed 44. Constraint swamp out if number of inverter available not exceed 44. This is to manage voltage oscillation. DS only | Outage | System Strength | NSW
Q_STR_7C8C0K_MEWF | 1.3333 | 0 | No limit to Mt Emerald WF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_YARANSF1_ZERO | 1.3333 | 0.083333 | Yarranlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
S:VS_XPAVC_460 | 1.3333 | 4.4167 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
S>>RBTU_TWPA_TPRS | 1.3333 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
T>T_NIL_BL_5C | 1.3333 | 3.4167 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
V>V_HWJL4_R_1 | 1.3333 | 0 | Out = Hazelwood to Jeeralang No.4 220kV line OR Hazelwood to Jeeralang No.4 line No.4 bus 220kV CB, avoid O/L MWTS B3 220/66kV txfmr for trip of HWPS A4 500/220kV txfmr, Radial mode, YWG1 on 500kV. Swamp out if YWG1 on 220kV mode | Outage | Thermal | Vic
VSML_190 | 1.3333 | 0 | Vic to SA on ML upper transfer limit of 190 MW | Outage | Discretionary | Vic
V_WETX_BANN_70 | 1.3333 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr, limit Bannerton Solar Farm upper limit to 70 MW | Outage | Discretionary | Vic
#BRYB1WF1_E | 1.25 | 0 | VBBT1B.ENERGY * 1 <= 122 (Wt = 360) | Other | DEFAULT | Quick
N>>N-PKWL_94K_3 | 1.25 | 2.8333 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | Outage | Thermal | NSW
Q>SRMB_M020/2_M020/1 | 1.25 | 0 | Out= Susan River to Maryborough 66kV line section 2 (M020/2), avoid O/L on Susan River to Maryborough 66kV line section 1 (M020/2) trip of Nil | Outage | Thermal | Qld
Q_DDSF1_ZERO | 1.25 | 0 | Darling Downs solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
T_FARC1_2 | 1.25 | 0 | Out=Farrell - Reece 1 220KV line. Discretionary 144 MW limit on Reece 2 + Granville Harbour WF | Outage | Discretionary | Tas
T_T_TU_105 | 1.25 | 0 | Discretionary 105 MW upper limit on Tungatinah | Outage | Discretionary | Tas
CA_BRIS_507E31FE_1 | 1.1667 | 0 | Constraint Automation, O/L 66:LSM3:Z:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
N::V_DDSM_MSDD | 1.1667 | 0 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
Q_MARYRSF1_5MW | 1.1667 | 0 | Maryrorough Solar Farm upper limit of 5 MW | Outage | Discretionary | Qld
S-MWPS2-PV_0 | 1.1667 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW | Outage | Unit Zero | SA
S>>BWMP_RBTU_WTTP | 1.1667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V::S_RBTU_MAXG | 1.1667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V_BANSF_22INV | 1.1667 | 3.3333 | Limit Bannerton Solar Farm upper limit to 0 MW if number of inverter available exceed 22. Constraint swamp out if number of inverter available not exceed 22. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
#JUNEESF1_E | 1.0833 | 0 | NWGJ1J.ENERGY * 1 <= 22 (Wt = 360) | Other | DEFAULT | Quick
#VBBG1_E | 1.0833 | 0 | VMLB1V.ENERGY * 1 <= 125 (Wt = 35) | Other | DEFAULT | Quick
N_WRWSF_ZERO | 1.0833 | 0 | White Rock wind farm and White Rock solar farm upper limit of zero MW | Outage | Discretionary | NSW
Q_MEWF1_ZERO | 1.0833 | 211 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C2K_DAYSF_2 | 1.0833 | 0 | Limit 80% to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S-MWPS1-PV_0 | 1.0833 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 1 PV generation of 0 MW | Outage | Unit Zero | SA
S>RBMW4+TX_NIL_RBTX2 | 1.0833 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, avoid O/L of remaining Robertstown 132/275kV TX on Nil trip, Feedback | NIL | Thermal | SA
V::N_X_HWSM_ROSM_xxx | 1.0833 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>V_X_HWTX1_TWO_R_1 | 1.0833 | 0 | Out= Hazelwood A1 and either A2 or A3 or A4 500/220kV transformers, avoid O/L the remaining HWTS A 500/220kV transformer on trip of the other HWTS A transformer, Radial Mode, YWG1 on 500kV, Feedback | Outage | Thermal | Vic
V^^S_TBCB94_35_SETB | 1.0833 | 0 | Out= Tailem Bend 275kV CB6594 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Voltage Stability | SA
V_MURRAWR_ZERO | 1.0833 | 2.8333 | Murra Warra wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
#PPCCGT_E | 1 | 3.9167 | SPPT.ENERGY * 1 <= 470 (Wt = 35) | Other | DEFAULT | Quick
#SEBSF1_E | 1 | 0 | NWGJ2S.ENERGY * 1 <= 30 (Wt = 360) | Other | DEFAULT | Quick
NC_Q_MPP_1 | 1 | 3.4167 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance | Non-Conformance
Q>CPWO_BI_INTACT | 1 | 15 | Out= 813 or 814,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, Feedback | Outage | Thermal | Qld
Q_HAUGHTSF1_ZERO | 1 | 106.5833 | Haughton Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
S>>RBTX1_RBTX2_WEWT | 1 | 1.3333 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
T>T_NIL_BL_IMP_7C | 1 | 0 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
T_V_NIL_FCSPS | 1 | 0 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Other | Tas
V::N_SMTT_xxx | 1 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>>V_NIL_5 | 1 | 0 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Thermal | Vic
CA_BRIS_50132A69_1 | 0.91667 | 0 | Constraint Automation, O/L BRIRED_T:LBR:I:132@BUNGAM@SA for CTG LSJA on trip of BLYT_W-MUNN_P 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N::V_MSUT | 0.91667 | 0 | Out= Murray to Upper Tumut (65) line, NSW to Victoria Transient stability limit. | Outage | Transient Stability | NSW
NC_N_FINLYSF1 | 0.91667 | 0.66667 | Non Conformance Constraint for FINLEY SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE4 | 0.91667 | 0 | Non Conformance Constraint for Gladstone 4 Power Station | Other | Non-Conformance | Non-Conformance
N_LIMOSF1_0INV | 0.91667 | 0 | Constraint to violate if Limondale 1 Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
S>>X_RBTU+CB_1 | 0.91667 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) lines, Feedback | Outage | Thermal | SA
T>T_BUSH1_220 | 0.91667 | 0 | Out = Burnie to Sheffield 220kV line, West Coast 220/110 kV parallel open, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer | Outage | Thermal | Tas
V::N_KTSY_xxx | 0.91667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
NC_Q_LILYSF1 | 0.83333 | 0 | Non Conformance Constraint for LILYVALE SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-4 | 0.83333 | 1.3333 | Non Conformance Constraint for Stanwell STAN-4 Power Station | Other | Non-Conformance | Non-Conformance
N^^V_SMTXF2_1 | 0.83333 | 4.1667 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_YARANSF1_37MW_N-1 | 0.83333 | 0 | Limit Yarrenlea Solar Farm to 37 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip, Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
S>>BWMP_BGBR_HUWT | 0.83333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | Thermal | SA
S>LFTI_PPPW_LFTX4 | 0.83333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX4 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Thermal | SA
S>RB_275KV_N_BUS_1 | 0.83333 | 13.8333 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | Thermal | SA
S_V_NIL_ROCOF | 0.83333 | 0 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | SA
V>>V_KTS_TX_A2_2B_R | 0.83333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Thermal | Vic
V^^S_XPAVC_SETB | 0.83333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
V_GANNSF_12INV | 0.83333 | 3.0833 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out if number of inverter available not exceed 12. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
#T-V-MNSP1_RAMP_E_F | 0.75 | 0.083333 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other | Ramping | Quick
NC_Q_TNPS1 | 0.75 | 0.25 | Non Conformance Constraint for Tarong North Power Station | Other | Non-Conformance | Non-Conformance
NC_S_BNGSF1 | 0.75 | 1.3333 | Non Conformance Constraint for Bungala #1 Solar Farm | Other | Non-Conformance | Non-Conformance
NC_S_OSB-AG | 0.75 | 0 | Non Conformance Constraint for Osborne Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YWPS4 | 0.75 | 1.6667 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance | Non-Conformance
NRM_VIC1_NSW1 | 0.75 | 0.083333 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
N^^V_DDWG | 0.75 | 10.5833 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_CRWASF1_ZERO | 0.75 | 0 | Corowa solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_9C3_10C21_3_MEWF | 0.75 | 0 | Limit Mt_Emerald 70% of Max Capacity for 10C(central units)+2Kar+1Bar,NQLD>750&770(AVG),Ross_FN>440&460(AVG),65% for 10C+3Kar+1Bar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),40% for 9C+3Kar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Otherwise | Outage | System Strength | Qld
Q_WHITSF1_ZERO | 0.75 | 0.91667 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>V_RBNW_MWP1NWB | 0.75 | 0 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Morgan Whyalla Pipeline 1 - North West Bend 132kV line on Nil trip, Feedback | Outage | Thermal | SA
T>T_LIPM_110_2A | 0.75 | 0 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
T_FAJB | 0.75 | 0.16667 | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
T_T_FASH2_2 | 0.75 | 0 | Out = Farrell to Sheffield no.2 220kV line, Farrell bus split, limit John Butters, Bastyan and Mackintosh to greater than 90% West Coast load | Outage | Other | Tas
V^^SML_ARWBBA_1 | 0.75 | 0 | Out = Ballarat to Waubra to Ararat 220kV line (or any line section between Ballarat and Ararat), avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
V_CWWF_FLT_40 | 0.75 | 0 | Limit Crowlands Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KARSF_12INV | 0.75 | 12.6667 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out otherwise. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
V_WEMENSF_21INV | 0.75 | 3.25 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
#DRYCGT1_D_E | 0.66667 | 3.1667 | SDCA1.ENERGY * 1 = 35 (Wt = 755) | Other | DEFAULT | Direction
#DRYCGT3_D_E | 0.66667 | 10.6667 | SDCA3.ENERGY * 1 = 35 (Wt = 755) | Other | DEFAULT | Direction
#QLD1_E_20210406 | 0.66667 | 0 | Multiple QLD1 LHS >= 700 (Wt = 35) | Other | DEFAULT | Quick
N::N_UTYS_2 | 0.66667 | 8.3333 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
N>>Q_LDMU_B | 0.66667 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage | Thermal | NSW
NC_N_ER02 | 0.66667 | 0 | Non Conformance Constraint for Eraring ER02 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_MOLNGSF1 | 0.66667 | 0 | Non Conformance Constraint for MOLONG SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_N_WELLSF1 | 0.66667 | 0 | Non Conformance Constraint for WELLINGTON SF | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE6 | 0.66667 | 0 | Non Conformance Constraint for Gladstone 6 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_BNGSF2 | 0.66667 | 2.75 | Non Conformance Constraint for Bungala #2 Solar Farm | Other | Non-Conformance | Non-Conformance
NC_V_BALBG1 | 0.66667 | 0 | Non Conformance Constraint for BALLARAT BATT (GEN) | Other | Non-Conformance | Non-Conformance
NC_V_EILDON2 | 0.66667 | 0 | Non Conformance Constraint for Eildon 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YWPS1 | 0.66667 | 0.083333 | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_YWPS2 | 0.66667 | 0.83333 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance | Non-Conformance
Q>>CLWU_BCRG_BCCP | 0.66667 | 0.5 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
Q_STR_7C8C0K_CLRSF | 0.66667 | 0 | No limit to Clare SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
SVML_080 | 0.66667 | 0.5 | SA to Vic on ML upper transfer limit of 80 MW | Outage | Discretionary | SA
T_GO_300 | 0.66667 | 0 | Discretionary 300 MW upper limit on total Gordon generation | Outage | Discretionary | Tas
V::S_PAVC1_SETB | 0.66667 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
V>>N-LTWG_RADIAL_1 | 0.66667 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
N_DARLSF1_ZERO | 0.66667 | 91.9167 | Darlington Point solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>>N-NIL_64 | 0.58333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | Thermal | NSW
N>>V-NIL_0X1 | 0.58333 | 0.083333 | Out= NIL, avoid O/L Buronga to Redcliff (OX1) on Nil trip, Feedback | NIL | Thermal | NSW
N>N_LSDU_9U6_3 | 0.58333 | 0 | Out= one of Lismore 132 to Mullumbimby 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line for trip of 9G5 (Mullumbimby to Ewingsdale) 132kV line | Outage | Thermal | NSW
NC_N_JUNEESF1 | 0.58333 | 0 | Non Conformance Constraint for JUNEE SF | Other | Non-Conformance | Non-Conformance
NC_N_SUNRSF1 | 0.58333 | 0 | Non Conformance Constraint for SSF1 | Other | Non-Conformance | Non-Conformance
QN_1000 | 0.58333 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage | Discretionary | Qld
Q_YARANSF1_37MW | 0.58333 | 0 | Yarrenlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
S>>PARS_BWPA_TWPA | 0.58333 | 0 | Out= Roseworthy - Para 132kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>RBTU_BWMP_TWPA | 0.58333 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>RBPA_BWMP_HUWT | 0.58333 | 0 | Out= Robertstown-Para 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | Thermal | SA
S_CNLK_270 | 0.58333 | 0 | Out =Canowie-Mt Lock 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3 + Hornsdale battery (i.e. generation + load component)<= 270 MW | Outage | Discretionary | SA
T>T_FASH_2_N-2 | 0.58333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.1 transformer | Outage | Thermal | Tas
T_ROCOF_3 | 0.58333 | 0.41667 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
V::S_NIL_TBSE_1 | 0.58333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | Transient Stability | SA
V>>V_NIL_3 | 0.58333 | 0.91667 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback. Swamp if SIPS available | NIL | Thermal | Vic
#BNGSF1_E | 0.5 | 1.5 | SBEM1B.ENERGY * 1 <= 80 (Wt = 360) | Other | DEFAULT | Quick
#EMERASF1_E | 0.5 | 0 | QLIS1E.ENERGY * 1 <= 30 (Wt = 35) | Other | DEFAULT | Quick
N>>N-NIL__3_OPENED & CLOSED | 0.5 | 0.33333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | Thermal | NSW
NC_N_BW01 | 0.5 | 0.41667 | Non Conformance Constraint for Bayswater 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE5 | 0.5 | 0 | Non Conformance Constraint for Gladstone 5 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_KAREEYA4 | 0.5 | 0 | Non Conformance Constraint for Kareeya 4 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_KPP_1 | 0.5 | 0 | Non Conformance Constraint for Kogan Creek Power Station | Other | Non-Conformance | Non-Conformance
NC_V_EILDON1 | 0.5 | 0.083333 | Non Conformance Constraint for Eildon 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_WINTSF1 | 0.5 | 0 | Non Conformance Constraint for WINTON SF | Other | Non-Conformance | Non-Conformance
N^^V_MSUT_KVCW_1 | 0.5 | 0 | Out = Murray to Upper Tumut(65) and Kangaroo Valley to Capital (3W) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_STR_8C0K_MEWF | 0.5 | 0 | Limit Mt Emerald to 100% of Max capacity if Stan>=3+CalB+C>=2+Glad>=2+(Stan+Cal+Glad)>=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG),0 otherwise. | Outage | System Strength | Qld
Q_STR_8C0K_SMSF | 0.5 | 0 | Limit Sun Metals to 100% of Max capacity if Stan>=3+CalB+C>=2+Glad>=2+(Stan+Cal+Glad)>=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG),0 otherwise. | Outage | System Strength | Qld
S>>NIL_RBTU_WTTP | 0.5 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S>NIL_NIL_NWMH2 | 0.5 | 10.3333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
S>NWB6022_TX2 | 0.5 | 0 | Out= North West Bend CB 6022 O/S, avoid O/L North West Bend 275/132kV TX2 on trip of Robertstown-North West Bend #1 132kV line, Feedback | Outage | Thermal | SA
SVML_050 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 50 MW | Outage | Discretionary | SA
T>T_X_TU_LE_WA_TWO_2 | 0.5 | 0 | Out= both Tungatinah to Waddamana 110kV lines (direct and via Lake Echo tee), avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
V::N_JNWO_xxx | 0.5 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_SMSY_xxx | 0.5 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::S_KHKN_MAXG | 0.5 | 1.5833 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V>>V_BURC_5 | 0.5 | 0 | Out= Buronga to Redcliffs (0X1) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
V>>V_KTS_TX_A3_2B_R | 0.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Thermal | Vic
V>V_NIL_6 | 0.5 | 0.33333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
VS_050 | 0.5 | 0.083333 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Discretionary | Vic
#BNGSF2_E | 0.41667 | 424.5 | SBEM2B.ENERGY * 1 <= 80 (Wt = 360) | Other | DEFAULT | Quick
#COLWF01_E | 0.41667 | 0.91667 | NCLW1C.ENERGY * 1 <= 219 (Wt = 360) | Other | DEFAULT | Quick
#GLRWNSF1_E | 0.41667 | 0 | VGNS1G.ENERGY * 1 <= 55 (Wt = 360) | Other | DEFAULT | Quick
I_QNI_ONE_PHASE_N-2 | 0.41667 | 18.5 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Discretionary | Other
N>N-NIL_TE_E1 | 0.41667 | 0.16667 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL | Thermal | NSW
NC_N_BW02 | 0.41667 | 0.16667 | Non Conformance Constraint for Bayswater 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_LD01 | 0.41667 | 0 | Non Conformance Constraint for Liddell LD01 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_CPP_3 | 0.41667 | 0.16667 | Non Conformance Constraint for Callide C CPP_3 | Other | Non-Conformance | Non-Conformance
NC_S_PPCCGT | 0.41667 | 0.91667 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance | Non-Conformance
NC_S_SNUG1 | 0.41667 | 0 | Non Conformance Constraint for Snuggery 1 Power Station | Other | Non-Conformance | Non-Conformance
Q_CLARESF1_ZERO | 0.41667 | 0 | Clare solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_RRSF1_ZERO | 0.41667 | 0.083333 | Ross River solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S-LBBAT-L_0 | 0.41667 | 0 | Discretionary upper limit for Lake Bonney Battery (Load component) of 0 MW | Outage | Unit Zero | SA
S>>CNRB_BWPA_HUWT | 0.41667 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>V_NIL_DVBG_STBG | 0.41667 | 0 | Out= Nil, avoid O/L Snowtown - Bungama 132kV on trip of Davenport - Bungama 275kV line, Feedback | NIL | Thermal | SA
S>RBMW4__WTTP_STBG-T | 0.41667 | 0 | Out= Robertstown - MWP4 O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | Thermal | SA
T>T_PMWA_IMP_4DD | 0.41667 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 2 220 kV line on trip of the Palmerston to Hadspen No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V::N_HWCB_xxx | 0.41667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
VSML_220 | 0.41667 | 55.8333 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Discretionary | Vic
V_KIAMAL_0INV | 0.41667 | 1.6667 | Constraint to violate if Kiamal Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
N>N-ARKK_CH_CB892A | 0.41667 | 0 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Swamp out when all 3 directlink cable O/S, Feedback. TG formulation in PD/ST | Outage | Thermal | NSW
#WDGPH1_E | 0.33333 | 0 | QWDR1W.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
CA_BRIS_4F8E5761_1 | 0.33333 | 0 | Constraint Automation, O/L TU_NN3:LNN3:Z:110@TUNGATIN@TAS for CTG LTAB on trip of LIAPOOTA WADA PALMSTN2 220KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
N>>N-TW_CB5102_1 | 0.33333 | 0 | Out= Tamworth 330kV CB 5102, avoid O/L Tamworth No.1 330/132 kV Tx , flow LV to HV, on trip of Armidale to Tamworth (86) line, Feedback. Nameplate rating of 150MVA is used. OM523 | Outage | Thermal | NSW
NC_Q_DDPS1 | 0.33333 | 0.25 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE2 | 0.33333 | 0.16667 | Non Conformance Constraint for Gladstone 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_GSTONE3 | 0.33333 | 0.16667 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_TORRB3 | 0.33333 | 0 | Non Conformance Constraint for Torrens B3 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_TORRB4 | 0.33333 | 0 | Non Conformance Constraint for Torrens B4 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLB01 | 0.33333 | 0.083333 | Non Conformance Constraint for Jeeralang B - 01 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_STOCKYD1 | 0.33333 | 0 | Non Conformance Constraint for STOCKYARD HILL | Other | Non-Conformance | Non-Conformance
N_BOMENSF1_ZERO | 0.33333 | 1.6667 | Bomen SF upper limit of 0 MW | Outage | Unit Zero | NSW
N_CRWF1_ZERO | 0.33333 | 0 | Crudine Ridge wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_FINLYSF1_0INV | 0.33333 | 0 | Constraint to violate if Finley solar farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
N_MOREESF1_0INV | 0.33333 | 0 | Constraint to violate if Moree Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q::N_LDMU_AR_2L-G | 0.33333 | 0 | Out = Liddell to Muswellbrook (83) line, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
Q>COLTX | 0.33333 | 0 | Out = Collinsville North T1 or T2 132/33 kV transformer, limit Collinsville Solar Farm to 35MW to prevent overload on RMU of the remaining transformer | Outage | Thermal | Qld
Q>NIL_MRTA_C | 0.33333 | 0 | Out = Nil, Oakey PS constrained to the maximum measurement limit of 1900 amps, swamp if Oakey PS runback scheme is not armed. | NIL | Thermal | Qld
Q_CLERMSF1_ZERO | 0.33333 | 0 | Clermont Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_8C0K_HASF | 0.33333 | 0 | Limit Haughton to 100% of Max capacity if Stan>=3+CalB+C>=2+Glad>=2+(Stan+Cal+Glad)>=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG),0 otherwise. | Outage | System Strength | Qld
S>>NIL_RBTX_RBTX_2 | 0.33333 | 0 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL | Thermal | SA
S>NIL_BWMP_RHBR-T | 0.33333 | 0.33333 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
T_V_FCSPS_RAMP | 0.33333 | 2.3333 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Ramping | Tas
V::S_NIL_SETB_SECP_1 | 0.33333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | Transient Stability | SA
V::V_1900 | 0.33333 | 1.1667 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
V^^N_CNYS_1 | 0.33333 | 0 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^N_LTMS_1 | 0.33333 | 0 | Out = Murray to Lower Tumut 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V_BRYBWF_ZERO | 0.33333 | 0 | Berrybank Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
#BARKIPS1_D_E | 0.25 | 0 | SBPS1B.ENERGY * 1 = 32 (Wt = 755) | Other | DEFAULT | Direction
#BRAEMAR3_E | 0.25 | 10.5 | QBRA3.ENERGY * 1 <= 85 (Wt = 360) | Other | DEFAULT | Quick
N>>N-NIL_65 | 0.25 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL | Thermal | NSW
N>>N-NIL__A_15M | 0.25 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Stockdill (1) line, Feedback | NIL | Thermal | NSW
N>N_LSDU_9U6_2 | 0.25 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage | Thermal | NSW
NC_N_COLEASF1 | 0.25 | 0 | Non Conformance Constraint for COLEAMBALLY SF | Other | Non-Conformance | Non-Conformance
NC_N_LD02 | 0.25 | 0 | Non Conformance Constraint for Liddell LD02 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_MP2 | 0.25 | 2 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_YABULU2 | 0.25 | 0 | Non Conformance Constraint for Yabulu 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_NPS | 0.25 | 0 | Non Conformance Constraint for Newport Power Station | Other | Non-Conformance | Non-Conformance
NC_V_VBBG1 | 0.25 | 0 | Non Conformance Constraint for VBB GENERATOR | Other | Non-Conformance | Non-Conformance
N_GOONSF1_20 | 0.25 | 0 | Goonumbla solar farm upper limit of 20 MW | Outage | System Strength | NSW
N_LIMOSF2_FLT_0 | 0.25 | 0 | Limit Limondale 2 solar farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_WR_30_WT-INV | 0.25 | 0.083333 | Limit White Rock wind/solar farm upper limit to 0 MW if number of wind turbine + inverter available exceed 30. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
Q_HAYMSF1_ZERO | 0.25 | 0 | Hayman solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_SRSF1_ZERO | 0.25 | 0 | Susan River Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
S>HUWT_NIL_STBG-T | 0.25 | 0 | Out= Hummocks-Waterloo 132kV line, avoid O/L Snowtown-Bungama T 132kV line on Nil trip, Feedback | NIL | Thermal | SA
S>NIL_NIL_SGMYSE-T2 | 0.25 | 0.66667 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | Thermal | SA
S>VMLMHNW2 | 0.25 | 0 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage | Thermal | SA
S_LB2WF_CONF | 0.25 | 1.9167 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
T>T_TU_MB_NN_N-2_1 | 0.25 | 0.91667 | Out= Nil, Loss of both Tungatinah - Meadowbank - New Norfolk 110kV lines declared credible, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of both Tungatinah to Meadowbank to New Norfolk 110kV lines plus Meadowbank generation. | Outage | Thermal | Tas
TV_ZERO | 0.25 | 0 | Tas to Vic on Basslink upper limit of 0 MW | Outage | Interconnector Zero | Tas
T_LIWY | 0.25 | 0 | Out=Liapootah-Wayatinah 220KV line | Outage | Unit Zero | Tas
T_T_MC_ZERO | 0.25 | 0.25 | Discretionary 0 MW upper limit on Macintosh generation | Outage | Discretionary | Tas
V::S_KHKN_MAXG_2 | 0.25 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V>>N-MSUT_4 | 0.25 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Thermal | Vic
V>>N-WA_330_BUSA | 0.25 | 0 | Out= Wagga 330kV bus A, avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
V>>V_NIL_4C | 0.25 | 0 | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL | Thermal | Vic
V_WKPS12_000 | 0.25 | 0 | Discretionary upper limit for West Kiewa Hydro 1 & 2 aggregate Generation of 0 MW | Outage | Unit Zero | Vic
#GANGARR1_E | 0.16667 | 0 | QWSS1G.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
#MINTARO_E | 0.16667 | 0 | SMPS.ENERGY * 1 >= 29 (Wt = 360) | Other | DEFAULT | Direction
#MUWAWF1_E | 0.16667 | 55.6667 | VMRT1M.ENERGY * 1 <= 160 (Wt = 35) | Other | DEFAULT | Quick
#OAKEY2SF_E | 0.16667 | 125.0833 | QTKS2O.ENERGY * 1 <= 55 (Wt = 360) | Other | DEFAULT | Quick
#VIC1_E_20210331 | 0.16667 | 0 | Multiple VIC1 LHS <= 100 (Wt = 35) | Other | DEFAULT | Quick
CA_SYDS_4F1E1FC4_1 | 0.16667 | 0 | Constraint Automation, O/L 85:LN85:Z:330@ARMIDALE@NSW for CTG LNPC on trip of TAMWORTH-ARMIDALE 86 330KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
N>>V_SMDD5 | 0.16667 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H2 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
NC_N_LD04 | 0.16667 | 0.66667 | Non Conformance Constraint for Liddell LD04 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#1 | 0.16667 | 0.66667 | Non Conformance Constraint for Tarong 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_ADPBA1G | 0.16667 | 0 | Non Conformance Constraint for ADELAIDE DESAL BG1 | Other | Non-Conformance | Non-Conformance
NC_S_WATERLWF | 0.16667 | 0 | Non Conformance Constraint for Waterloo Windfarm | Other | Non-Conformance | Non-Conformance
NC_V_LYA3 | 0.16667 | 0 | Non Conformance Constraint for Loy Yang A3 Power Station | Other | Non-Conformance | Non-Conformance
NRM_NSW1_QLD1 | 0.16667 | 0 | Negative Residue Management constraint for NSW to QLD flow. | NIL | Negative Residue | Negative Residue
N_GNNDHSF1_ZERO | 0.16667 | 0 | Gunnedah solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_GOONSF_11_INV | 0.16667 | 0 | Limit Goonumbla Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
N_MOREESF1_ZERO | 0.16667 | 0 | Moree Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q>NIL_MRTA_B | 0.16667 | 0 | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
Q_9C3_10C21_3_HASF | 0.16667 | 0 | Limit Haughton70% of Max Capacity for 10C(central units)+2Kar+1Bar,NQLD>750&770(AVG),Ross_FN>440&460(AVG),50% for 10C+3Kar+1Bar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),40% for 9C+3Kar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Otherwise | Outage | System Strength | Qld
Q_HAMISF1_ZERO | 0.16667 | 1.0833 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>BWMP_RBTU_TWPA | 0.16667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers West-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>PLTX2_TX1_TX3 | 0.16667 | 0 | Out = Port Lincoln 33/132kV TX2 OR CB4342 O/S, Maximum generation at Port Lincoln to avoid OL Port Lincoln transformer 132/33kV #3 for trip Port Lincoln transformer 132/33kV #1. | Outage | Thermal | SA
S>RBMW4_TWPA_TPRS | 0.16667 | 0 | Out= Robertstown - MWP4 O/S, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
SV_100_DYN | 0.16667 | 0 | SA to Victoria on Heywood upper transfer limit of 100 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
S_LB3_0 | 0.16667 | 0 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | Unit Zero | SA
T>T_NIL_BL_IMP_6EE | 0.16667 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
T_T_FASH_8_N-2 | 0.16667 | 3.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation >= 90% of West Coast load | Outage | Other | Tas
V::S_2SE+PAVC_MAXG | 0.16667 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V>>N-LTYS_CH | 0.16667 | 0 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
V>>SML_NSWRB_11_1 | 0.16667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Balranald to Buronga (X3) 220 kV line, feedback | NIL | Thermal | Vic
V>>V-LTWG_RADIAL_2 | 0.16667 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.1 330kV line for loss of the parallel No.2 line, 15 min ratings; Feedback. Swamp if VBB/SIPS available | Outage | Thermal | Vic
V>>V_EPTT_2B_R | 0.16667 | 0 | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage | Thermal | Vic
V_BANNERTSF_ISL_0 | 0.16667 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_BULGNA_BAT_G_ISL_0 | 0.16667 | 0 | Bulgana Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_MURRAWRWF_30WT | 0.16667 | 6 | Limit Murra Warra Wind Farm upper limit to 0 MW if number of turbine ON exceed 30. Constraint swamp out if number of turbine ON not exceed 30. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
V_VS_MLMO_NETT | 0.16667 | 0.66667 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | FCAS | Vic
V_WEMENSF_0INV | 0.16667 | 0 | Constraint to violate if Wemen Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
V_WEMENSF_FLT_10 | 0.16667 | 0.083333 | Limit Wemen Solar Farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
#BBTHREE3_E | 0.083333 | 0 | TBB13.ENERGY * 1 <= 25 (Wt = 360) | Other | DEFAULT | Quick
#CTHLWF1_E | 0.083333 | 648.1667 | TWC11C.ENERGY * 1 = 0 (Wt = 360) | Other | DEFAULT | Quick
#LKBONNY1_E | 0.083333 | 0 | SMAY1.ENERGY * 1 <= 5 (Wt = 360) | Other | DEFAULT | Quick
#WALGRVG1_E | 0.083333 | 0 | NSWB1W.ENERGY * 1 <= 50 (Wt = 360) | Other | DEFAULT | Quick
CA_BRIS_4F1FDF04_1 | 0.083333 | 0 | Constraint Automation, O/L XFMR T_4@T_BEND@SA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N-NSNY_9GU | 0.083333 | 0 | Out = Narromine South to Nyngan132 (9GU) 132 kV line, Upper limit of 52.5 on Nevertire SF, EE advice on 13/02/2020 | Outage | Other | NSW
N::V_MSUT_CNYS_1 | 0.083333 | 0 | Out= Murray to Upper Tumut (65) and Canberra - Yass (9) 330kV lines , NSW to Victoria Transient stability limit. | Outage | Transient Stability | NSW
N:V_DDSM_BWRG | 0.083333 | 0 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage | Transient Stability | NSW
N>>N-NIL_61 | 0.083333 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) using 15 mins rating on trip of Yass to Marulan (5) line, Feedback | NIL | Thermal | NSW
N>>N-NIL_DPTX | 0.083333 | 0.083333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL | Thermal | NSW
N>N-BALS_66_OPEN_A | 0.083333 | 0 | Out = Any 2 66 kV lines in parallel between Lismore and Ballina that opens the 66 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | Thermal | NSW
NC_N_CG2 | 0.083333 | 0 | Non Conformance Constraint for Colongra 2 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_ER03 | 0.083333 | 0.083333 | Non Conformance Constraint for Eraring ER03 Power Station | Other | Non-Conformance | Non-Conformance
NC_N_GNNDHSF1 | 0.083333 | 0 | Non Conformance Constraint for GUNNEDAH SF | Other | Non-Conformance | Non-Conformance
NC_N_LIMOSF21 | 0.083333 | 0 | Non Conformance Constraint for LIMONDALE SF 2 | Other | Non-Conformance | Non-Conformance
NC_N_TALWA1 | 0.083333 | 0.16667 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_BARRON-1 | 0.083333 | 0 | Non Conformance Constraint for Barron Gorge 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_CALL_B_2 | 0.083333 | 0 | Non Conformance Constraint for Callide B_2 | Other | Non-Conformance | Non-Conformance
NC_Q_CLERMSF1 | 0.083333 | 2.75 | Non Conformance Constraint for CLERMONT SOLAR FARM | Other | Non-Conformance | Non-Conformance
NC_Q_COOPGWF1 | 0.083333 | 0 | Non Conformance Constraint for COOPERS GAP WF | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-2 | 0.083333 | 0.41667 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_STAN-3 | 0.083333 | 0.25 | Non Conformance Constraint for Stanwell STAN-3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_TARONG#3 | 0.083333 | 0 | Non Conformance Constraint for Tarong 3 Power Station | Other | Non-Conformance | Non-Conformance
NC_Q_W/HOE#1 | 0.083333 | 0.083333 | Non Conformance Constraint for Wivenhoe No 1 Power Station | Other | Non-Conformance | Non-Conformance
NC_S_AGLHAL | 0.083333 | 0.58333 | Non Conformance Constraint for AGL Hallet Power Station | Other | Non-Conformance | Non-Conformance
NC_S_BARKIPS1 | 0.083333 | 0.25 | Non Conformance Constraint for BARKER INLET PS | Other | Non-Conformance | Non-Conformance
NC_S_QPS4 | 0.083333 | 0 | Non Conformance Constraint for Quarantine QPS4 Power Station | Other | Non-Conformance | Non-Conformance
NC_T_LI_WY_CA | 0.083333 | 0 | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations | Other | Non-Conformance | Non-Conformance
NC_V_BULGANA1 | 0.083333 | 0 | Non Conformance Constraint for BULGANAGREENPOWERHUB | Other | Non-Conformance | Non-Conformance
NC_V_JLA01 | 0.083333 | 0 | Non Conformance Constraint for Jeeralang A - 01 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLA02 | 0.083333 | 0.083333 | Non Conformance Constraint for Jeeralang A - 02 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_JLA03 | 0.083333 | 0 | Non Conformance Constraint for Jeeralang A - 03 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_LYA2 | 0.083333 | 0.083333 | Non Conformance Constraint for Loy Yang A2 Power Station | Other | Non-Conformance | Non-Conformance
NC_V_MORTLK12 | 0.083333 | 0.25 | Non Conformance Constraint for Mortlake GT unit 2 | Other | Non-Conformance | Non-Conformance
N_BOCORWF1_ZERO | 0.083333 | 0 | Boco Rock WF upper limit of 0 MW | Outage | Unit Zero | NSW
N_GOONSF1_ZERO | 0.083333 | 0 | Goonumbla solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N_SUNRSF1_0INV | 0.083333 | 0 | Constraint to violate if Sunraysia Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | NSW
Q:N_TW330_CB5102_1 | 0.083333 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW transient stability limit for trip of a Qld potline | Outage | Transient Stability | Qld
Q>NIL_MRTA_A | 0.083333 | 0 | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
Q>YLTX_DS | 0.083333 | 1.3333 | Out = Nil, limit to Maryrorough Solar Farm to dynamic runback limit of Yarranlea 110/33kV transformer(s), DS formulation only | NIL | Thermal | Qld
QN_1078_OSC_AUTO | 0.083333 | 0 | Upper transfer limit of 1078 MW from Qld to NSW on QNI, Active only when QNI mode cannot be monitored | NIL | Oscillatory Stability | Qld
S:V_PA_SVC_270-DS | 0.083333 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW (NOTE:DS RHS ONLY) | Outage | Oscillatory Stability | SA
S>>BWMP_BRTW_WTTP | 0.083333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
S>>NIL_BRTW_WTTP | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | NIL | Thermal | SA
S>>PARB_RBTU_RBMWP4 | 0.083333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>>RBTX_BRTW_WTTP | 0.083333 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | Outage | Thermal | SA
S>>V_NIL_NIL_MW1NWB | 0.083333 | 0 | Out = Nil, avoid overloading Morgan Whyalla Pump 1- North West Bend 132kV line for no contingencies, feedback | NIL | Thermal | SA
S>BRTW_BWPA_HUWT | 0.083333 | 0.66667 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>HUWT_BGTX_RHBR-T | 0.083333 | 4.1667 | Out= Hummocks-Waterloo 132kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Bungama 132/275kV TX, Feedback | Outage | Thermal | SA
S>MYTX1_44248OPN_LB2 | 0.083333 | 0 | Out = Mayura No.1 132/33kV transformer O/S (with 33kV bus tie isolator 44248 open), Lake Bonney 2 Windfarm is constraint to a max of 60 MW | Outage | Other | SA
S>NIL_NIL_MYSG-T | 0.083333 | 0.083333 | Out = NIL; Limit LB2 and LB3 generation to avoid OL Mayura - Snuggery T 132kV line. | NIL | Thermal | SA
S>NIL_NIL_SGBN | 0.083333 | 0.16667 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | Thermal | SA
S>NIL_NWMH1_NWMH2 | 0.083333 | 0 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on trip of North West Bend-Monash #1 132kV line, Feedback | NIL | Thermal | SA
S>PLTX3_TX2_TX1 | 0.083333 | 0 | Out = Port Lincoln 33/132kV TX3 (Note: with CB4636 & CB4543 OPEN) O/S, Maximum generation at Port Lincoln to avoid OL Port Lincoln transformer 132/33kV #1 for trip Port Lincoln transformer 132/33kV #2. | Outage | Thermal | SA
S>SETX_SETX_PWKN | 0.083333 | 0 | Out= One South East 275/132kV transformer O/S (i.e. TX ONLY O/S with associated TX CBs I/S), avoid O/L Penola West-KinCraig 132kV line on trip of remaining 132/275kV South East TX, Feedback | Outage | Thermal | SA
S^BRTW_SA_NTH | 0.083333 | 0 | Out = Brinkworth-Templers West 275kV line, Manage voltage collapse in northern SA for the trip of Robertstown-Mokota 275kV line | Outage | Voltage Stability | SA
S_LBMY_2B-LB2 | 0.083333 | 0 | Out= Mayurra-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN), upper limit on Lake Bonney 2 WF generation constrained to 60 MW. | Outage | Discretionary | SA
S_LBMY_2B-LB3 | 0.083333 | 0 | Out= Mayurra-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN), Lake Bonney 3 constrained to 0 MW | Outage | Unit Zero | SA
T>T_NIL_BL_110_8_1 | 0.083333 | 0.16667 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Thermal | Tas
T_BLINK_VT_NGZ | 0.083333 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow < 0, Basslink Target MW <= 0, swamped if Basslink Metered Flow > -0.1 DS only. | Outage | Other | Tas
V::S_BLKRG_MAXG_3 | 0.083333 | 0 | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | Outage | Transient Stability | SA
V::S_NIL_MG_TB_2-DS | 0.083333 | 0 | Out =Nil(Note: with both Black Range series capacitors O/S); Vic-SA Tran. Stab limit for loss of SA largest generator with loss of Torrens Island B PS declared as credible (South East Capacitor Available). (NOTE: DS RHS ONLY) | NIL | Transient Stability | SA
V:SS_820_HY_TEST | 0.083333 | 0.5 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
V>>N-DDWO_RADIAL_1 | 0.083333 | 0 | Out = Dederang to Wodonga, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Thermal | Vic
V>>N-LTUT_M_15M | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Lower Tumut to Canberra (07) trip; Feedback | Outage | Thermal | Vic
V^^N_CNLT_1 | 0.083333 | 0 | Out = Canberra to Lower Tumut(07), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V^^S_PAVC1_MAXG | 0.083333 | 0.33333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V^^S_PAVC_MAXG | 0.083333 | 0 | Out= Para one SVC (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V^^S_XPAVC_MAXG | 0.083333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
V_ARWF_FSTTRP_5 | 0.083333 | 0.83333 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
V_BANSF_0INV | 0.083333 | 0 | Constraint to violate if Bannerton Solar Farm inverter availability greater than zero. Constraint swamp out otherwise. DS only | Outage | System Strength | Vic
V_BA_BAT_G_ZERO | 0.083333 | 0 | Ballarat Battery (Generation Component) upper limit of 0 MW | Outage | Unit Zero | Vic
V_COHUNASF_ISL_0 | 0.083333 | 0 | Cohuna Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V_CROWLANDS_ZERO | 0.083333 | 0 | Crowlands Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_KIAMSF_FLT_90 | 0.083333 | 0 | Limit Kiamal Solar Farm upper limit to 90 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_MWWF_0_WT12 | 0.083333 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW if Murra Warra wind farm turbine collector group 1 and/or 2 generating. Constraint swamp out if only turbine collector group 3 and/or 4 generating. DS only | Outage | System Strength | Vic
V_VBB_L_ZERO | 0.083333 | 0 | Victorian Big Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | Vic
V_V_HYMO_1 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line, Limit voltage unbalance at the APD 500 kV bus and Heywood 275 kV bus | Outage | Voltage Stability | Vic

## Binding FCAS
Constraint Equation ID | 2021 Hours | 2020 Hours | Description | Type
F_I+LREG_0210 | 7901.25 | 7771.25 | NEM Lower Regulation Requirement greater than 210 MW | NIL
F_I+RREG_0220 | 7689.75 | 5017 | NEM Raise Regulation Requirement greater than 200 MW | NIL
F_I+NIL_MG_R6 | 7559.25 | 6571.0833 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L5 | 7127.9167 | 7261.0833 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R60 | 7075.9167 | 6295.4167 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L60 | 6785.6667 | 6571.0833 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R5 | 6579 | 7270.5833 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL
F_I+ML_L6_0400 | 5952.5 | 4191.25 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL
F_T_AUFLS2_R6 | 4265.25 | 4276.3333 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL
F_T+NIL_ML_L6 | 2616.5 | 184.1667 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L60 | 2558.4167 | 184.25 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R60 | 2394.4167 | 2523.25 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R6 | 2389.25 | 2407.1667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++APD_TL_L5 | 2029.4167 | 2276.8333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 1607.75 | 728 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R60 | 1585.25 | 854.5833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 1525.0833 | 1207.75 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_T+NIL_MG_RECL_R5 | 1486.6667 | 743.9167 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_TASCAP_LREG_0210 | 1483.3333 | 322.9167 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T+NIL_WF_TG_R5 | 1430.8333 | 1076.3333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 1421.1667 | 891.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 1401.3333 | 2754.5 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_T+NIL_WF_TG_R6 | 1386.9167 | 944.0833 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L5 | 1344.0833 | 91.8333 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_BL_L60 | 1172.0833 | 181.9167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_MAIN++ML_L6_0400 | 1166.3333 | 781.25 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_MAIN++RREG_0220 | 964 | 151.1667 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
F_TASCAP_RREG_0220 | 955.8333 | 250.1667 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T_NIL_MINP_R6 | 834.0833 | 1528.0833 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL
F_I+NIL_APD_TL_L6 | 751.0833 | 1981.0833 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_MAIN+NIL_DYN_RREG | 749.5833 | 3201.9167 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL
F_MAIN++LREG_0210 | 681.8333 | 648.4167 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
F_MAIN+NIL_DYN_LREG | 543.6667 | 313.8333 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL
F_T+NIL_MG_R60 | 522.1667 | 847.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T++RREG_0050 | 473.25 | 1048.1667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_T+NIL_MG_R6 | 445 | 787.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T++LREG_0050 | 432.4167 | 261.5 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_T+NIL_MG_R5 | 404.8333 | 1149.25 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T++NIL_ML_L60 | 344.3333 | 152 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_V_APD01_R60 | 328.4167 | 385.3333 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_V_APD01_R6 | 328.4167 | 385.3333 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_MAIN++APD_TL_L6 | 328.25 | 984.9167 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_V_APD01_R5 | 327.1667 | 385.3333 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_Q++MUTW_L6 | 287.9167 | 1164.6667 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_Q++MUTW_L60 | 278.1667 | 1115.5833 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_Q++ARTW_L6 | 272.5 | 69 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
F_Q++ARTW_L60 | 267.1667 | 72.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_I+GFT_TG_R5 | 265.0833 | 165.75 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_I+GFT_TG_R60 | 262.75 | 162.9167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_T+LREG_0050 | 259.1667 | 210.1667 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 258.5 | 207.5 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 255.5833 | 204.8333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 254.8333 | 203.9167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T+RREG_0050 | 251.8333 | 209.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 247.5833 | 202.5 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+RREG_0220 | 242.9167 | 111.25 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL
F_I+CPP_N-2_MG_R5 | 238.4167 | 0 | Out= Nil, loss of all Callide C units declared credible, Global Raise 5 Min requirement | Outage
F_MAIN+ML_L6_0400 | 237.0833 | 102.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 234.6667 | 201.5 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+LREG_0210 | 234.5833 | 195.6667 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL
F_I+CPP_N-2_MG_R6 | 232.0833 | 0 | Out= Nil, loss of all Callide C units declared credible, Global Raise 6 sec requirement | Outage
F_I+CPP_N-2_MG_R60 | 221.4167 | 0 | Out= Nil, loss of all Callide C units declared credible, Global Raise 60 sec requirement | Outage
F_Q++LDTW_L6 | 203.0833 | 108.25 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
F_Q++LDTW_L60 | 182.0833 | 104.6667 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_MAIN++NIL_BL_L6 | 149.75 | 4.6667 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_T++NIL_ML_L6 | 135.75 | 221.75 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_Q++BCDM_L60 | 126.25 | 43.9167 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
F_S++HYSE_L60 | 122.9167 | 28.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
F_Q++ARTW_L5 | 122.75 | 20.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
F_Q++BCDM_L6 | 122.1667 | 44.6667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
F_T++NIL_MG_RECL_R5 | 120.0833 | 125.1667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_I+ML_L6_APD | 102.8333 | 0.41667 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_Q++LDTW_R60 | 102.5 | 4.25 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_I+ML_L6_APD_LD | 97.0833 | 378.25 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage
F_Q++LDTW_R6 | 96.8333 | 2.25 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
F_Q++LDMU_L6 | 96.75 | 6.5 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
F_Q++LDMU_L60 | 92.1667 | 7.6667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
F_I+TTS_TG_R60 | 91.75 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_I+TTS_TG_R5 | 89.1667 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_T++NIL_WF_TG_R5 | 84.1667 | 64 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN++GFT_TG_R60 | 81.4167 | 22.9167 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_Q++MUTW_L5 | 81.1667 | 312.4167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_T++NIL_MG_RECL_R6 | 77.3333 | 66.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_MG_RECL_R60 | 70.6667 | 84.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_S+MLMO_TL_L60 | 69.3333 | 191.8333 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
F_I+ML_L60_0400 | 57.5 | 40.1667 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL
F_ESTN++MLMO_L60 | 57 | 103.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_T++NIL_WF_TG_R60 | 56.5833 | 26.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++8C_L6 | 56.4167 | 12.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
F_Q++8C_L60 | 56 | 10.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
F_I+ML_L5_0400 | 53.5833 | 46.75 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL
F_T++NIL_WF_TG_R6 | 50.25 | 24.4167 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_ESTN++MLMO_L6 | 49 | 27.5 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
F_Q++LDMU_R6 | 45.5833 | 1.3333 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
F_Q++LDMU_R60 | 43.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement | Outage
F_T++NIL_MG_R5 | 41.5 | 97.5 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++MUTW_R6 | 40.8333 | 57.5 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
F_I+GFT_TG_R6 | 40.3333 | 45.1667 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL
F_MAIN++GFT_TG_R5 | 39.6667 | 7.5 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_Q++MUTW_R60 | 39 | 67.75 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
F_MAIN++CP_N-2_MGR60 | 38.4167 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_QNV++MLMO_L6 | 37.5833 | 19.75 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++LDMU_L5 | 37.25 | 1.1667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
F_MAIN++CPP_N-2_MGR6 | 37.0833 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_ESTN++MLMO_L5 | 36.5 | 14.1667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
F_Q++BCDM_L5 | 34.9167 | 11.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
F_T++NIL_MG_R60 | 34.4167 | 59.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_ESTN++HGML_L60 | 33.25 | 1.3333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 60 sec Requirement | Outage
F_Q++LDTW_L5 | 32.0833 | 31.3333 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
F_MAIN++ML_L6_APD_LD | 32.0833 | 174 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
F_Q++LDTW_R5 | 31.6667 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 5 min Requirement | Outage
F_S++HYSE_L6_1 | 31.5833 | 5.4167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_Q++ARTW_R60 | 28.25 | 0.83333 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_QNV++MLMO_L60 | 27.3333 | 20.8333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++ARTW_R6 | 25.4167 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
F_S+MLMO_TL_L6_1 | 24.4167 | 5.5833 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage
F_ESTN++HGTR_L60 | 23.0833 | 1.3333 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_Q++LDMU_R5 | 20.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage
F_I+TTS_TG_R6 | 19.25 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL
F_Q++8E_L60 | 18.75 | 14.5 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage
F_Q++8E_L6 | 18.3333 | 14.6667 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
F_T++NIL_MG_R6 | 18.3333 | 34.5833 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T+CSGO_TG_R60 | 18.25 | 5.5 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_T+CSGO_TG_R5 | 18.1667 | 5.4167 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_ESTN++HGML_L5 | 17.0833 | 0.83333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 5 min Requirement | Outage
F_T+FASH_N-2_RREG | 16.5833 | 3 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_ESTN++HGTR_L5 | 16.1667 | 1.0833 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_MAIN+APD_TL_L6 | 14.9167 | 95.0833 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_ESTN++HGML_L6 | 14.3333 | 0.083333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 6 sec Requirement | Outage
F_ESTN++HYMO_L60 | 14 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
F_Q++8C_L5 | 13.1667 | 5.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
F_QNV++MLMO_L5 | 13.1667 | 0.5 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_MAIN++CPP_N-2_MGR5 | 12.3333 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
F_ESTN++HGTR_L6 | 11.0833 | 0.16667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_MAIN++ML_L6_APD | 10.4167 | 0.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_T++FARE_N-2_TG_R6 | 10.3333 | 0.66667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_Q++8E_L5 | 9.9167 | 2.5 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
F_T+FASH_N-2_TG_R5 | 9.5833 | 1.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T++FASH_N-2_TG_R60 | 9.25 | 6.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN+GFT_TG_R60 | 8.8333 | 5.4167 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_ESTN++HYMO_L6 | 8.8333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
F_T+FASH_N-2_TG_R6_2 | 8.75 | 1.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage
F_T++FASH_N-2_TG_R5 | 8.6667 | 5.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+FASH2_C_TG_R5 | 8.4167 | 0 | Out= Farrell to Sheffield No.2 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_MAIN+GFT_TG_R5 | 8.3333 | 5.4167 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_Q++BCDM_R6 | 8.1667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
F_Q++BCDM_R60 | 7.9167 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
F_MAIN++TTS_TG_R60 | 7.4167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_Q++8C_R6 | 7.1667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 6 sec Requirement | Outage
F_Q++8C_R60 | 7.0833 | 0.16667 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage
F_QNV++HGTR_L60 | 6.9167 | 1.1667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_QNV++HGML_L60 | 6.75 | 1.3333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+FARE_N-2_TG_R5 | 6.75 | 1.0833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_MAIN++GFT_TG_R6 | 5.9167 | 4.1667 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
F_QNV++HGML_L6 | 5.75 | 1.4167 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++ARTW_R5 | 5.5 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
F_T+CSGO_TG_R6_2 | 5.25 | 3.5 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage
F_S++HYSE_L6_2 | 4.9167 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
F_I+LD_N-2_MG_R60 | 4.6667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Global Raise 60 sec requirement | Outage
F_I+LD_N-2_MG_R6 | 4.6667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Global Raise 6 sec requirement | Outage
F_I+LD_N-2_MG_R5 | 4.6667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Global Raise 5 Min requirement | Outage
F_I+ML_L60_APD | 4.6667 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage
F_Q++MUTW_R5 | 4.5833 | 6.6667 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
F_T+CSGO_TG_R6_1 | 4.5 | 4.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage
F_T+FASH2_C_TG_R6 | 4.3333 | 0 | Out= Farrell to Sheffield No.2 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_I+ML_L5_APD | 4.3333 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_T+FASH2_C_TG_R60 | 4.1667 | 0 | Out= Farrell to Sheffield No.2 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_QNV++HGTR_L6 | 4.0833 | 1.0833 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_MAIN++ML_L5_0400 | 3.75 | 5.0833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_QNV++HGTR_L5 | 3.6667 | 0.41667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_S+MLMO_TL_L6_2 | 3.5833 | 17.8333 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage
F_MAIN+ML_L60_0400 | 3.5 | 0.91667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_S_DLBAT-G_R60 | 3.4167 | 0.16667 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage
F_S_TORRB2_R60 | 3.4167 | 0 | Out= NIL, Torrens B2 R60 Requirement <= 0MW | Outage
F_S_TORRB2_R6 | 3.4167 | 0 | Out= NIL, Torrens B2 R6 Requirement <= 0MW | Outage
F_S_DLBAT-G_R6 | 3.4167 | 0.16667 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage
F_MAIN+TTS_TG_R60 | 3.4167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_S_DLBAT-L_L60 | 3.3333 | 0.16667 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage
F_S_DLBAT-L_L6 | 3.3333 | 0.16667 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage
F_S_DLBAT-L_L5 | 3.3333 | 0.16667 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage
F_MAIN+ML_L5_0400 | 3.3333 | 0.91667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T+FARE_N-2_TG_R6_2 | 3.25 | 0.66667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_MAIN+ML_L6_APD_LD | 3.25 | 6.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage
F_NSW_LD_R6 | 3.1667 | 0 | Out= NIL, Liddell Power Station R6 Requirement <= 0MW | Outage
F_QNV++HGML_L5 | 3.1667 | 0.66667 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++FARE_N-2_TG_R5 | 3.0833 | 0.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_NSW_LD_R60 | 3 | 0 | Out= NIL, Liddell Power Station R60 Requirement <= 0MW | Outage
F_T++FARE_N-2_TG_R60 | 3 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_NSW_LD_RREG | 3 | 0 | Out= NIL, Liddell Power Station RREG Requirement <= 0MW | Outage
F_S_TORRB4_R6 | 2.9167 | 0 | Out= NIL, Torrens B4 R6 Requirement <= 0MW | Outage
F_S_TORRB4_R60 | 2.9167 | 0 | Out= NIL, Torrens B4 R60 Requirement <= 0MW | Outage
F_T++COGT_TL_L6 | 2.9167 | 50.5 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_S_DLBAT-G_R5 | 2.9167 | 0.16667 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage
F_T+FASH_N-2_TG_R60 | 2.8333 | 1.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_MAIN+TTS_TG_R5 | 2.75 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL
F_MAIN++LD_N-2_G_R5 | 2.75 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
F_ESTN+MO_TG_R5 | 2.6667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line | Outage
F_T++FASH_N-2_TG_R6 | 2.5 | 4.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+FARE_N-2_TG_R6_1 | 2.5 | 0.41667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_ESTN+MO_TG_R60 | 2.1667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line | Outage
F_Q++8C_R5 | 2.1667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 5 min Requirement | Outage
F_MAIN++LD_N-2_G_R6 | 2.0833 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_MAIN+CPP_N-2_MG_R6 | 2.0833 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+CP_N-2_MG_R60 | 2 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+CPP_N-2_MG_R5 | 2 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 5 Min requirement, Basslink unable to transfer FCAS | Outage
F_T++NIL_ML_L5 | 1.9167 | 0 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_MAIN++TTS_TG_R5 | 1.9167 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
F_MAIN+ML_L6_APD | 1.75 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_ESTN++HYMO_L5 | 1.6667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
F_QNV+MLMO_L6 | 1.5 | 1.8333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_V+NIL_APD01_R60 | 1.3333 | 2.75 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_APD01_R6 | 1.3333 | 2.75 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_S_TORRB3_R60 | 1.3333 | 0 | Out= NIL, Torrens B3 R60 Requirement <= 0MW | Outage
F_STHN++LDTW_L60 | 1.3333 | 0 | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage
F_S_TORRB3_R6 | 1.3333 | 0 | Out= NIL, Torrens B3 R6 Requirement <= 0MW | Outage
F_V+NIL_APD01_R5 | 1.3333 | 2.75 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_Q_W/HOE_R5 | 1.25 | 6 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage
F_QNV+HYMO_L60 | 1.25 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T++BLSPS_EXP_L6_1 | 1.25 | 2.0833 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_T++BLSPS_EXP_L60_1 | 1.25 | 2.0833 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_QNV+MLMO_L60 | 1.25 | 2.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN++ML_L60_0400 | 1.1667 | 4.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T+FARE_N-2_RREG | 1.1667 | 0.41667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_S_TORRB4_RREG | 1.0833 | 0 | Out= NIL, Torrens B4 RREG Requirement <= 0MW | Outage
F_MAIN++ML_L5_APD | 1 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_T+FASH2_C_RREG | 1 | 0 | Out = Farrell to Sheffield No.2 line; Bastyan, John Butters, Tribute and Reece 1, 2 and Mackintosh unavailable for raise regulation | Outage
F_MAIN++LD_N-2_G_R60 | 0.91667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_S_TORRB2_RREG | 0.91667 | 0 | Out= NIL, Torrens B2 RREG Requirement <= 0MW | Outage
F_QNV++HYMO_L60 | 0.91667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_QNV+HYMO_L6 | 0.91667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_S++HYSE_L5 | 0.83333 | 5.0833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
F_T+FASH_N-2_TG_R6_1 | 0.83333 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage
F_S_TORRB3_RREG | 0.83333 | 0 | Out= NIL, Torrens B3 RREG Requirement <= 0MW | Outage
F_QNV+MLMO_L5 | 0.66667 | 0.16667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_QNV++HYMO_L6 | 0.58333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
F_QNV+HGML_L60 | 0.58333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T+FARE_N-2_TG_R60 | 0.58333 | 1.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_ESTN++HYTR_L60 | 0.5 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_T++CSGO_TG_R5 | 0.5 | 4.5833 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_QNV+HYMO_L5 | 0.5 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_T+GTTE_TL_L6 | 0.5 | 21.0833 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_T+GTTE_TL_L60 | 0.5 | 21 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_V_MBMK_L60 | 0.5 | 0 | Lower 60 sec Service Requirement for McKay Creek & Bogong PS set to zero due to outage of Mt Beauty to Mackay 220 kV line | Outage
F_WESTCOAST_LREG_0 | 0.41667 | 1.4167 | LREG FCAS of West Coast Generation limited to 0 MW | Outage
F_NVS+LDTW_L60 | 0.41667 | 0 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_Q++NIL_R5 | 0.41667 | 16.5 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_ESTN++HYTR_L6 | 0.41667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_QNV+HGML_L6 | 0.33333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_QNV+HGML_L5 | 0.33333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+GFT_TG_R6 | 0.33333 | 0.41667 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL
F_ESTN++HYTR_L5 | 0.33333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_QNV+HGTR_L60 | 0.33333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_V_WKIEWA1_L60 | 0.25 | 0 | Out= NIL, West Kiewa 1 L60 Requirement <= 0MW | Outage
F_WESTCOAST_RREG_0 | 0.25 | 1.3333 | RREG FCAS of West Coast Generation limited to 0 MW | Outage
F_T++CSGO_TG_R6 | 0.25 | 6.8333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_Q++8E_R6 | 0.25 | 0 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage
F_T++CSGO_TG_R60 | 0.16667 | 9.9167 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_T++NIL_BLSPS_R5 | 0.16667 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
F_T++NIL_BLSPS_R60_3 | 0.16667 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 3, FCSPS unavailable | NIL
F_T++NIL_BLSPS_R6_2 | 0.16667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T++NIL_BLSPS_R6_3 | 0.16667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 3, FCSPS unavailable | NIL
F_T++NIL_BLSPS_R6_4 | 0.16667 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 4, FCSPS unavailable | NIL
F_Q++8E_R60 | 0.16667 | 0 | Out = Sapphire to Armidale (8E) line, Qld Raise 60 sec Requirement | Outage
F_T++NIL_BLSPS_R60_4 | 0.16667 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 4, FCSPS unavailable | NIL
F_T++NIL_BLSPS_R60_2 | 0.16667 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T++NIL_BLSPS_R60_1 | 0.16667 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_QNV+MO_TG_R5 | 0.083333 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage
F_V_WKIEWA1_R6 | 0.083333 | 0 | Out= NIL, West Kiewa 1 R6 Requirement <= 0MW | Outage
F_STHN++LDTW_L6 | 0.083333 | 0 | Out = Liddell to Tamworth (84) line, Southern Lower 6 sec Requirement | Outage
F_T_FAJB_R5 | 0.083333 | 0 | Out=Farrell-John Butters 220KV line. R5 <= 0MW | Outage
F_V_WKIEWA1_R60 | 0.083333 | 0 | Out= NIL, West Kiewa 1 R60 Requirement <= 0MW | Outage
F_QNV++HYMO_L5 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_BLSPS_R6_1 | 0.083333 | 0.16667 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_NVS+LDTW_L6 | 0.083333 | 0 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_V_WKIEWA1_L6 | 0.083333 | 0 | Out= NIL, West Kiewa 1 L6 Requirement <= 0MW | Outage
F_MAIN++ML_L60_APD | 0.083333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_MAIN+ML_L5_APD | 0.083333 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_QNV+HGTR_L5 | 0.083333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
F_T++NIL_BLSPS_L60_1 | 0.083333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_QNV+HGTR_L6 | 0.083333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T++NIL_BLSPS_L6_1 | 0.083333 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_MAIN+ML_L60_APD | 0.083333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage

## Binding Impact
Constraint Equation ID | 2021 Marginal Values | 2020 Marginal Values | 2021 Hours | 2020 Hours | Description | Type | Limit Type | Region
N^^N_NIL_2 | 13387430.9783 | 1123394.3221 | 1028.5 | 165.25 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
N>>N-NIL_94T | 11942468.2359 | 0 | 844.0833 | 0 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | NIL | Thermal | NSW
S>NIL_MHNW1_MHNW2 | 8487751.4099 | 596843.5063 | 1722.5833 | 144 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL | Thermal | SA
S_NIL_STRENGTH_1 | 7697221.166 | 11147928.6698 | 649 | 942.1667 | Out= NIL, Upper limit (2500 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements | NIL | System Strength | SA
N^^N_NIL_3 | 6739547.4244 | 394269.3632 | 1245.25 | 104.4167 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL | Voltage Stability | NSW
NRM_QLD1_NSW1 | 5761967.614 | 381008.7281 | 94.5 | 5.9167 | Negative Residue Management constraint for QLD to NSW flow | NIL | Negative Residue | Negative Residue
Q>NIL_EMCM_6056 | 5497767.8756 | 0 | 475.5833 | 0 | Out= NIL, avoid thermal overload on Emerald to Comet (6056) 66 kV Feeder | NIL | Thermal | Qld
T_MRWF_FOS | 3956262.2882 | 6217993.99 | 1251.4167 | 1188 | Limit Musselroe wind farm due to upper limit on Tasmanian generator events. Limit is 153 MW (effective 144 MW at the connection point at Derby) | NIL | Other | Tas
V^^V_MLNK_KGTS | 2955395.9265 | 0 | 221.9167 | 0 | Out= Murraylink, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | Outage | Voltage Stability | Vic
F_Q++LDTW_R6 | 2949473.2448 | 83.4619 | 96.75 | 2.25 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
V_KIAMSF_FLT_50 | 2580762.7758 | 10463.4639 | 211.9167 | 0.83333 | Limit Kiamal solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_KARADSF_FLT_25 | 2503761.7239 | 786643.5279 | 209.25 | 63.4167 | Limit Karadoc solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_NIL_STRGTH_HAUSF | 2457197.1515 | 10412278.5645 | 191.4167 | 858.5833 | Out = Nil, limit Haughton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
F_Q++LDTW_R60 | 2425211.2442 | 152.0987 | 102.5 | 4.25 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
N>>N-NIL_969 | 2412928.344 | 0 | 183.5 | 0 | Out= Nil, avoid O/L Gunnedah to Tamworth (969) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
N>N-NIL_997_99A | 2368768.4717 | 0 | 235 | 0 | Out= Nil, avoid O/L Corowa to Albury 132kV line (997/1) on trip of Finley to Uranquinty 132kV line (99A), Feedback | NIL | Thermal | NSW
S^SETX_GEN_CAP | 2172975.9846 | 361492.7868 | 273.3333 | 79.4167 | Out= One South East 275/132kV transformer O/S, avoid local voltage collapse on trip of remaining South East transformer, | Outage | Thermal | SA
V^^V_NIL_KGTS | 2132627.6704 | 0 | 317 | 0 | Out= Nil, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | NIL | Voltage Stability | Vic
N>>N-NIL_94T_947 | 2119871.8128 | 159354.0133 | 407 | 129.6667 | Out= Nil, avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | NIL | Thermal | NSW
S-X_2DV+2RB_STRGHT_1 | 2084424.5872 | 0 | 200.5833 | 0 | Out = 2 x Davenport + 2 x Robertstown synchronous condensers O/S, Upper limit (1300 to 1750 MW) for SA ASG for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | Outage | System Strength | SA
V_MURRAWRWF_FLT_90 | 2041076.5381 | 1603340.3389 | 164.75 | 130.6667 | Limit Murra Warra Wind Farm upper limit to 90 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
V_YATPSF_FLT_25 | 2014657.9587 | 0 | 217 | 0 | Limit Yatpool solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_Q++LDMU_R6 | 1923279.0924 | 95.5142 | 45.5833 | 1.3333 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
S>NIL_HUWT_STBG2 | 1903054.8793 | 383878.6628 | 217.0833 | 42.25 | Out = Nil; avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=60 MW && when Dalymple Battery (i.e. both Gen and Load component) is I/S].[Note:Swamped when WTTPT<80 && DALR OFF OR DalrB OFF] | NIL | Thermal | SA
V>V_NIL_17 | 1848399.7813 | 2501675.7954 | 283.8333 | 235.5833 | Out = NIL, prevent pre-contingent overload of Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback | NIL | Thermal | Vic
N_BROKENH1_ZERO | 1817725.9293 | 727068.9855 | 136.0833 | 39.5 | Broken Hill Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>N-NIL_PK_TX2 | 1753091.3438 | 0 | 254.75 | 0 | Out= Nil, avoid O/L Parkes TX2 132/66kV transformer on trip of Nil, Feedback | NIL | Thermal | NSW
N_COLEASF1_FLT_45 | 1705895.3362 | 68366.0172 | 136.9167 | 5.4167 | Limit Coleambally solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_T_AUFLS2_R6 | 1649224.7148 | 1588523.7296 | 4264.9167 | 4276.6667 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL | FCAS | FCAS
V^^N_NIL_1 | 1639245.0945 | 255990.578 | 875 | 585.4167 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Voltage Stability | Vic
N_BROKENHSF_FLT_25 | 1579166.9813 | 577026.6811 | 133.4167 | 46.25 | Limit Broken Hill Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_KARADSF_FLT_20 | 1524714.3902 | 1041.9934 | 120.3333 | 0.083333 | Limit Karadoc solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_LIMOSF1_FLT_60 | 1518639.1521 | 0 | 136.1667 | 0 | Limit Limondale 1 solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_YATPSF_FLT_20 | 1449502.8358 | 0 | 115.4167 | 0 | Limit Yatpool solar farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V>>V_NIL_18 | 1410266.0201 | 55657.2206 | 228.1667 | 35.6667 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
V_MURRAWRWF_FLT_0 | 1392988.9773 | 854071.0466 | 112.0833 | 68.75 | Limit Murra Warra Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
SA_ISLE_STRENGTH_BU | 1370091.8439 | 217567.6826 | 115.8333 | 17.6667 | Out= 2x Davenport syn cons + 2 x Robertstown syn cons O/S when SA in Island mode, Maximum limit (130 MW) for Bungala Solar Farm for system strength requirements when SA is at risk of separation or when islanded.(Note:Swamped when all 4/any syncons I/S) | Outage | System Strength | SA
V_BANSF_BBD_60 | 1327289.4762 | 3040110.1981 | 199.9167 | 277 | Out = Nil, Limit Bannerton SF upper limit to 60 MW if Boundary Bend (BBD) loading is less than 10 MW, DS only. Swamp out if BBD loading is 10 MW or above. | NIL | Discretionary | Vic
N_FINLYSF_FLT_45 | 1238829.3461 | 579143.5898 | 100.9167 | 46.3333 | Limit Finley solar farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_I+RREG_0220 | 1234031.1304 | 599388.7364 | 7689.25 | 5015.6667 | NEM Raise Regulation Requirement greater than 200 MW | NIL | FCAS | FCAS
Q_OAKEY1SF_ZERO | 1225430.3325 | 0 | 95.9167 | 0 | Oakey 1 Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_Q++ARTW_L60 | 1216909.3858 | 21087.2181 | 267 | 72.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V_BANNERTSF_FLT_25 | 1196814.8022 | 798611.0205 | 101.6667 | 64.0833 | Limit Bannerton Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_BANNERTSF_FLT_45 | 1196811.2802 | 456214.3986 | 97.9167 | 40.0833 | Limit Bannerton Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q>NIL_BI_xxx | 1194689.835 | 81.1545 | 121.6667 | 0.5 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines | NIL | Thermal | Qld
N_LIMOSF2_FLT_15 | 1177396.721 | 0 | 94.5833 | 0 | Limit Limondale 2 solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_SUNRSF_FLT_60 | 1114808.5528 | 0 | 101.8333 | 0 | Limit Sunraysia solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_ARARATWF_FLT_0 | 1112493.8165 | 39979.3609 | 89.0833 | 15.75 | Limit Ararat Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N>>N-MPWW_ONE_8 | 1105397.0428 | 0 | 53.9167 | 0 | Out= Mt. Piper to Wallerawang(70 or 71), avoid O/L Molong to Orange North (94T) on trip of the remaining Mt Piper to Wallerawang (71 or 70) , Feedback | Outage | Thermal | NSW
N_SUNRSF1_ZERO | 1084503.1338 | 0 | 81.75 | 0 | Sunraysia 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_NUMURKAH_ZERO | 1082993.5352 | 649562.4303 | 88 | 52.0833 | Numurkah Solar Farm upper limit of 0 MW | NIL | Unit Zero | Vic
F_Q++ARTW_L6 | 1078462.8081 | 22397.3135 | 272.5833 | 69.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
NSA_Q_GSTONE34_xxx | 1055282.2777 | 35227.5143 | 18.9167 | 91.75 | Gladstone 3 + 4 >= 450 for Network Support Agreement | Outage | Network Support | Qld
Q_STR_MEWF_ZERO | 1021137.1866 | 0 | 83.5833 | 0 | Limit 0MW to Mt Emerald Wind farm for system strength requirement | Outage | System Strength | Qld
V_CWWF_FLT_0 | 994710.5302 | 219256.2057 | 80.25 | 17.5833 | Limit Crowlands Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_GANWRSF_FLT_30 | 966486.6059 | 91742.4469 | 80.25 | 7.4167 | Limit Gannawarra solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_MACWF_FLT_0 | 939999.678 | 0 | 72.1667 | 0 | Limit Macarthur Wind Farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V_MURRAWRWF_FLT_80 | 938488.0161 | 0 | 76.9167 | 0 | Limit Murra Warra Wind Farm upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
N^^Q_TW_330_BUS3_B1 | 934251.0969 | 0 | 30 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
F_I+LREG_0210 | 908349.202 | 744148.211 | 7901 | 7770.25 | NEM Lower Regulation Requirement greater than 210 MW | NIL | FCAS | FCAS
N>N-NIL_PK_TX1 | 904893.2993 | 0 | 139.25 | 0 | Out= Nil, avoid O/L Parkes TX1 132/66kV transformer on trip of Nil, Feedback | NIL | Thermal | NSW
N_COLEASF1_ZERO | 871283.0566 | 455677.8449 | 66.75 | 8.8333 | Coleambally solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N>>N-NIL_94B_9ML | 867327.3852 | 0 | 88.6667 | 0 | Out= Nil, avoid O/L Bodangora to Wellington (94B/1) on trip of Crudine Ridge to Ilford Tee (9ML) line, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
N_BROKENHSF_FLT_30 | 852430.4192 | 104967.0834 | 69.75 | 8.6667 | Limit Broken Hill Solar Farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q>>CPST_CLWU_RGLC | 844622.0053 | 0 | 101.9167 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
V_CWWF_FLT_55 | 803103.1132 | 0 | 65.1667 | 0 | Limit Crowlands Wind Farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 798340.2205 | 83284.3995 | 411.6667 | 138.75 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | Voltage Stability | NSW
F_T+NIL_WF_TG_R6 | 790984.3783 | 651219.4926 | 1386.6667 | 943.8333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_SILVERTWF_FLT_100 | 787783.7307 | 107240.7091 | 66.75 | 8.75 | Limit Silverton Wind Farm upper limit to 100 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
Q>NIL_COLNVSF1 | 744204.4369 | 2712977.2788 | 60.25 | 307.9167 | Out = Nil, Limit Collinsville Solar Farm to thermal rating of Powerlink's RMU | NIL | Thermal | Qld
V_MLMO_VS_LB_CAN_50 | 737948.6818 | 322408.5362 | 115.4167 | 147.5 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS generating. | Outage | System Strength | SA
F_I+NIL_MG_R6 | 720714.2397 | 444501.4491 | 7559 | 6571.75 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
N>N-NIL_9R4_99A | 707709.8433 | 527353.3867 | 71.75 | 44.0833 | Out= Nil, avoid O/L Finley to Mulwala 132kV line (9R4) on trip of Finley to Uranquinty (99A) line, Feedback | NIL | Thermal | NSW
Q_NIL_STRGTH_MEWF | 683834.4755 | 17924238.2776 | 37.0833 | 1507.9167 | Out = Nil, limit Mt Emerald wind farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
F_Q++LDMU_R60 | 662808.545 | 0 | 43.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
S-SNWWF_0 | 635196.9269 | 36317.2963 | 53.8333 | 8.0833 | Discretionary upper limit for Snowtown WF generation of 0 MW | Outage | Unit Zero | SA
V_WEMENSF_FLT_25 | 618317.0275 | 662686.3523 | 51.3333 | 53.25 | Limit Wemen Solar Farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S_SECB_LG-1 | 617261.4617 | 71254.832 | 39.25 | 5.6667 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | Thermal | SA
N_DARLSF_FLT_80 | 616156.8779 | 344342.1393 | 48.4167 | 27.5833 | Limit Darlington Pt Solar Farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_S+MLMO_TL_L60 | 608641.7269 | 230539.8934 | 69.3333 | 191.8333 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage | FCAS | FCAS
Q>>CPWO1_CPWO2_WUGG | 605446.9507 | 0 | 67.5 | 0 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Woolooga (814) on trip of Wurdong to Teebar Creek (819) line, Feedback | Outage | Thermal | Qld
Q>NIL_YLMR | 571931.6936 | 38419.1447 | 563.25 | 63.5833 | Out= Nil, avoid overload on 110kV feeders between Yarranlea and Middle Ridge(733/1 and 734/1), Feedback | NIL | Thermal | Qld
V>>V_NIL_9 | 569730.4007 | 316117.272 | 75.75 | 147.9167 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL | Thermal | Vic
V>>V_NIL_7 | 568018.3596 | 29810.3113 | 81.5 | 17.9167 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL | Thermal | Vic
Q_STR_HASF_ZERO | 564055.5251 | 0 | 46.1667 | 0 | Limit 0MW to Haughton Solar farm for system strength requirement | Outage | System Strength | Qld
N::N_NIL_63 | 557120.9356 | 0 | 52.25 | 0 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL | Voltage Stability | NSW
N_LIMOSF11_ZERO | 522533.6444 | 3375.9093 | 42.0833 | 0.33333 | Limondale 1 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_STR_32282_HASF | 509630.3352 | 0 | 41.0833 | 0 | Limit 75% to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q_NIL_STRGTH_KIDSF | 509611.1012 | 613792.2817 | 19.4167 | 50.6667 | Out = Nil, limit Kidston solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N_COLEASF1_FLT_30 | 504862.5446 | 234521.5836 | 40.75 | 18.6667 | Limit Coleambally solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V^^SML_NSWRB_2 | 503101.1041 | 106937.2868 | 59.3333 | 50.8333 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL | Voltage Stability | Vic
S>>RBTX_WEWT_RBTX | 496420.9904 | 0 | 66.75 | 0 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage | Thermal | SA
S>DVTX_NIL_DVTX | 490992.8649 | 285999.5094 | 40.6667 | 23.25 | Out= One Davenport 275/132kV TX O/S, avoid O/L of remaining Davenport 132/275kV TX on NIL trip. | NIL | Thermal | SA
F_MAIN++NIL_MG_R6 | 488377.2922 | 494315.1712 | 2389.6667 | 2407.0833 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
N>>N-PKWL_94K_2 | 477675.3362 | 0 | 79.4167 | 0 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Nil, Feedback | Outage | Thermal | NSW
N_LIMOSF2_FLT_25 | 477512.4596 | 657343.4851 | 43.4167 | 52.5 | Limit Limondale 2 solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
T::T_NIL_1 | 474322.7926 | 251799.7281 | 1427.4167 | 315.75 | Out = NIL, prevent transient instability for fault and trip of a Farrell to Sheffield line, Swamp if less than 3 synchronous West Coast units generating or Farrell 220kV bus coupler open or Hampshire 110kV line is closed. | NIL | Transient Stability | Tas
V_BANSF_BBD_80 | 469301.5123 | 312338.3776 | 86.0833 | 38.8333 | Out = Nil, Limit Bannerton SF upper limit to 80 MW if Boundary Bend (BBD) loading is between 10 and 15 MW, DS only. Swamp out if BBD loading is outside the range. | NIL | Discretionary | Vic
F_T+NIL_MG_RECL_R6 | 465507.6487 | 287533.6435 | 1607.5833 | 727.6667 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_SUNRSF_FLT_50 | 462687.4758 | 0 | 37.8333 | 0 | Limit Sunraysia solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_BULGANAWF_FLT_40 | 459006.1728 | 0 | 40.9167 | 0 | Limit Bulgana Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_NIL_STRGTH_RRSF | 455844.3469 | 212261.983 | 16.25 | 17.4167 | Out = Nil, limit Ross River solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
N^^Q_TW_330_BUS1_B1 | 455364.3546 | 0 | 35.9167 | 0 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
F_I+NIL_MG_R60 | 439024.9746 | 281862.7419 | 7075.4167 | 6295.5 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL | FCAS | FCAS
N_FINLYSF_FLT_30 | 433252.713 | 177455.0468 | 34.6667 | 14.4167 | Limit Finley solar farm upper limit to 30 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_NIL_STRGTH_HAMSF | 426832.6412 | 271893.3255 | 16.1667 | 22.3333 | Out = Nil, limit Hamilton solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_COLSF | 424045.9216 | 153290.1235 | 14.8333 | 29.25 | Out = Nil, limit Collinsville solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q>NIL_TV66 | 412897.7854 | 0 | 24.4167 | 0 | Out=Nil, limit Sun metals SF and Mt Stuart GTs to avoid over load on 66kV feeders on trip of one of the 66kV feeders in the Townsville area | NIL | Thermal | Qld
N::N_CNCW_2 | 412008.5023 | 0 | 17.5 | 0 | Out= Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | Transient Stability | NSW
V^^N_MSUT_1 | 406293.7668 | 0 | 183.3333 | 0 | Out = Murray to Upper Tumut (65), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S_SECB_LG3 | 392501.7068 | 41819.2997 | 25.0833 | 4.0833 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | Thermal | SA
Q_NIL_STRGTH_DAYSF | 390925.0697 | 74784.8962 | 12.1667 | 6.0833 | Out = Nil, limit Daydream solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_NIL_STRGTH_WHTSF | 388359.4931 | 231843.4766 | 13.0833 | 21.9167 | Out = Nil, limit Whitsunday solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
V_GANWRSF_FLT_25 | 387688.2672 | 593673.3138 | 31.5833 | 47.5833 | Limit Gannawarra solar farm upper limit to 25 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_T+NIL_ML_L6 | 385971.7815 | 31356.0764 | 2616.3333 | 184.5833 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_MAIN+NIL_DYN_RREG | 384174.2696 | 1089423.7806 | 749 | 3199.5 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL | FCAS | FCAS
Q_NIL_STRGTH_HAYSF | 381182.3707 | 11164.4507 | 14.75 | 0.91667 | Out = Nil, limit Hayman solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
Q_OAKEY2SF_ZERO | 371281.1135 | 0 | 29.4167 | 0 | Oakey 2 Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N_COLEASF1_FLT_60 | 361442.8693 | 0 | 29.1667 | 0 | Limit Coleambally solar farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_NIL_STRGTH_RGBSF | 354628.8449 | 370243.1578 | 9.25 | 49.4167 | Out = Nil, limit Rugby Run SF output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Townsville GT, Kareeya and Barron Gorge generators, Zero if it does not meet minimum generator online. Refer to Table 7 of SO_OG_NEM_62 | NIL | System Strength | Qld
V_CWWF_ISL_0 | 340934.3745 | 458514.3055 | 27.0833 | 37.4167 | Crowlands Wind Farm total upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V>>N-NIL_HA | 338671.9914 | 5729.3207 | 103.3333 | 18.1667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Thermal | Vic
Q_STR_7C8C_HASF | 338379.3162 | 0 | 30.8333 | 0 | Limit Haughton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V>>V_NIL_14 | 335628.5433 | 16301.8954 | 39.75 | 4.25 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
V_KIATAWF_FLT_0 | 333899.523 | 81313.1321 | 115.6667 | 45.3333 | Limit Kiata Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
SV_420_DYN | 327039.929 | 129504.5916 | 330.8333 | 121.9167 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
S>SETX_NIL_SETX | 321265.7892 | 0 | 84.5833 | 0 | Out= One South East 275/132kV transformer O/S, avoid O/L of other South East 132/275kV TX on Nil trip, | NIL | Thermal | SA
N>N-NIL_LSDU | 319145.9158 | 33152.8373 | 270 | 101.9167 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
N_LIMOSF1_FLT_50 | 317589.9724 | 227155.0556 | 26 | 18.0833 | Limit Limondale 1 solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_STWF1_ZERO | 316250.7432 | 848820.5999 | 25.1667 | 65.5833 | Silverton wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_MTMERCER_ZERO | 313648.9415 | 167778.1325 | 25.8333 | 13.25 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Unit Zero | Vic
N_TARALGAWF_ZERO | 312585.6938 | 149161.839 | 23.9167 | 11.9167 | Taralga WF upper limit of 0 MW | Outage | Unit Zero | NSW
Q_STR_7C8C_KIDSF | 311935.4182 | 0 | 26.0833 | 0 | Limit Kidston SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_BANNERTSF_FLT_20 | 305763.2791 | 0 | 24.4167 | 0 | Limit Bannerton Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
S>SE6161_SETX2_SGBL | 293813.622 | 0 | 71.5833 | 0 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | Thermal | SA
N^^Q_NIL_A | 292635.0741 | 4656.9044 | 39.25 | 8.8333 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | Voltage Stability | NSW
V_ARARATWF_FLT_160 | 280701.218 | 0 | 23.25 | 0 | Limit Ararat Wind Farm upper limit to 160 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_T+NIL_MG_R6 | 280157.6468 | 384090.3434 | 444.6667 | 787.75 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_FINLYSF_FLT_55 | 279973.1565 | 0 | 22.5 | 0 | Limit Finley solar farm upper limit to 55 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_311393_MEWF | 278565.79 | 140627.0545 | 22.0833 | 12.1667 | Limit Mt Emerald SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
V_MURRAWRWF_FLT_60 | 266544.6729 | 0 | 21.1667 | 0 | Limit Murra Warra Wind Farm upper limit to 60 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
F_Q++ARTW_R6 | 265089.6367 | 0 | 25.3333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
V_WEMENSF_FLT_45 | 261726.2431 | 325751.4221 | 26.8333 | 28.5 | Limit Wemen Solar Farm upper limit to 45 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
NSA_Q_BARCALDN | 254881.7366 | 163305.5047 | 20.3333 | 13.4167 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Network Support | Qld
Q_LILYSF1_ZERO | 243944.658 | 537460.9367 | 20.5 | 44 | Lilyvale Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q>CMTX | 239845.0556 | 318973.5115 | 19.5 | 26.75 | Out = Clermont T1 or T2 132/66 kV transformer, limit to Clermont Solar Farm to 30MW to prevent overload on remaining transformer | Outage | Thermal | Qld
Q>>BCST_BCST_CLWU | 238801.3915 | 0 | 89.3333 | 0 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line, avoid O/L the remaining Stanwell to Bouldercombe 848 or 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
F_Q++LDMU_R5 | 237818.8995 | 0 | 20.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
N_LIMOSF1_FLT_85 | 237710.0172 | 0 | 19.0833 | 0 | Limit Limondale 1 solar farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
N_DARLSF_FLT_110 | 235711.7968 | 0 | 18.9167 | 0 | Limit Darlington Pt Solar Farm upper limit to 110 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_MAIN++NIL_MG_R60 | 234736.8562 | 287325.6767 | 2393.8333 | 2523.25 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
V^^V_NIL_KGTS_2 | 234295.2394 | 0 | 32.5 | 0 | Out= Nil, Limit post-contingency flow on Wemen to Kerang 220kV line to be less than 310 MVA for loss of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF) to avoid voltage collapse | NIL | Voltage Stability | Vic
N_DARLSF_FLT_85 | 231716.3793 | 0 | 17.8333 | 0 | Limit Darlington Pt Solar Farm upper limit to 85 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_KIATAWF_FLT_15 | 230847.9186 | 14138.9855 | 74.9167 | 7.4167 | Limit Kiata Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
N>>N-PKWL_94K_1 | 225616.2755 | 7521.6193 | 31.25 | 11 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Forbes to Cowra (998) line, Feedback | Outage | Thermal | NSW
Q>>WOPW_WOSP_WOGP_2 | 217564.9101 | 0 | 28.5 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Thermal | Qld
N_SUNRSF_FLT_80 | 213334.7926 | 0 | 17.1667 | 0 | Limit Sunraysia solar farm upper limit to 80 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
SVML^NIL_MH-CAP_ON | 213298.4733 | 0 | 283.25 | 0 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL | Voltage Stability | SA
F_Q++MUTW_L6 | 208139.3936 | 214541.5296 | 288.0833 | 1164.3333 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V_GANWRSF_FLT_15 | 207925.5424 | 0 | 16.6667 | 0 | Limit Gannawarra solar farm upper limit to 15 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN++RREG_0220 | 207875.3072 | 10002.1351 | 964.1667 | 151.1667 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
T_T_FASH_10_N-2 | 206727.3272 | 297498.2673 | 5.5833 | 10.75 | Out = NIL, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain John Butters and Bastyan to 0 MW as per TAS Networks advice | Outage | Discretionary | Tas
Q_STR_7C8C_HAMSF | 206553.1839 | 0 | 17.4167 | 0 | Limit Hamilton SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
T_CTHLWF_ZERO | 205093.877 | 0 | 16.6667 | 0 | Wild Cattle Hill Wind Farm upper limit of 0 MW | Outage | Unit Zero | Tas
N>>N-NIL_9ML | 197668.7787 | 0 | 26.75 | 0 | Out= Nil, avoid O/L Crudine Ridge to Ilford Tee (9ML) on trip of Nil, Feedback. Metering is used as specified in OM520 | NIL | Thermal | NSW
S_TIPSB_270 | 197234.3217 | 0 | 2.1667 | 0 | Out = NIL, Loss of Torrens Island A Power Station declared credible as a single credible contingency, discretionary upper limit for TIPSB1+TIPSB2+TIPSB3+TIPSB4 <= 270 MW | Outage | Discretionary | SA
V^^N_DPWG_X5_1 | 189341.2673 | 0 | 73.3333 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_KSP1_ZERO | 183661.2895 | 0 | 16.25 | 0 | Kidston solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_STR_7C8C_HAYSF | 180502.0552 | 0 | 15.6667 | 0 | Limit Hayman SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_S_ROCOF | 179632.2605 | 0 | 2.8333 | 0 | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage | ROC Frequency | Vic
V_ARARATWF_ISL_0 | 179569.4273 | 68416.0808 | 14.1667 | 30.3333 | Limit Ararat Wind Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
Q_STR_7C8C_COLSF | 175361.4387 | 0 | 14.4167 | 0 | Limit Collinsville SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
SA_ISLE_STRENGTH | 171445.9715 | 111118.7289 | 13.4167 | 8.9167 | Maximum limit (1900 MW) for SA non-synchronous generation for system strength requirements when SA is at risk of separation or when islanded. | Outage | System Strength | SA
S>NIL_HUWT_STBG3 | 168272.3386 | 0 | 16 | 0 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Constraint Swamped when Wattle PT when generating >=60 MW) | NIL | Thermal | SA
V>>V_DDSM_1 | 168226.0013 | 0 | 91.4167 | 0 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Thermal | Vic
V_KIATA_ISL_0 | 167819.8772 | 127954.3821 | 29.5 | 82.9167 | Kiata Wind Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
V^^N_LTYS_1 | 165918.9717 | 0 | 98 | 0 | Out = Lower Tumut - Yass (3) 330kV line , avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N>N-NIL_CO_TX | 163465.6443 | 0 | 14.8333 | 0 | Out= Nil, avoid O/L either Corowa 22kV/132kV Transformer on NIL trip, Feedback. NOTE: System normal is only one transformer in service. 90% of Rating and no operating margin is used as per Essential Energy advice. | NIL | Thermal | NSW
Q_STR_7C8C_DAYSF | 161889.5294 | 0 | 13.3333 | 0 | Limit Daydream SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N_SILVERTWF_FLT_80 | 160472.9144 | 0 | 12.6667 | 0 | Limit Silverton Wind Farm upper limit to 80 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
F_Q++ARTW_L5 | 158747.6903 | 4856.9003 | 122.75 | 20.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
Q_STR_7C8C_RRSF | 153767.5436 | 0 | 26.6667 | 0 | Limit Ross River SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_311393_HASF | 147328.0397 | 432687.7303 | 11.9167 | 33.8333 | Limit Haughton SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
S-MWPS4-PV_0 | 146701.5028 | 0 | 14.0833 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW | Outage | Unit Zero | SA
F_S++HYSE_L60 | 143882.4195 | 16153.8532 | 122.9167 | 28.9167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage | FCAS | FCAS
V_S_NIL_ROCOF | 142367.5442 | 2160.6409 | 326.75 | 11.25 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | Vic
S:V_PA_SVC_420 | 141724.0026 | 301726.6067 | 180.5 | 362.4167 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
Q_STR_7C8C_RUGSF | 141215.6314 | 0 | 12.75 | 0 | Limit Rugby Run SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V^^N_CNCW_1 | 139050.1003 | 0 | 93 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_T+NIL_ML_L60 | 138745.3081 | 7925.1109 | 2558.1667 | 184.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
Q_NIL_STRGTH_CLRSF | 137800.5269 | 422268.6823 | 9.9167 | 34.75 | Out = Nil, limit Clare solar farm output depends on the number units online in Stanwell, Callide B, Callide C, Gladstone, Kareeya generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
V_BULGANAWF_FLT_60 | 136188.0195 | 0 | 11.0833 | 0 | Limit Bulgana Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
F_MAIN+NIL_DYN_LREG | 133127.8034 | 65383.6088 | 543.6667 | 313.8333 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL | FCAS | FCAS
N_FINLYSF_FLT_50 | 132751.4183 | 30247.7761 | 10.6667 | 2.4167 | Limit Finley solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_MAIN++NIL_BL_L60 | 132302.6486 | 1385.5073 | 1172.0833 | 181.9167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
F_TASCAP_LREG_0210 | 131289.5614 | 20119.1861 | 1482.6667 | 321.5 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
Q>NIL_SRMB_M020/1 | 130999.4408 | 204342.0903 | 10.5833 | 17.3333 | Out = Nil, Susan River constrained to the emergency rating of M020/1 Susan River to Maryborough 66kV line, swamp if Susan River runback scheme is armed, Dispatch RHS only. | NIL | Thermal | Qld
Q>NIL_EMBW_EMLV_DS | 128977.9057 | 443958.4026 | 11.5833 | 36.0833 | Out= Nil, limit Emerald SF to 40MW to avoid overload on Emerald - Lilyvale 66kV line on trip of Emerald - Comet - Blackwater 66kV line (6056 or 6011), swamp if Emerald CBs S612,S610 and Blackwater CB S605 are closed (DS only) | NIL | Thermal | Qld
F_Q++ARTW_R60 | 126477.0806 | 29.3966 | 28.25 | 0.83333 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_8C10C_HASF75 | 126441.9223 | 0 | 10.25 | 0 | Limit Haughton SF to 75% if Stan>=3+CalB+C>=2+Glad>=2+ (Stan+Cal+Glad) >=8+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG) 25% if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG). Zero otherwise | Outage | System Strength | Qld
VSML_ROC_80 | 126190.4882 | 54043.0925 | 84.1667 | 77.6667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | Vic
S>>PARB_RBTU_WEWT | 125974.1424 | 0 | 56.25 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T>T_NIL_110_1 | 124562.0889 | 393637.9652 | 41.8333 | 32.5833 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Thermal | Tas
V_STOCKYH_ZERO | 123694.7207 | 0 | 105.6667 | 0 | Stockyard Hill wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
S_NBH_0 | 123213.0345 | 0 | 9.75 | 0 | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | Unit Zero | SA
V_WEMENSF_FLT_20 | 120017.5783 | 0 | 9.5833 | 0 | Limit Wemen Solar Farm upper limit to 20 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
SVML_ROC_80 | 119792.831 | 75917.6914 | 101.25 | 71.9167 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | Ramping | SA
V:S_600_HY_TEST_DYN | 117434.9887 | 3972.7477 | 40.3333 | 23.25 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Oscillatory Stability | Vic
F_T+NIL_WF_TG_R60 | 116502.9461 | 79765.1627 | 1420.6667 | 891.5833 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T+NIL_MG_RECL_R60 | 116228.0696 | 85186.7881 | 1585.0833 | 854.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_T+RREG_0050 | 115671.0325 | 97839.1294 | 251.5833 | 208.75 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
T_T_TI_GH_RC12_250 | 114317.9809 | 17032.4349 | 29.3333 | 4.1667 | Discretionary 250 MW upper limit on Tribute, Granville Harbour, Reece 1 and 2 generation | Outage | Discretionary | Tas
V_MURRAWRWF_FLT_15 | 112938.5297 | 272491.7435 | 8.9167 | 21.6667 | Limit Murra Warra Wind Farm upper limit to 15 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_STR_32282_MEWF | 111638.7444 | 0 | 7.6667 | 0 | Limit 75% to Mt Emerald WF during day or no limit during night if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),. Zero otherwise. . | Outage | System Strength | Qld
S>>X_RBPA+CB_03 | 109311.3399 | 0 | 14.8333 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | Thermal | SA
V_GANWRSF_ISL_0 | 109211.7462 | 1084.5776 | 8.4167 | 0.083333 | Gannawarra Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_Q++MUTW_L60 | 108693.325 | 343223.5276 | 278 | 1115.5833 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
V_VS_LB_CAN_50 | 108519.5843 | 1097.7712 | 128.0833 | 4.75 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage | System Strength | SA
S-BUPV2_0 | 107637.8908 | 44868.7715 | 8.6667 | 2.9167 | Discretionary upper limit for Bungala Stage 2 PV generation of 0 MW | Outage | Unit Zero | SA
NRM_NSW1_VIC1 | 107581.3591 | 381247.2023 | 23.75 | 22.0833 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue | Negative Residue
N>>Q-LDTW_2 | 106589.219 | 2.892 | 1.1667 | 0.083333 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage | Thermal | NSW
S-BUPV1_0 | 105166.9595 | 44868.7712 | 8.5 | 2.9167 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | Unit Zero | SA
S-MWPS3-PV_0 | 104198.1971 | 0 | 9.9167 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW | Outage | Unit Zero | SA
V>SMLMHNW1 | 102764.0302 | 14.6464 | 15.9167 | 1.9167 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
Q>>CPST_CLWU_BCST | 101212.3243 | 0 | 33.8333 | 0 | Out = 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Stanwell to Bouldercombe 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
Q_STR_7C9C_MEWF | 100679.6659 | 0 | 8.1667 | 0 | Mt Emerald WF to 100% of Max capacity if Stan>=3+CalB+C>=2+Glad>=3+ (Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG).80% if Stan>=3+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>2 or if Stan>=3+Glad>=2+(Stan+Cal+Glad)>=6+Kar>2 .Zero otherwise | Outage | System Strength | Qld
F_TASCAP_RREG_0220 | 100587.2358 | 18104.6907 | 954.75 | 249.5833 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS | FCAS
S>NIL_BWMP_HUWT | 98565.5915 | 141851.1296 | 8 | 10.6667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | Thermal | SA
F_T_NIL_MINP_R6 | 97413.2195 | 304090.6277 | 833.25 | 1530.0833 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL | FCAS | FCAS
N_LIMOSF21_ZERO | 97159.2663 | 0 | 7.5 | 0 | Limondale 2 solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_BANNERTON_ZERO | 96153.1654 | 2089.5138 | 8 | 0.16667 | Bannerton Solar Farm upper limit of 0 MW | Outage | Unit Zero | Vic
Q_CPSA_44 | 95732.1264 | 0 | 7.1667 | 0 | Discretionary, Condamine PS =< 44MW | Outage | Discretionary | Qld
V_T_NIL_FCSPS | 88382.5482 | 180901.095 | 238.0833 | 345.5 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Other | Vic
Q_STR_7C2K_KIDSF_3 | 87960.4115 | 0 | 6.9167 | 0 | Limit 80% to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
N_MBTE1_B | 87146.7771 | 205699.9648 | 175.75 | 119.5 | Out= one Directlink cable, Qld to NSW limit | Outage | Unit Zero | NSW
N>>N-NIL__3_OPENED | 86895.0004 | 50.9096 | 0.5 | 0.33333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | Thermal | NSW
N_DARLSF_FLT_100 | 86732.719 | 0 | 7.0833 | 0 | Limit Darlington Pt Solar Farm upper limit to 100 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_7C8C_WHTSF | 86626.6142 | 0 | 8 | 0 | Limit Whitsunday SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V>V_NIL_8 | 86530.8674 | 95189.681 | 21.9167 | 66.4167 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kiamal to Red Cliffs 220kV line, Feedback. Constraint active only when GFT2 on Murra Warra WF I/S. | NIL | Thermal | Vic
S>>PARB_RBTU_WTTP | 84978.3439 | 0 | 31.5 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
S>X_RBPA+CB_01 | 84783.7795 | 0 | 13.0833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), | Outage | Thermal | SA
F_I+NIL_APD_TL_L60 | 83950.2271 | 46915.127 | 6785.75 | 6570.9167 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
Q_STR_8C7C1S_RGBSF | 83708.6552 | 0 | 6.8333 | 0 | No limit Rugby Run SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_COLSF | 83708.0253 | 0 | 6.8333 | 0 | No limit Collinsville SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_RRSF | 83707.9472 | 0 | 6.8333 | 0 | No limit Ross River SF if Stan>=2+Cal>=2+Glad>=2+(Stan+Cal+Glad)>=8+Kar>=2,NQLD>350&370(AVG),Ross_FN>250&,470(AVG),(NQLD>450&470(AVG),Ross_FN>250&270(AVG),Stan>=3+Kar=0),50% if Stan>=2+Kar=0) ,80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. 0 otherwise | Outage | System Strength | Qld
Q_STR_8C7C1S_DAYSF | 83707.9465 | 0 | 6.8333 | 0 | No limit Daydream SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
N_X_MBTE_3A & N_X_MBTE_3B | 83314.6976 | 67542.3813 | 319.9167 | 796.0833 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | Unit Zero | NSW
Q_STR_7C2K_HAMSF_3 | 82932.3957 | 0 | 6.5 | 0 | Limit 80% to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_WHTSF_3 | 82900.6858 | 0 | 6.5833 | 0 | Limit 80% to Whitsunday Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
Q_STR_9C10C_CMSF | 82648.2418 | 0 | 6.5833 | 0 | Limit Clermont SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10 +Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG) or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG) . Zero otherwise | Outage | System Strength | Qld
N^^V_NIL_1 | 82621.9489 | 122981.9435 | 114.8333 | 535.5 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL | Voltage Stability | NSW
S_HALWF_0 | 82442.991 | 0 | 6.8333 | 0 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW | Outage | Unit Zero | SA
Q_9C3_10C21_HASF | 82128.5536 | 352199.4057 | 6.5 | 29.4167 | Limit Haughton70% Max capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
Q_MB_66_CB_E352 | 81115.2984 | 0 | 6.0833 | 0 | Out = Maryborough(T59) 66kV CB E352, limit Susan River to 33.20MW to prevent instability | Outage | System Strength | Qld
Q_STR_7C2K_HAYSF_3 | 80874.7978 | 0 | 6.4167 | 0 | Limit 80% to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
V_OWF_TGTSNRBHTN_30 | 80172.2907 | 131563.512 | 9.75 | 10.6667 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Discretionary | Vic
N_FINLYSF1_ZERO | 79947.9143 | 247664.3383 | 4.1667 | 3.75 | Finley solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
N^^Q_AR_VC_B1 | 77347.2884 | 0 | 45.8333 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
Q_STR_9C10C_RGBSF | 77276.0061 | 0 | 6.1667 | 0 | Limit Rugby Run SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG)or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
SVML_ZERO | 77164.7913 | 241588.716 | 131 | 407.9167 | SA to Vic on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | SA
V_DUNDWF2_ZERO | 77145.7316 | 388169.6738 | 6.4167 | 31.8333 | Dundonnell wind farm 2 upper limit of 0 MW | Outage | Unit Zero | Vic
V^^N_SDUT_1 | 76980.1139 | 0 | 28.75 | 0 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_7C8C_CLRSF | 76686.9059 | 0 | 15.25 | 0 | Limit Clare SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_DUNDWF1_ZERO | 76142.2076 | 416720.5833 | 6.3333 | 34.3333 | Dundonnell wind farm 1 upper limit of 0 MW | Outage | Unit Zero | Vic
Q_STR_8C7C1S_HAYSF | 75480.3768 | 0 | 6.75 | 0 | No limit Hayman SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_HAMSF | 75380.431 | 0 | 6.75 | 0 | No limit Hamilton SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
S>>NIL_BWMP_TWPA | 74209.9977 | 2858.0007 | 7.75 | 1.1667 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
Q_STR_7C2K_DAYSF_3 | 73369.4903 | 0 | 5.75 | 0 | Limit 80% to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_HASF_3 | 73358.7373 | 0 | 5.75 | 0 | Limit 80% to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C7C1S_KIDSF | 73056.8599 | 0 | 6.75 | 0 | No limit Kidston SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
N::N_LTYS_2 | 73041.5791 | 0 | 41 | 0 | Out = Lower Tumut -Yass(3), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
N_SILVERTWF_FLT_50 | 72320.5425 | 0 | 5.6667 | 0 | Limit Silverton Wind Farm upper limit to 50 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | NSW
Q_STR_7C2K_KIDSF_2 | 71714.3614 | 0 | 5.9167 | 0 | Limit 80% to Kidston Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C2K_COLSF_3 | 71346.9014 | 0 | 5.5833 | 0 | Limit 80% to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
F_T+LREG_0050 | 71334.4247 | 106371.2263 | 258.9167 | 210 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V>V_RCTS_TX1B_1 | 70871.4921 | 0 | 12.5 | 0 | Out= Red Cliffs 1B 220/66kV transformer, avoid O/L Red Cliffs 2B 66/220kV transformer on trip of Red Cliffs 3A transformer, Feedback | Outage | Thermal | Vic
V^^S_MLSY_2 | 70805.9368 | 12.3774 | 11.4167 | 0.33333 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Voltage Stability | Vic
S::V_TBSE_TBSE_2 | 69225.0629 | 0 | 11.4167 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
N::N_SDUT_2 | 69169.4866 | 30306.3614 | 42.75 | 0.5 | Out = Upper Tumut -Stockdill(1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
F_T++RREG_0050 | 68902.8145 | 163153.0447 | 473.3333 | 1051.0833 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
V>>V_NIL_24 | 68813.7038 | 0 | 6.25 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
Q_STR_9C10C_EMSF | 67503.0372 | 0 | 5.4167 | 0 | Limit Emerald SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG) or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
N^^V_CNCW_1 | 66961.8583 | 16562.6901 | 113.5833 | 19.25 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
Q_9C3_10C21_MEWF | 66874.253 | 417301.2772 | 5.3333 | 34 | Limit Mt_Emerald 70% capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
V::S_SETB_MAXG_2 | 66625.9408 | 0 | 7.9167 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with both Black Range series capacitors O/S). | Outage | Transient Stability | SA
VSML_ZERO | 66397.2129 | 5224.9884 | 19.6667 | 23.8333 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Interconnector Zero | Vic
Q_STR_8C7C1S_CLRSF | 66325.398 | 0 | 5.4167 | 0 | No limit Clare SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
V::S_NIL_MAXG_xxx | 66097.5122 | 121.9668 | 18.3333 | 2.0833 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | Transient Stability | SA
T_GRANVH_ZERO | 65383.0736 | 116937.8323 | 5.3333 | 11.1667 | Granville Harbour wind farm upper limit of 0 MW | Outage | Unit Zero | Tas
S-TBSF1_0 | 64458.1768 | 44868.7435 | 5.5 | 2.9167 | Discretionary upper limit for Tailem Bend (Coorong) Solar PV of 0 MW | Outage | Unit Zero | SA
S>BRDV_BWPA_RHBR | 63412.2883 | 115582.0142 | 5.8333 | 9.6667 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
Q>>CPST_BCRG_CLWU | 61446.3222 | 0 | 6.0833 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
N^^Q_LDTW_1_B1 | 60885.5613 | 0 | 11.5833 | 0 | Out = Liddell to Tamworth (84), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
N^^V_DDSM1 | 60555.7224 | 63452.0056 | 72.5833 | 74 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | Voltage Stability | NSW
V:S_600_HY_TEST | 60228.3116 | 1937.1832 | 49.0833 | 17.8333 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
Q>>NIL_BCCP_RGLC | 60216.6863 | 95029.0468 | 21.25 | 23.5 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL | Thermal | Qld
Q_DAYDSF1_ZERO | 59677.8538 | 26202.2941 | 4.8333 | 2.5833 | Daydream solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_MAIN++LREG_0210 | 59384.6477 | 39614.393 | 681.5 | 647.5 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
N_WRWSF_055 | 59326.3046 | 11754.1035 | 43.3333 | 16.6667 | White Rock wind farm and White Rock solar farm upper limit of 55 MW | Outage | Other | NSW
V::N_DDSM_xxx | 58992.3862 | 2284.3298 | 131.4167 | 11.0833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_OWF_NRB_0 | 58451.7233 | 35715.7971 | 4.9167 | 2.8333 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Discretionary | Vic
Q^^NIL_QNI_SRAR | 58348.4641 | 271555.5405 | 134 | 397.3333 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL | Voltage Stability | Qld
S>>NIL_TWPA_TPRS | 58123.4744 | 1936.0536 | 7.8333 | 0.58333 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL | Thermal | SA
F_MAIN+NIL_MG_R6 | 57056.712 | 62312.1137 | 258.4167 | 207.5 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
Q_EMERASF1_ZERO | 56855.6064 | 2163.5702 | 4.4167 | 0.16667 | Emerald Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_I+NIL_MG_R5 | 56365.183 | 81104.8282 | 6578.3333 | 7270.4167 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL | FCAS | FCAS
T_MRWF_QLIM_xx | 55685.5424 | 55606.9362 | 17 | 14.8333 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Transient Stability | Tas
T>T_NIL_BL_110_4 | 55426.4294 | 3608.1804 | 68.9167 | 3.3333 | Out = Nil, avoid O/L New Norfolk to Creek Road 110 kV line (flow to South) on trip of New Norfolk to Chapel St 110 kV line, feedback | NIL | Thermal | Tas
Q_STR_7C2K_RUGSF_3 | 54975.5767 | 0 | 4.3333 | 0 | Limit 80% to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
V^^N_CNUT_1 | 54743.773 | 682.7097 | 61.3333 | 1 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S>NIL_NIL_SETX12 | 54230.4708 | 0 | 14.5 | 0 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | Thermal | SA
S^DVBR_SA_NTH | 54020.1214 | 29260.6418 | 5.8333 | 2.3333 | Out = Davenport-Brinkworth 275kV line, Manage voltage collapse in northern SA for the trip of Davenport-Belalie 275kV line(NOTE: ARCHIVE POST COMMISSIONING OF DAVENPORT SYN CONS) | Outage | Voltage Stability | SA
VSML_030 | 53594.5497 | 0 | 2.9167 | 0 | Vic to SA on ML upper transfer limit of 30 MW | Outage | Discretionary | Vic
Q_STR_8C7C1S_MEWF | 52104.3889 | 0 | 4.25 | 0 | No limit Mt Emerald WF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
N>Q-NIL_757_758 | 52062.6586 | 0 | 115.25 | 0 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL | Thermal | NSW
F_MAIN+RREG_0220 | 51795.8175 | 15797.6844 | 242.75 | 111.25 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S:V_XPAVC_310 | 50540.2322 | 79847.3845 | 57.6667 | 26.9167 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
F_T+NIL_MG_R60 | 50352.4631 | 72842.1198 | 522.0833 | 847.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_MAIN+LREG_0210 | 49428.7344 | 22939.5099 | 234.4167 | 195.6667 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_BULGANAWF_FLT_0 | 49357.9125 | 680909.0585 | 3.75 | 53.1667 | Limit Bulgana Wind Farm upper limit to 0 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
Q_STR_8C7C1S_HASF | 49111.5472 | 0 | 4 | 0 | No limit Haughton SF if Stan>=2+Cal>=2+Glad>=2+(Stan+Cal+Glad)>=8+Kar>=2,NQLD>350&370(AVG),Ross_FN>250&,470(AVG),(NQLD>450&470(AVG),Ross_FN>250&270(AVG),Stan>=3+Kar=0),50% if Stan>=2+Kar=0),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. 0 otherwise. | Outage | System Strength | Qld
VS_050_DYN | 48983.5235 | 0 | 12.25 | 0 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
V>>N-NIL_HG | 48318.6877 | 201.1892 | 5.75 | 0.083333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Thermal | Vic
N^N-89_LSTX_SVC | 47955.6799 | 0 | 52.5833 | 0 | Out= Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage | Voltage Stability | NSW
N_DARLSF_FLT_60 | 46612.9682 | 0 | 3.6667 | 0 | Limit Darlington Pt Solar Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
Q_STR_30272_HASF | 46320.5755 | 0 | 3.75 | 0 | Haughton SF to100% if Stan>=3+Glad>=2+ (Stan+Cal+Glad)>=7+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG),80% if Stan>=3+Glad>=2+(Stan+Cal+Glad)>=6+Kar>2 .0 otherwise | Outage | System Strength | Qld
S:V_PA_SVC_270 | 45901.9785 | 503.2412 | 45.5 | 1.5833 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage | Oscillatory Stability | SA
N>>N-NIL_998 | 45829.4562 | 0 | 2.5833 | 0 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL | Thermal | NSW
F_Q++LDTW_R5 | 45443.8055 | 0 | 31.6667 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
V_BULGANAWF_FLT_50 | 45397.1176 | 0 | 3.5833 | 0 | Limit Bulgana Wind Farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_COLEASF1_FLT_40 | 45349.0479 | 0 | 3.5833 | 0 | Limit Coleambally solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V>>V_NIL_4C | 45000 | 0 | 0.25 | 0 | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL | Thermal | Vic
V_MACARTHUR_ZERO | 44812.6277 | 766127.9249 | 3.5833 | 78.9167 | Macarthur upper limit of 0 MW | Outage | Unit Zero | Vic
S>>RBTX2_RBTX1_WEWT | 44667.3147 | 24423.3362 | 6.5833 | 4.9167 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage | Thermal | SA
Q_STR_7C0K9C_HASF | 44034.2028 | 0 | 3.8333 | 0 | No limit to Haughton Solar Farm if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=9+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG) or 50% if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7,Zero otherwise. | Outage | System Strength | Qld
Q_STR_8C_7C2K_RGBSF | 42983.2873 | 0 | 3.3333 | 0 | No limit to Rugby Run SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_CMSF | 42983.2818 | 0 | 3.3333 | 0 | No limit to Clermont SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
Q_STR_8C_7C2K_EMSF | 42983.2741 | 0 | 3.3333 | 0 | No limit to Emerald SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG), limit 50% if Stan>=2+Cal>=1+Glad>=3+ (Stan+Cal+Glad) >=7 + Kar>=2. Zero otherwise | Outage | System Strength | Qld
S>>X_PARB+RB_SBUS_10 | 42894.0117 | 0 | 4.3333 | 0 | Out= Robertstown South 275kV Bus(275kV CBs ONLY O/S with associated 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Para 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V>>N-JNWO_RADIAL_2 | 42659.7869 | 0 | 5 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Thermal | Vic
Q_STR_7C2K_RUGSF_2 | 42082.284 | 0 | 3.3333 | 0 | Limit 80% to Rugby Run Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
S_BRBG_CMWF_0 | 41830.0724 | 2091.2698 | 3.3333 | 0.16667 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | Unit Zero | SA
V^^N_HWSM_1 | 41499.5944 | 74584.8587 | 63.3333 | 155.1667 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q_STR_8C7C1S_WHTSF | 40869.2078 | 0 | 6.25 | 0 | No limit Whitsunday SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),Ross_FN>250&270(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
S>>PATW_BWPA_TPRS | 40830.4686 | 0 | 5.4167 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
TVBL_ROC | 40516.2664 | 21609.9672 | 22.8333 | 16.1667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Tas
V>X_NWCB6225+6021_T1 | 40468.797 | 0 | 11.5833 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1132kV line.(Note: swamped when ML Sever scheme is I/S) | Outage | Thermal | SA
V::N_SMF2_xxx | 39971.9374 | 320.1228 | 93 | 4.0833 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q>>NIL_CLWU_RGLC | 39810.0475 | 96119.0275 | 3.4167 | 23.6667 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL | Thermal | Qld
V::N_HWSM_xxx | 39493.9826 | 27739.8146 | 94.5833 | 125 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_MAIN++APD_TL_L60 | 39272.5744 | 70164.9076 | 1401.0833 | 2754.1667 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
V_GANWR_SF_BAT_50 | 38920.0484 | 9286.8834 | 11.75 | 6.1667 | Out = Nil, limit total output of Gannawarra Solar Farm and Battery (Gen component) to 50 MW to prevent overload on Gannawarra txfmr | NIL | Discretionary | Vic
F_MAIN++APD_TL_L5 | 38454.9576 | 34682.9157 | 2029.5 | 2276.5833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
N_FINLYSF_FLT_40 | 38226.4107 | 0 | 3 | 0 | Limit Finley solar farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
VSML_080 | 38083.7346 | 8425.531 | 5.6667 | 3.6667 | Vic to SA on ML upper transfer limit of 80 MW | Outage | Discretionary | Vic
N^^Q_ARTW_B1 | 38056.051 | 4242.5741 | 37.8333 | 17.3333 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | Voltage Stability | NSW
VS_250_DYN | 37928.4376 | 17853.6237 | 8.5 | 13.0833 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | Vic
Q_STR_7C2K_COLSF_2 | 37765.2229 | 0 | 3 | 0 | Limit 80% to Collinsville Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
F_T++LREG_0050 | 37550.2011 | 14990.5497 | 432.4167 | 261.5 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS | FCAS
Q_RGBYRSF1_ZERO | 37461.469 | 1037.5837 | 2.75 | 0.083333 | Rugby Run Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
F_Q++LDTW_L6 | 37013.2495 | 24166.0029 | 202.9167 | 108.25 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
N>>Q_LDMU_B | 36869.1294 | 0 | 0.5 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage | Thermal | NSW
CA_BRIS_50B292E2_1 | 36812.0811 | 0 | 1.5833 | 0 | Constraint Automation, O/L 64:LSM2:I:330@TUMUT3@NSW for CTG LXPD on trip of LOWER TUMUT-CANBERRA 07 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N^^Q_MUTW_1_B1 | 36627.7903 | 2637.3234 | 37.75 | 3.75 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
Q_STR_7C8C_MEWF | 36431.7744 | 0 | 2.9167 | 0 | Limit Mt Emerald WF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kar>=3 (or Bar>=1+Kar>=2) (,NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>=2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_MAIN+NIL_MG_R60 | 36309.7318 | 23004.9927 | 247.75 | 202.5 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
S_DVRB2_270 | 36089.0314 | 23610.6569 | 8.0833 | 5.4167 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | Discretionary | SA
S>>CGTB1_TBTU_TBMO | 35910.0207 | 100.6205 | 22.75 | 1.5 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_Q++LDTW_L60 | 35021.9374 | 14140.7366 | 182.3333 | 104.6667 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_9C10C_LYSF | 34155.4703 | 0 | 2.75 | 0 | Limit Lilyvale SF to 50% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+ (Stan+Cal+Glad) >=10+Strathmore SVC OS,NQLD>650&670(AVG),Ross_FN>350&370(AVG)or Glad>2+(Stan+Cal+Glad) >=9+Kar>2,NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise | Outage | System Strength | Qld
S>X_RBPA+CB_06 | 33998.4605 | 0 | 8.5833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage | Thermal | SA
F_MAIN++NIL_MG_R5 | 33925.0508 | 13607.1409 | 1525.0833 | 1207.75 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS | FCAS
N^N_CHLS_1 | 33857.5845 | 627.6775 | 134 | 15.6667 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
V^^N_MNYS_1 | 33512.101 | 6940.7366 | 14.0833 | 20.6667 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_Q++BCDM_L60 | 32699.3051 | 5972.6219 | 126.5 | 43.75 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
S>>NIL_RBTU_WEWT | 32570.2379 | 356.5552 | 5.8333 | 0.16667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
S_HALWF2_0 | 32475.3154 | 0 | 2.5833 | 0 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | Unit Zero | SA
Q_MARYRSF1_RB | 32267.1885 | 0 | 26.5833 | 0 | Maryrorough Run Back limit | NIL | Discretionary | Qld
N_LIMOSF2_FLT_10 | 31834.2943 | 0 | 2.5 | 0 | Limit Limondale 2 solar farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
F_I+NIL_APD_TL_L5 | 31750.0375 | 46460.1323 | 7127.75 | 7260.8333 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
S>>BRTX3_BWMP_WTTP | 31345.0546 | 0 | 3.25 | 0 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
Q_STR_7C8C_RGBSF | 31262.4676 | 0 | 2.5 | 0 | Limit Rugby Run SF output to 80% if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Strathmore SVC OS if Kar=0),60% if (Stan+Cal+Glad) >=7, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_S_HEYWOOD_UFLS | 30983.1398 | 3891.0423 | 110.3333 | 7.8333 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC.Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL | Other | Vic
N_BODWF1_ZERO | 30489.5114 | 18772.7231 | 2.4167 | 1.5 | Bodangora wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
T_T_MC_ZERO | 30000 | 15169.6463 | 0.16667 | 0.25 | Discretionary 0 MW upper limit on Macintosh generation | Outage | Discretionary | Tas
V>>S_MWP3RB_NWRB1 | 29917.8152 | 0 | 4.0833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L North West Bend-Roberstown #1 132kV line on Nil trip, Feedback | Outage | Thermal | SA
Q_STR_7C8C0K_RRSF | 29572.596 | 0 | 2.5 | 0 | No limit to Ross River SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_DAYSF | 29572.5904 | 0 | 2.5 | 0 | No limit to Daydream SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_COLSF | 29572.5747 | 0 | 2.5 | 0 | No limit to Collinsville SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_RGBSF | 29572.5638 | 0 | 2.5 | 0 | No limit to Rugby Run SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>>N-NIL_94B | 29280.214 | 0 | 5.4167 | 0 | Out= Nil, avoid O/L Beryl to Wellington 132 kV (94B) on nil trip, Feedback. Metering at Wellington is used | NIL | Thermal | NSW
Q_YARANSF1_RB | 28774.3849 | 0 | 30.25 | 0 | Yarrranlea Run Back limit | NIL | Discretionary | Qld
F_Q++LDMU_L60 | 28723.3884 | 1412.2247 | 92.4167 | 7.6667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C8C_50_HASF | 28598.6298 | 0 | 2.4167 | 0 | No limit to Haughton SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(50% if Kar=0),40% if (Stan+Cal+Glad) >=7+Kar>2,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
NRM_NSW1_QLD1 | 28244.327 | 0 | 0.25 | 0 | Negative Residue Management constraint for NSW to QLD flow. | NIL | Negative Residue | Negative Residue
Q_STR_7C2K_HASF_2 | 28202.9378 | 0 | 2.8333 | 0 | Limit 80% to Haughton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_SMSF | 27260.4251 | 0 | 2.3333 | 0 | No limit to Sun Metals SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_MAIN+APD_TL_L60 | 27046.533 | 7993.458 | 254.75 | 203.9167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V_DUNDWF3_ZERO | 27035.3644 | 413394.31 | 2.25 | 34 | Dundonnell wind farm 3 upper limit of 0 MW | Outage | Unit Zero | Vic
F_I+ML_L6_0400 | 26697.5694 | 20534.1186 | 5952.5 | 4191.0833 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
N^^Q_AR_330_BS1_1_B1 | 26609.0328 | 0 | 10.9167 | 0 | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
Q_STR_7C2K_HAMSF_2 | 26485.0887 | 0 | 2.1667 | 0 | Limit 80% to Hamilton Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
QNTE_ROC | 26296.7421 | 28587.4203 | 59.5833 | 29.9167 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | Qld
V_KIATAWF_FLT_18 | 26252.0081 | 0 | 2.5 | 0 | Limit Kiata Wind Farm upper limit to 18 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | Vic
S>>X_RBPA+CB_02 | 26225.9011 | 0 | 3.5833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | Thermal | SA
V>>N-X_MSUT_99P_1 | 25910.8764 | 0 | 36.0833 | 0 | Out= Murray to Upper Tumut(65) and either 993 or 99P,avoid Murray to Lower Tumut(66) O/L on trip of Wagga to Lower Tumut(051) and With subsequent operation of Wagga-Yass trip scheme that will open Yass?Wagga parallel(Trip 990+991),Feedback.OM607 and OM527 | Outage | Thermal | Vic
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 25687.8543 | 549343.9385 | 34.25 | 12.0833 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Thermal | Qld
N_COLEASF1_FLT_50 | 25640.5191 | 28121.8494 | 1.9167 | 2.25 | Limit Coleambally solar farm upper limit to 50 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
V_DDWF_MOPS_600 | 25547.2341 | 0 | 1.75 | 0 | Limit Dundonnell wind farm and Mortlake GT combined upper limit to 600 MW | Outage | Discretionary | Vic
S>>BRDV_RBTU_WEWT | 25263.0637 | 0 | 2.6667 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
VSML_FLT_150 | 24975.3897 | 0 | 11.3333 | 0 | Vic to SA on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to voltage oscillation | Outage | System Strength | Vic
F_V_APD01_R60 | 24438.8517 | 73403.6422 | 328.4167 | 385.3333 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
SVML_FLT_125 | 24373.5438 | 8010.4479 | 34.8333 | 3.9167 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
S>NIL_SGBN_SGSE-T2 | 24362.9657 | 92231.959 | 7.5833 | 28 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | Thermal | SA
Q_OKYOKYSF | 24319.0007 | 0 | 47.8333 | 0 | De-rating of 33kV Cable from Oakey(T189) substation to Oakey solar farms, limit total output of Oakey SF 1 and SF2 to 40MW | Outage | Thermal | Qld
F_Q++LDMU_L6 | 23321.5762 | 512.147 | 96.6667 | 6.5 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
NQTE_ROC | 22979.3103 | 6220.5569 | 63.3333 | 37.5 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Ramping | NSW
S-MWPS2-PV_0 | 22926.7507 | 0 | 1.75 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW | Outage | Unit Zero | SA
V::S_SETB_TBSE_2 | 22532.606 | 0 | 30.8333 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Transient Stability | SA
Q>>CPST_LCCP_CLWU | 22447.4907 | 0 | 2.3333 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage | Thermal | Qld
V>V_WETS_BTX_1 | 22415.0642 | 0 | 8.75 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr, prevent pre-contingent overload the remaining Wemen 220/66 kV txfmr, flow from 66 kV to 220 kV, feedback. | Outage | Thermal | Vic
F_Q++BCDM_L6 | 22246.2802 | 8586.9572 | 122 | 44.75 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
F_I+GFT_TG_R60 | 22054.0644 | 7774.985 | 262.9167 | 162.9167 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
T_T_FASH_2_N-2 | 21499.3603 | 25241.4764 | 9.8333 | 5.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Other | Tas
V_ARARATWF_FLT_60 | 21297.3101 | 0 | 7.75 | 0 | Limit Ararat Wind Farm upper limit to 60 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_STR_8C7C1S_SMSF | 21093.9623 | 0 | 4.0833 | 0 | No limit Sun Metals SF output if Stan>=2+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG)(Kar>=2 if NQLD>350&370(AVG),Ross_FN>150&170(AVG),80% if Stan>=1+(Stan+Cal+Glad) >=7+Kar>=2. Zero otherwise. | Outage | System Strength | Qld
S>>X_PARB+RB_SBUS_11 | 21065.3177 | 0 | 3.5833 | 0 | Out= Robertstown South 275kV Bus(275kV CBs ONLY O/S with associated 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Para 275kV line O/S, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
N_WELLSF1_ZERO | 21017.405 | 0 | 1.6667 | 0 | Wellington solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
T::T_HA_GT_PM_4 | 21009.3844 | 3476.7421 | 33.5833 | 4.5 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
N>>N-NIL_DPTX_2 | 20916.6771 | 9490.8491 | 1.8333 | 4.6667 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL | Thermal | NSW
V^^N_BADP_1 | 20813.4191 | 0 | 7.8333 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
S^NIL_PL_MAX | 20710.697 | 4163.4155 | 1.5833 | 0.33333 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | Voltage Stability | SA
V>>V_NIL_23 | 20613.4454 | 0 | 10.5 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL | Thermal | Vic
F_Q++MUTW_L5 | 20519.713 | 83455.227 | 81.0833 | 312.4167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
S>X-WTTP+CB_1 | 20404.8519 | 0 | 2.9167 | 0 | Out= Waterloo-Templers 132kV line + associated line CBs O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Mintaro-Waterloo 132kV line(this offloads Hummocks-Waterloo 132kV line), Feedback | Outage | Thermal | SA
V::N_NIL_xxx | 20352.5606 | 8418.7299 | 44.9167 | 37.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Transient Stability | Vic
F_S+MLMO_TL_L6_1 | 20199.2725 | 2087.0922 | 24.4167 | 5.5833 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage | FCAS | FCAS
S>>RBTU_RBPA_WTTP | 19923.4284 | 0 | 2.5833 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
N^^Q_ARDM_B1 | 19765.4932 | 0 | 9.5 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
V^SML_BUDP_3 | 19723.1089 | 3181.9122 | 88.8333 | 28.8333 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
S>>RBTU_RBPA_WEWT | 19447.6519 | 0 | 3.25 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
N>V_MSSGG_TX | 19372.7739 | 0 | 26.25 | 0 | Out = one Murray to Guthega 330/132kV Tx, Avoid another parallel Tx overload by limiting Guthega generation | Outage | Thermal | NSW
Q>>CPST_CLWU_LCCP | 18876.4943 | 0 | 3 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Thermal | Qld
N^N-LS_SVC | 18564.6516 | 32389.6039 | 69.5 | 638.5833 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | Voltage Stability | NSW
S>>BWMP_TWPA_TPRS | 18533.9896 | 1896.5051 | 2.8333 | 0.33333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
F_V_APD01_R6 | 18514.0197 | 87147.0587 | 328.4167 | 385.3333 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>N-NIL_MBDU | 18476.6807 | 18309.2436 | 56.8333 | 8.4167 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | Thermal | NSW
T_FASH_MAXGEN_1 | 18149.395 | 0 | 22.75 | 0 | Upper limit on Mackintosh + Bastyan + John Butters with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Other | Tas
S:V_550_HY_TEST | 17926.0538 | 5275.2791 | 17.75 | 19.75 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage | Oscillatory Stability | SA
T^V_NIL_11 | 17559.7133 | 12.1346 | 30.1667 | 0.083333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink harmonic filter, swamped if TVCC in service | NIL | Voltage Stability | Tas
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 17465.4017 | 60907.9478 | 31.5833 | 155.3333 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Transient Stability | Qld
Q_STR_211383_9_DAYSF | 17365.2924 | 23080.1003 | 1.25 | 1.8333 | Limit Daydream SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_RRSF | 17365.2883 | 23111.8209 | 1.25 | 1.8333 | Limit Ross River SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_CLRSF | 17365.2857 | 0 | 1.25 | 0 | Limit Clare SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_RGBSF | 17365.2856 | 23158.4512 | 1.25 | 1.8333 | Limit Rugby Run SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_HAMSF | 17365.2824 | 23131.143 | 1.25 | 1.8333 | Limit Hamilton SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_WHTSF | 17365.2814 | 24171.1287 | 1.25 | 1.9167 | Limit Whitsunday SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_HAYSF | 17365.2803 | 22052.2146 | 1.25 | 1.75 | Limit Hayman SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_COLSF | 17365.2778 | 23089.1972 | 1.25 | 1.8333 | Limit Collinsville SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
Q_STR_211383_9_KIDSF | 17365.2726 | 8384.1814 | 1.25 | 0.66667 | Limit Kidston SF,If Stan>=2+CalB>=1+CalC>=1+Glad>=3+Kar>=3,NQLD>450&470(AVG),Ross_FN>250&270(AVG),[80% of Max capacity if(Stan+Cal+Glad)>=8+Strathmore SVC OS(ramp to zero if SVC remains IS),swamp out if Stan>=3+ (Stan+Cal+Glad) >=9],Zero otherwise | Outage | System Strength | Qld
F_I+LD_N-2_MG_R6 | 17314.3528 | 0 | 4.6667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Global Raise 6 sec requirement | Outage | FCAS | FCAS
Q_STR_7C2K_HAYSF_2 | 17131.2028 | 0 | 1.5833 | 0 | Limit 80% to Hayman Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
V_WKPS12_000 | 17098.419 | 0 | 0.25 | 0 | Discretionary upper limit for West Kiewa Hydro 1 & 2 aggregate Generation of 0 MW | Outage | Unit Zero | Vic
Q::N_DM_CB_AR_2L-G | 16515.5835 | 2.2158 | 13.1667 | 0.083333 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
S>>RBTU_TWPA_TPRS | 16504.4514 | 0 | 1.3333 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
S-MWPS1-PV_0 | 16430.2562 | 0 | 1.0833 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 1 PV generation of 0 MW | Outage | Unit Zero | SA
Q_STR_7C8C0K_HAMSF | 16215.8192 | 0 | 2.3333 | 0 | No limit to Hamilton SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
Q_STR_7C8C0K_HAYSF | 16184.5609 | 0 | 2.25 | 0 | No limit to Hayman SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_MAIN++ML_L6_0400 | 16004.7461 | 10739.0038 | 1166.25 | 781.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
T_FAJB | 15937.9661 | 29400 | 0.75 | 0.16667 | Out=Farrell-John Butters 220KV line. Energy <= 0MW | Outage | Unit Zero | Tas
F_T+FASH2_C_TG_R6 | 15883.5952 | 0 | 4.3333 | 0 | Out= Farrell to Sheffield No.2 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V^^N_UTYS_1 | 15836.7172 | 31492.4201 | 33.0833 | 76.75 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q>SRMB_M020/2_M020/1 | 15816.1267 | 0 | 1.25 | 0 | Out= Susan River to Maryborough 66kV line section 2 (M020/2), avoid O/L on Susan River to Maryborough 66kV line section 1 (M020/2) trip of Nil | Outage | Thermal | Qld
Q_STR_7C8C0K_MEWF | 15776.75 | 0 | 1.3333 | 0 | No limit to Mt Emerald WF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
V_VBB_L_ZERO | 15100 | 0 | 0.083333 | 0 | Victorian Big Battery (Load Component) upper limit of 0 MW | Outage | Unit Zero | Vic
Q_STR_7C8C0K_KIDSF | 15078.9234 | 0 | 1.8333 | 0 | No limit to Kidston SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
N>>N-KVCW_4N | 15000 | 0 | 0.083333 | 0 | Out = KangarooValley-Capital(3W), avoid O/L Marulan to Dapto (8) on trip of Marulan to Avon (16) line, Feedback | Outage | Thermal | NSW
VTBL_ROC | 14278.5298 | 24961.5429 | 16.75 | 9 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Ramping | Vic
NRM_VIC1_NSW1 | 13996.0903 | 14726.8185 | 0.75 | 0.16667 | Negative Residue Management constraint for VIC to NSW flow | NIL | Negative Residue | Negative Residue
S>>X_RBTU+CB_7 | 13872.6619 | 0 | 2.3333 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, avoid O/L Robertstown 275/132kV #1 transformer on trip of Robertstown - Para line (this offloads Robertstown TX#2 132/275kV ) | Outage | Thermal | SA
VSML_190 | 13810.3401 | 0 | 1.3333 | 0 | Vic to SA on ML upper transfer limit of 190 MW | Outage | Discretionary | Vic
Q_STR_7C2K_DAYSF_2 | 13720.5231 | 0 | 1.0833 | 0 | Limit 80% to Daydream Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
T^T_LIPM_1 | 13540.375 | 0 | 8 | 0 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Voltage Stability | Tas
V::N_SMF2_SD2 | 13508.684 | 0 | 11.3333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Transient Stability | Vic
Q_MEWF1_ZERO | 13454.8043 | 2856655.1272 | 1.0833 | 247.9167 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_HAUGHTSF1_ZERO | 13263.0528 | 1431791.1197 | 1 | 114.25 | Haughton Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
F_T++NIL_MG_R5 | 12797.291 | 23670.4258 | 41.6667 | 97.25 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_T++NIL_MG_RECL_R6 | 12471.293 | 29772.7638 | 77.3333 | 66.75 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_NSW_LD_R6 | 12428.7844 | 0 | 3.1667 | 0 | Out= NIL, Liddell Power Station R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_S++HYSE_L6_1 | 12245.3283 | 362.4869 | 31.5833 | 5.4167 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS | FCAS
S>>X_CNRB+CB_01 | 12216.4275 | 0 | 4.25 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
F_MAIN++GFT_TG_R60 | 11974.9405 | 3150.6353 | 81.5833 | 22.9167 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
N^^V_LTYS_1 | 11831.4758 | 0 | 9.3333 | 0 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
T_T_FASH2_1 | 11732.6234 | 0 | 19.9167 | 0 | Out = Farrell to Sheffield no.2 220kV line, Farrell bus split, limit John Butters, Bastyan and Mackintosh to less than 110% West Coast load | Outage | Other | Tas
V_WEMENSF_21INV | 11682.0698 | 38954.5615 | 0.75 | 3.0833 | Limit Wemen Solar Farm upper limit to 0 MW if number of inverter available exceed 21. Constraint swamp out if number of inverter available not exceed 21. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
S:VS_PA_SVC_570 | 11362.3785 | 23061.8302 | 12.3333 | 31.3333 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | Oscillatory Stability | SA
S>>X_RBPA+CB_04 | 11304.9492 | 0 | 1.75 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Templers West-Para 275kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | Thermal | SA
F_T+NIL_ML_L5 | 10941.1957 | 568.1329 | 1343.8333 | 91.8333 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N_CRWASF1_ZERO | 10932.3488 | 0 | 0.75 | 0 | Corowa solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V>>N-DDWO_RADIAL_2 | 10834.442 | 0 | 13.8333 | 0 | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Thermal | Vic
V_MURRAWR_ZERO | 10703.5185 | 16005.9317 | 1 | 2.8333 | Murra Warra wind farm upper limit of 0 MW | Outage | Unit Zero | Vic
V_VS_MLMO_NETT | 10585.2638 | 80.0667 | 0.16667 | 0.66667 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage | FCAS | Vic
S>LFTI_PPPW_LFTX4 | 10565.3791 | 0 | 0.83333 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S), avoid O/L LeFevre 275/132kV TX4 on trip of Pelican Point-Parafield Gardens West 275kV line, Feedback | Outage | Thermal | SA
T>T_TUMBNN2_110_3 | 10519.5217 | 0 | 12.8333 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.2 110kV lines, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV line, Feedback | Outage | Thermal | Tas
F_I+CPP_N-2_MG_R6 | 10204.1317 | 0 | 231.9167 | 0 | Out= Nil, loss of all Callide C units declared credible, Global Raise 6 sec requirement | Outage | FCAS | FCAS
F_Q++BCDM_L5 | 10200.1978 | 2613.9893 | 34.9167 | 11.1667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
I_CTRL_ISSUE_ML | 10186.1105 | 12218.2672 | 4.0833 | 16.8333 | DC Link Control Issue Constraint for Murraylink | Outage | Other | Other
N^^V_CTMN_1 | 10097.1387 | 0 | 14.3333 | 0 | Out = Collector - Marulan (4) or Collector - Yass (3L) or Marulan - Yass (5), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>>BWMP_BGBR_HUWT | 9814.3336 | 0 | 0.83333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Redhill tee-Brinkworth 132kV line (this trips Clements Gap WF), Feedback | Outage | Thermal | SA
N^^Q_CPP_N-2 | 9741.2947 | 0 | 17.5 | 0 | Out= Nil, loss of all Callide C units declared credible, to prevent Voltage Collapse on loss of all Callide C units | Outage | Voltage Stability | NSW
V_CWWF_FLT_40 | 9491.059 | 0 | 0.75 | 0 | Limit Crowlands Wind Farm upper limit to 40 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
Q_WHITSF1_ZERO | 9381.6215 | 10334.2767 | 0.75 | 0.83333 | Whitsunday solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
Q_9C3_10C21_3_MEWF | 9352.1889 | 0 | 0.75 | 0 | Limit Mt_Emerald 70% of Max Capacity for 10C(central units)+2Kar+1Bar,NQLD>750&770(AVG),Ross_FN>440&460(AVG),65% for 10C+3Kar+1Bar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),40% for 9C+3Kar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Otherwise | Outage | System Strength | Qld
V_GANNSF_12INV | 9273.6375 | 38581.9719 | 0.58333 | 3.0833 | Limit Gannawarra Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out if number of inverter available not exceed 12. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
N_NIL_TE_B | 9231.6398 | 58800 | 26.8333 | 0.33333 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | Other | NSW
F_Q++MUTW_R6 | 9190.1175 | 97289.4127 | 40.9167 | 57.5 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
Q>NIL_MRTA_A | 9130.58 | 0 | 0.083333 | 0 | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
F_Q++8C_L60 | 9073.8119 | 2879.4176 | 55.8333 | 10.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
Q_STR_7C2K_RRSF_3 | 9025.9404 | 0 | 5.9167 | 0 | Limit 80% to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG)Zero otherwise. | Outage | System Strength | Qld
S_WATERLWF_RB | 8985.5333 | 53120.5966 | 1 | 6.3333 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | Discretionary | SA
N_DARLSF1_ZERO | 8977.3642 | 1143095.0198 | 0.66667 | 92 | Darlington Point solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
F_MAIN++NIL_BL_L6 | 8969.6091 | 346.2715 | 149.75 | 4.6667 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS | FCAS
V>>N-MSUT_1 | 8721.1692 | 0 | 24.3333 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Wagga to Lower Tumut(051) trip; Feedback | Outage | Thermal | Vic
Q^^N_AR_SVC_1 | 8662.9268 | 1099.0697 | 22 | 8.9167 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage | Voltage Stability | Qld
VSML_160 | 8552.2758 | 0 | 1.5833 | 0 | Vic to SA on ML upper transfer limit of 160 MW | Outage | Discretionary | Vic
F_MAIN+APD_TL_L5 | 8393.8681 | 3722.0793 | 255.5 | 204.8333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_Q++8C_L6 | 8308.0308 | 931.5213 | 56.4167 | 12.5833 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V::N_BYPASS_HW_SY_xxx | 8204.4788 | 8414.0544 | 12.0833 | 27.9167 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Transient Stability | Vic
F_Q++LDMU_L5 | 7894.2845 | 146.7542 | 37.25 | 1.1667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
V^^N_BURC_1 | 7892.6471 | 0 | 3.5 | 0 | Out = Buronga to Red Cliffs (0X1) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 7872.9906 | 6560.873 | 31.0833 | 47.0833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Thermal | Vic
S>RBMW4+TX_NIL_RBTX2 | 7818.3063 | 0 | 1.0833 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, avoid O/L of remaining Robertstown 132/275kV TX on Nil trip, Feedback | NIL | Thermal | SA
V_GANWR_BAT_G_ISL_0 | 7656.1482 | 216.2049 | 5.5833 | 0.33333 | Gannawarra Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
S>>X_RBTU+CB_2 | 7608.2763 | 0 | 1.4167 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) | Outage | Thermal | SA
V^^N_DTMN_1 | 7547.3824 | 0 | 5.25 | 0 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
F_T+NIL_WF_TG_R5 | 7353.9339 | 10182.252 | 1430.5 | 1076.0833 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby, Waddamana to Cattle Hill or Pieman to Granville Harbour line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N^^V_LTWG_1 | 7336.0875 | 0 | 3.75 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
T>T_NIL_BL_IMP_6EE | 6954.1281 | 0 | 0.33333 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
F_MAIN+ML_L6_0400 | 6948.8211 | 1705.6228 | 237 | 102.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
S>>PATW_RBTU_TPRS | 6920.8445 | 0 | 4.0833 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V::N_SMF2_SD1 | 6917.0637 | 0 | 9.1667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage | Transient Stability | Vic
F_T++NIL_MG_RECL_R5 | 6903.7099 | 76671.9861 | 120 | 125.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
F_T++NIL_MG_RECL_R60 | 6756.6436 | 10931.8988 | 70.5 | 84.5 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
S>>BWMP_RBTU_WTTP | 6747.1843 | 0 | 1.1667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
V_KARSF_12INV | 6737.8731 | 101092.7759 | 0.41667 | 11.9167 | Limit Karadoc Solar Farm upper limit to 0 MW if number of inverter available exceed 12. Constraint swamp out otherwise. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
F_T++NIL_MG_R60 | 6661.4977 | 9374.539 | 34.6667 | 59.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
N>>N-NIL_67 | 6542.7552 | 0 | 2.0833 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL | Thermal | NSW
S>>CGTB1_TUTB_MOTB | 6521.4772 | 3203.3772 | 2.8333 | 9.6667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage | Thermal | SA
F_T+NIL_MG_RECL_R5 | 6333.9442 | 13214.3086 | 1486.6667 | 742.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V>V_HWJL4_R_1 | 6333.3078 | 0 | 0.5 | 0 | Out = Hazelwood to Jeeralang No.4 220kV line OR Hazelwood to Jeeralang No.4 line No.4 bus 220kV CB, avoid O/L MWTS B3 220/66kV txfmr for trip of HWPS A4 500/220kV txfmr, Radial mode, YWG1 on 500kV. Swamp out if YWG1 on 220kV mode | Outage | Thermal | Vic
V_T_NIL_BL1 | 6289.4855 | 12215.5044 | 11.9167 | 13.0833 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Other | Vic
S>>NIL_BWMP_BRTW | 6273.4568 | 26753.5643 | 2.25 | 3.1667 | Out= Nil, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
Q_RRSF1_ZERO | 6239.2867 | 1047.2508 | 0.5 | 0.083333 | Ross River solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
N>>N-NIL__A_15M | 6162.5197 | 0 | 0.25 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Stockdill (1) line, Feedback | NIL | Thermal | NSW
S:V_550_HY_TEST_DYN | 6161.6853 | 24622.7428 | 26.25 | 32.3333 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | Oscillatory Stability | SA
N^^V_NIL_ARWBBA | 6121.3348 | 6670.1638 | 22 | 39.6667 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL | Voltage Stability | NSW
F_T++NIL_WF_TG_R6 | 6093.6326 | 8980.4142 | 50.3333 | 24.4167 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
N_MOREESF1_ZERO | 5854.6672 | 0 | 0.58333 | 0 | Moree Solar Farm upper limit of 0 MW | Outage | Unit Zero | NSW
N^^V_GRYS_1 | 5658.2718 | 0 | 3.5833 | 0 | Out = Gullen Range to Yass (3J), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V::N_MLSY_xxx | 5639.6202 | 0 | 15.8333 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_I+NIL_APD_TL_L6 | 5536.4109 | 26597.9656 | 751.0833 | 1980.8333 | Lower 6 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS | FCAS
V::N_KGRC_xxx | 5382.4999 | 0 | 15.3333 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q_CLARESF1_ZERO | 5347.877 | 0 | 0.41667 | 0 | Clare solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
T_T_FASH_1_N-2 | 5332.8638 | 12388.188 | 12.9167 | 13.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Other | Tas
Q_MARYRSF1_10 | 5161.2396 | 0 | 4.6667 | 0 | Maryrorough Solar Farm upper limit of 10 MW | Outage | Discretionary | Qld
Q_STR_7C2K_CLRSF_3 | 4990.7646 | 0 | 6.6667 | 0 | Limit 80% to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>450&470(AVG),Ross_FN>250&270(AVG), 40% if NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
F_I+CPP_N-2_MG_R60 | 4989.1541 | 0 | 221.5833 | 0 | Out= Nil, loss of all Callide C units declared credible, Global Raise 60 sec requirement | Outage | FCAS | FCAS
V::N_MLTR_xxx | 4952.8363 | 0 | 44.0833 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_LTWG_xxx | 4938.647 | 0 | 15.4167 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
N_BOMENSF1_ZERO | 4894.1552 | 1010.3221 | 0.33333 | 1.6667 | Bomen SF upper limit of 0 MW | Outage | Unit Zero | NSW
V>V_NIL_6 | 4871.9698 | 652.1015 | 0.5 | 0.33333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
N>N-NIL_DC | 4839.9619 | 1893.1196 | 11.75 | 4.5 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | Thermal | NSW
CA_BRIS_50132A69_1 | 4835.3417 | 0 | 0.91667 | 0 | Constraint Automation, O/L BRIRED_T:LBR:I:132@BUNGAM@SA for CTG LSJA on trip of BLYT_W-MUNN_P 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
Q:N_TW330_CB5102_OSC | 4813.4209 | 1791.0194 | 5.4167 | 6.8333 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage | Oscillatory Stability | Qld
F_Q++MUTW_R60 | 4807.8641 | 315245.2416 | 38.9167 | 67.75 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_Q++LDTW_L5 | 4788.5156 | 5112.5677 | 32.0833 | 31.3333 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
F_T++NIL_ML_L60 | 4785.5397 | 2526.6229 | 344.5 | 152.0833 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
F_T++NIL_MG_R6 | 4697.8029 | 19271.9152 | 18.25 | 34.5833 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
V_SHWF_FLT_286 | 4590.962 | 0 | 2.6667 | 0 | Limit Stockyard Hill wind farm to 286 MW if Heywood flow is above 400 MW (SA to VIC direction). Swamp otherwise. This is to manage voltage oscillation. | NIL | System Strength | Vic
F_Q++8C_L5 | 4390.3037 | 951.386 | 13.1667 | 5.1667 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage | FCAS | FCAS
SVML_FLT_150 | 4380.8613 | 1788.9746 | 8.9167 | 4.4167 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage | System Strength | SA
Q>COLTX | 4355.4895 | 0 | 0.33333 | 0 | Out = Collinsville North T1 or T2 132/33 kV transformer, limit Collinsville Solar Farm to 35MW to prevent overload on RMU of the remaining transformer | Outage | Thermal | Qld
SVML_FLT_130 | 4275.188 | 0 | 19.1667 | 0 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage | System Strength | SA
S>RBTX2_RBTX1_WEMWP4 | 4269.7117 | 0 | 3.5 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage | Thermal | SA
Q_SRSF1_ZERO | 4139.0062 | 0 | 0.33333 | 0 | Susan River Solar Farm upper limit of 0MW | Outage | Unit Zero | Qld
F_T++NIL_WF_TG_R5 | 4138.1551 | 4052.4066 | 84.1667 | 64 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
V>>V_NIL_13 | 4132.7125 | 0 | 5.5833 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL | Thermal | Vic
N_CRWF1_ZERO | 4129.7099 | 0 | 0.33333 | 0 | Crudine Ridge wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V>>N-NIL_HH | 4072.0974 | 0 | 6.5 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL | Thermal | Vic
NRM_VIC1_SA1 | 4056.5873 | 0 | 1.3333 | 0 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue | Negative Residue
T:T_LIPM_1 | 4016.2225 | 0 | 5 | 0 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Transient Stability | Tas
Q_OKYTX3 | 3966.8986 | 0 | 11.0833 | 0 | Out = Oakey 3T 110/33kV transformer, limit total output of Oakey Solar Farm 1 and 2 to 67.3MW | Outage | Thermal | Qld
S>V_RBNW_RBMWP3 | 3835.3871 | 0 | 2.8333 | 0 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage | Thermal | SA
F_Q++8E_L60 | 3821.7053 | 1295.4472 | 18.5 | 14.5833 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage | FCAS | FCAS
N^^V_MSUT_1 | 3814.2452 | 0 | 5.4167 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
F_T++NIL_WF_TG_R60 | 3802.4751 | 2544.3088 | 56.5 | 26.4167 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS | FCAS
T_BLINK_TV_NGZ | 3778.5524 | 0 | 4.25 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | Outage | Other | Tas
T_MRWF_ZERO | 3720.1224 | 37830.0485 | 1 | 9.3333 | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Unit Zero | Tas
V^T_NIL_9 | 3554.6364 | 0 | 6.3333 | 0 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL | Voltage Stability | Vic
N_MBTE1_A | 3530.7554 | 2338.1567 | 6 | 29.5833 | Out= one Directlink cable, NSW to Qld limit | Outage | Unit Zero | NSW
T::T_NIL_3 | 3516.1605 | 6461.3917 | 16.25 | 20.4167 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL | Transient Stability | Tas
F_MAIN++CPP_N-2_MGR6 | 3479.4637 | 0 | 37.0833 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>>X_CNRB+CB_04 | 3425.1012 | 0 | 2 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 132/275kV TX2 on trip of Robertstown-Para 275kV line, Feedback | Outage | Thermal | SA
Q::N_AR_CP2_AR_2L-G | 3411.9004 | 2206.8446 | 21.0833 | 9.4167 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
F_T+FASH_N-2_RREG | 3376.7454 | 539.7649 | 16.5833 | 3 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | Unit Zero - FCAS | FCAS
VSML_220 | 3358.7948 | 18457.9096 | 0.41667 | 55.75 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Discretionary | Vic
V_ELAINEWF_ZERO | 3356.727 | 2772.2353 | 2.3333 | 3.3333 | Elaine Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
I_QNI_ONE_PHASE_N-2 | 3337.2242 | 186847.9176 | 0.41667 | 18.5833 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Discretionary | Other
N>>N-PKWL_94K_3 | 3285.527 | 1696.7991 | 1.25 | 2.8333 | Out= Parkes to Wellington (94K), avoid O/L Molong to Orange North (94T) on trip of Wellington to Orange North (947), Feedback | Outage | Thermal | NSW
F_Q++8E_L6 | 3270.9847 | 2726.4541 | 18.5833 | 14.5833 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage | FCAS | FCAS
V::S_XPAVC_MAXG | 3227.2508 | 0 | 4.5833 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage | Transient Stability | SA
T::T_HA_GT_PM_6 | 3184.0996 | 0 | 4 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT out of service. | Outage | Transient Stability | Tas
Q_YARANSF1_37 | 3174.5938 | 0 | 2.8333 | 0 | Yarranlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
F_MAIN++APD_TL_L6 | 3135.3644 | 21830.0835 | 328.25 | 984.9167 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
T>T_GTSH_IMP_4K | 3102.0671 | 15212.995 | 6.5833 | 37.6667 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
N_GOONSF1_20 | 3082.6978 | 0 | 0.25 | 0 | Goonumbla solar farm upper limit of 20 MW | Outage | System Strength | NSW
N_LIMOSF2_FLT_0 | 3039.2261 | 0 | 0.25 | 0 | Limit Limondale 2 solar farm upper limit to 0 MW to manage post contingent voltage oscillation | Outage | System Strength | NSW
VS_250 | 2999.3127 | 79.0546 | 7.9167 | 1.5 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Discretionary | Vic
N>>N-NIL__H_15M | 2988.0939 | 0 | 2.5 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | Thermal | NSW
V::N_EPMB_xxx | 2970.2673 | 3607.1259 | 5.0833 | 21.1667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q:N_1078 | 2954.6116 | 347.8793 | 3.3333 | 2.4167 | QNI oscillatory stability limit of 1078 MW | Outage | Oscillatory Stability | Qld
Q_CLERMSF1_ZERO | 2925.5151 | 0 | 0.33333 | 0 | Clermont Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
SVML^MH-CAP_OFF | 2912.8577 | 0 | 7.5833 | 0 | Out= One or both Capacitor banks (i.e. 61 or 62) at Monash O/S or not available for switching, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash. | Outage | Voltage Stability | SA
F_T++FARE_N-2_TG_R6 | 2894.9167 | 1307.1104 | 10.3333 | 0.66667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
Q_STR_8C0K_HASF | 2888.581 | 0 | 0.33333 | 0 | Limit Haughton to 100% of Max capacity if Stan>=3+CalB+C>=2+Glad>=2+(Stan+Cal+Glad)>=8,NQLD>450&470(AVG),Ross_FN>250&270(AVG),0 otherwise. | Outage | System Strength | Qld
F_Q++8E_L5 | 2817.0114 | 160.3815 | 9.9167 | 2.5 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage | FCAS | FCAS
T_MRWF_GCS | 2809.8406 | 0 | 4.1667 | 0 | Musselroe wind farm Generator Control Scheme (GCS) constraint to maintain TAS FOS for a Tasmania generator event. Limit Musselroe wind farm based on load available/armed by Musselroe GCS | NIL | Other | Tas
N^^Q_LS_VC_B1 | 2754.5239 | 267.5577 | 9.4167 | 1.9167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
Q_STR_7C2K_RRSF_2 | 2752.1251 | 0 | 2 | 0 | Limit 80% to Ross River Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
F_MAIN+GFT_TG_R60 | 2748.7984 | 806.2414 | 8.5833 | 5.4167 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
N^^V_DDWG | 2663.7144 | 7476.1559 | 1 | 10.6667 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S>RBPA_BWMP_HUWT | 2646.1196 | 0 | 0.58333 | 0 | Out= Robertstown-Para 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | Thermal | SA
T^V_NIL_9 | 2645.1797 | 12738.8686 | 9.1667 | 36.3333 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Voltage Stability | Tas
N^^Q_AR_330_BS5_1_B1 | 2618.6242 | 0 | 4.25 | 0 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | Voltage Stability | NSW
T>T_FASH_1_N-2 | 2616.1803 | 1764.5968 | 3.5 | 3.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, limit Bastyan, John Butters & Mackintosh to west coast load plus Hampshire link line rating | Outage | Thermal | Tas
Q_CCHW_RAMP_ZERO | 2573.8199 | 0 | 0.16667 | 0 | Ramp Clare, Collinsville, Hamilton and Whitsunday Solar farms to zero and hold at zero. | Outage | Unit Zero | Qld
S>>CNRB_BWPA_HUWT | 2559.1469 | 0 | 0.41667 | 0 | Out= Canowie-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_I+TTS_TG_R60 | 2553.1752 | 0 | 92.1667 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
V::S_TBCP1_SETB_2 | 2543.6979 | 0 | 9.75 | 0 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
Q_NIL_STRGTH_SMSF | 2532.59 | 278438.2312 | 3.1667 | 368.8333 | Out = Nil, limit Sun metals solar farm output depends on the number units online in Stanwell, Callide B, Callide C, generators and Haughton Syncon, North Queensland demand. Zero if it does not meet the condition. | NIL | System Strength | Qld
F_T+NIL_MG_R5 | 2524.4571 | 23488.4663 | 404.75 | 1149.25 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>>V_NIL_NIL_RBNW1 | 2473.4086 | 610.0474 | 5.3333 | 0.91667 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL | Thermal | SA
S>>V_MWP3RB_RBNW1 | 2473.2818 | 0 | 6.5833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L Roberstown-North West Bend 132kV line on trip of Nil trip, Feedback | Outage | Thermal | SA
Q>>NIL_STCP_RGLC | 2442.2762 | 0 | 1.5 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Stanwell to Calliope River (848+812) line, Feedback | NIL | Thermal | Qld
F_V_APD01_R5 | 2438.2514 | 8150.1193 | 327.1667 | 385.3333 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V_MURRAWRWF_30WT | 2432.6632 | 65272.2507 | 0.16667 | 6.0833 | Limit Murra Warra Wind Farm upper limit to 0 MW if number of turbine ON exceed 30. Constraint swamp out if number of turbine ON not exceed 30. This is to manage voltage oscillation. DS only | Outage | System Strength | Vic
F_I+CPP_N-2_MG_R5 | 2397.608 | 0 | 238.4167 | 0 | Out= Nil, loss of all Callide C units declared credible, Global Raise 5 Min requirement | Outage | FCAS | FCAS
F_T+FASH_N-2_TG_R6_2 | 2394.2372 | 1721.2699 | 8.5833 | 1.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS | FCAS
N_COLWF01_ZERO | 2377.9601 | 0 | 2.3333 | 0 | Collector wind farm upper limit of 0 MW | Outage | Unit Zero | NSW
V::N_HYMO_xxx | 2325.3295 | 0 | 4.25 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_MAIN++LD_N-2_G_R6 | 2297.0797 | 0 | 2.0833 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V>V_X_HWTX1_TWO_R_1 | 2283.2475 | 0 | 1.0833 | 0 | Out= Hazelwood A1 and either A2 or A3 or A4 500/220kV transformers, avoid O/L the remaining HWTS A 500/220kV transformer on trip of the other HWTS A transformer, Radial Mode, YWG1 on 500kV, Feedback | Outage | Thermal | Vic
S:VS_PA_SVC_420 | 2272.2299 | 0 | 2.4167 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage | Oscillatory Stability | SA
F_I+LD_N-2_MG_R60 | 2261.4526 | 0 | 4.6667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Global Raise 60 sec requirement | Outage | FCAS | FCAS
F_I+GFT_TG_R5 | 2260.6095 | 1621.3049 | 265.4167 | 165.75 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
S:VS_XPAVC_460 | 2259.6426 | 2820.539 | 1.8333 | 4.4167 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood and Murraylink combined upper transfer limit of 460 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
V_MOORBWF_ZERO | 2255.5223 | 0 | 2.8333 | 0 | Moorabool Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
V>>V-LTWG_RADIAL_1 | 2246.6932 | 0 | 1.9167 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, 15 min ratings; Feedback. Swamp if VBB/SIPS available | Outage | Thermal | Vic
S>>NIL_CGTB_TUTB_1 | 2223.0608 | 17.7792 | 3.0833 | 0.41667 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL | Thermal | SA
Q_9C3_10C21_SMSF | 2221.596 | 0 | 2.25 | 0 | Limit Sun_Metals 70% Capacity if Stan>=3+CalB+CalC>=2+Glad>=3+(Stan+Cal+Glad)>=10+kar>=2+Bar>=1,NQLD>750&770(AVG),Ross_FN>440&460(AVG),40%if Stan>=3+CalB>=1+CalC>=1+Glad>=3+(Stan+Cal+Glad) >=9,kar>=3,NQLD>650&670(AVG),Ross_FN>350&370(AVG).Zero otherwise | Outage | System Strength | Qld
S>>V_NIL_NIL_RBMW3 | 2214.0401 | 2620.0579 | 1.4167 | 3.25 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL | Thermal | SA
F_MAIN+NIL_MG_R5 | 2201.6914 | 2546.359 | 234.9167 | 201.5 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS | FCAS
Q>NIL_MRTA_C | 2187.9908 | 0 | 0.33333 | 0 | Out = Nil, Oakey PS constrained to the maximum measurement limit of 1900 amps, swamp if Oakey PS runback scheme is not armed. | NIL | Thermal | Qld
S:V_XPAVC_230 | 2178.6056 | 0 | 3.3333 | 0 | Out = Para SVC 1 and 2 (Note: with both or one Black Range series caps O/S), SA to VIC on Heywood upper transfer limit of 230 MW based on oscillatory stability. | Outage | Oscillatory Stability | SA
Q_YARANSF1_37MW_N-1 | 2171.3502 | 0 | 0.83333 | 0 | Limit Yarrenlea Solar Farm to 37 MW when feeder 733/1 or 733/3 or 734/1 or 734/3 (T10 Yarranlea to H14 Middle Ridge) trip, Swamp when the feeders are in service. DS formulation only | NIL | Unit Zero | Qld
T_T_FASH2_2 | 2162.7757 | 0 | 0.75 | 0 | Out = Farrell to Sheffield no.2 220kV line, Farrell bus split, limit John Butters, Bastyan and Mackintosh to greater than 90% West Coast load | Outage | Other | Tas
S>>NIL_TBTU_TBMO_1 | 2161.3316 | 7.4914 | 2.8333 | 0.16667 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | Thermal | SA
F_T+CSGO_TG_R6_2 | 2129.9416 | 7185.0159 | 5.25 | 3.5 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS | FCAS
Q_9C3_10C21_3_HASF | 2124.9435 | 0 | 0.16667 | 0 | Limit Haughton70% of Max Capacity for 10C(central units)+2Kar+1Bar,NQLD>750&770(AVG),Ross_FN>440&460(AVG),50% for 10C+3Kar+1Bar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),40% for 9C+3Kar,NQLD>650&670(AVG),Ross_FN>350&370(AVG),Otherwise | Outage | System Strength | Qld
V_BANNERTSF_ISL_0 | 2118.4377 | 0 | 0.16667 | 0 | Limit Bannerton Solar Farm upper limit to 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
T_T_FASH_7_N-2 | 2106.7905 | 38409.7639 | 5.1667 | 6.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation <= 110% of West Coast load | Outage | Other | Tas
SVML^NIL_160 | 2104.6903 | 11646.0568 | 17.6667 | 52.1667 | Out=NIL, SA to Vic on ML upper transfer limit of 160 MW to manage voltage collapse at Monash | NIL | Discretionary | SA
N_GOONSF_11_INV | 2093.2196 | 0 | 0.16667 | 0 | Limit Goonumbla Solar Farm upper limit to 0 MW if number of inverter available exceed 11. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
N_GNNDHSF1_ZERO | 2070.5918 | 0 | 0.16667 | 0 | Gunnedah solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
Q_HAYMSF1_ZERO | 2059.2559 | 0 | 0.16667 | 0 | Hayman solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
S>>V_NWRB2_RBNW1 | 2038.6631 | 0 | 2.3333 | 0 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage | Thermal | SA
T_V_NIL_BL1 | 2017.5908 | 1178.0546 | 6.9167 | 3.5 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Other | Tas
V_BULGNA_BAT_G_ISL_0 | 2000.0075 | 0 | 0.16667 | 0 | Bulgana Battery (Generation Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
S>RBMW4__WTTP_STBG-T | 1992.641 | 0 | 0.41667 | 0 | Out= Robertstown - MWP4 O/S, avoid O/L Snowtown-Bungama T 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | Thermal | SA
F_T++FASH_N-2_TG_R60 | 1942.5108 | 15422.1425 | 9.25 | 6.3333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
T_V_NIL_FCSPS | 1941.3167 | 0 | 1 | 0 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Other | Tas
CA_BRIS_4F1FE461_1 | 1936.9477 | 0 | 6.75 | 0 | Constraint Automation, O/L MOBTAB_1:LMOB:Z:132@T_BEND@SA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
QNI_SOUTH_1150_DYN | 1936.6596 | 77156.8643 | 1.6667 | 7.8333 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL | Transient Stability | Qld
S>RBMW4+TX_NIL_RBTX1 | 1927.2783 | 0 | 4.5833 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, avoid O/L of remaining Robertstown 275/132kV TX on Nil trip, Feedback | NIL | Thermal | SA
S>>NIL_RBTU_WTTP | 1924.7128 | 0 | 0.5 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | NIL | Thermal | SA
V>>N-MSUT_2 | 1919.3015 | 0 | 8 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage | Thermal | Vic
N^^Q_BCDM_B1 | 1893.3319 | 582.8093 | 7.6667 | 0.25 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | Voltage Stability | NSW
V::N_HYSE_xxx | 1880.3852 | 0 | 3.4167 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q_MARYRSF1_5MW | 1879.5189 | 0 | 1.1667 | 0 | Maryrorough Solar Farm upper limit of 5 MW | Outage | Discretionary | Qld
N>>V_SMDD6 | 1869.1197 | 0 | 5.6667 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
T>T_PMWA_110_7 | 1834.5781 | 0 | 3.4167 | 0 | Out= Palmerston to Waddamana 110 kV line, avoid overloading the New Norfolk to Chapel St 110 kV line (flow to South) on trip of New Norfolk to Creek Road 110 kV line, feedback | Outage | Thermal | Tas
V^^N_UTRV_1 | 1811.2466 | 0 | 1.4167 | 0 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
Q^N_AR_330_BS3_1 | 1785.0681 | 0 | 4.8333 | 0 | Out= Armidale No.3 330kV bus, QLD to NSW voltage stability limit for trip of a Dumaresq to Armidale 330kV line 8E | Outage | Voltage Stability | Qld
Q_STR_7C2K_CLRSF_2 | 1777.4169 | 0 | 3.1667 | 0 | Limit 80% to Clare Solar Farm if Stan>=2+Cal>=1+Glad>=2+ (Stan+Cal+Glad) >=7+Kar>=2,NQLD>350&370(AVG),Ross_FN>150&170(AVG),Zero otherwise. | Outage | System Strength | Qld
F_T++NIL_BLSPS_R6_1 | 1763.9218 | 15213.8905 | 0.083333 | 0.16667 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS | FCAS
N^^V_BUDP_1 | 1712.3425 | 17122.4551 | 1.0833 | 15.4167 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N^^V_LTMS_1 | 1690.4094 | 0 | 3.6667 | 0 | Out = Murray to Lower Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N::N_CNSD_2 | 1688.2748 | 15468.6197 | 1.4167 | 0.33333 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | Transient Stability | NSW
N::N_BYCR_2 | 1644.0563 | 0 | 4.25 | 0 | Out = Bannaby to Crookwell (61), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | Transient Stability | NSW
F_S+MLMO_TL_L6_2 | 1631.8949 | 48102.0841 | 3.5833 | 17.8333 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage | FCAS | FCAS
S>>V_NIL_DVBG_STBG | 1616.238 | 0 | 0.41667 | 0 | Out= Nil, avoid O/L Snowtown - Bungama 132kV on trip of Davenport - Bungama 275kV line, Feedback | NIL | Thermal | SA
T^V_NIL_8 | 1598.9351 | 3643.6053 | 5.0833 | 12.8333 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Voltage Stability | Tas
T>>T_NIL_BL_EXP_7C | 1594.9968 | 4488.0013 | 6.5833 | 3.9167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Thermal | Tas
F_MAIN++CP_N-2_MGR60 | 1557.5107 | 0 | 38.4167 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S>>BRTW_BWPA_WTTP | 1548.8083 | 2.3489 | 2 | 0.25 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
S>>BRBG_BGTX_HUWT | 1528.3704 | 3083.6517 | 1.75 | 0.25 | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | Thermal | SA
S>>TBTU_TBCG_TBMO | 1525.3891 | 247.4226 | 3 | 4.1667 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage | Thermal | SA
Q_YARANSF1_37MW | 1517.9699 | 0 | 0.58333 | 0 | Yarrenlea Solar Farm upper limit of 37 MW | Outage | Discretionary | Qld
S>BRTW_BWPA_HUWT | 1505.1729 | 0.01759 | 0.083333 | 0.66667 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
V>>N-JNWO_RADIAL_1 | 1502.44 | 0 | 1.5833 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
T>T_SH_TX | 1500.4138 | 0 | 2.0833 | 0 | Out = Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open, avoid O/L the Burnie to Sheffield 220kV line or Burnie No. 2 220/110 kV txfmr for loss of the remaining Sheffield 220/110kV transformer | Outage | Thermal | Tas
F_Q++MUTW_R5 | 1492.6398 | 2292.4965 | 4.5833 | 6.6667 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
T_LIWY | 1447.72 | 0 | 0.25 | 0 | Out=Liapootah-Wayatinah 220KV line | Outage | Unit Zero | Tas
F_S_TORRB2_R60 | 1438.581 | 0 | 3.4167 | 0 | Out= NIL, Torrens B2 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V^^S_SETB_TBSE_2 | 1438.5139 | 0 | 2.0833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | Voltage Stability | SA
V::S_KHKN_MAXG_2 | 1411.1245 | 0 | 0.25 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V^SML_KGRC_4 | 1410.5375 | 557.5654 | 10.1667 | 4.1667 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Voltage Stability | Vic
F_I+GFT_TG_R6 | 1403.6462 | 1395.1589 | 40.3333 | 45.1667 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line | NIL | FCAS | FCAS
S>RB_275KV_N_BUS_1 | 1376.65 | 19592.4362 | 0.83333 | 13.8333 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage | Thermal | SA
F_S_TORRB4_R60 | 1370.131 | 0 | 2.9167 | 0 | Out= NIL, Torrens B4 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>RBTU_BWMP_TWPA | 1351.4819 | 0 | 0.58333 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | Thermal | SA
Q_YARANSF1_ZERO | 1316.4662 | 65.4655 | 1.3333 | 0.083333 | Yarranlea Solar Farm upper limit of 0 MW | Outage | Unit Zero | Qld
N^^V_SMTXF2_1 | 1306.9925 | 1952.2309 | 0.83333 | 4.1667 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
N_GOONSF1_ZERO | 1299.9896 | 0 | 0.083333 | 0 | Goonumbla solar farm upper limit of 0 MW | Outage | Unit Zero | NSW
V_ARWF_FSTTRP_5 | 1299.8426 | 2650.1933 | 0.083333 | 0.83333 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Discretionary | Vic
V::S_NIL_MG_TB_2-DS | 1274.201 | 0 | 0.083333 | 0 | Out =Nil(Note: with both Black Range series capacitors O/S); Vic-SA Tran. Stab limit for loss of SA largest generator with loss of Torrens Island B PS declared as credible (South East Capacitor Available). (NOTE: DS RHS ONLY) | NIL | Transient Stability | SA
Q_DDSF1_ZERO | 1261.4262 | 0 | 1.25 | 0 | Darling Downs solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
T>T_PMWA_110_6 | 1238.3932 | 0 | 1.6667 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
F_NSW_LD_R60 | 1208.9084 | 0 | 3.0833 | 0 | Out= NIL, Liddell Power Station R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
SVML_050 | 1207.7034 | 0 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 50 MW | Outage | Discretionary | SA
F_T+CSGO_TG_R60 | 1204.1256 | 2621.7915 | 18.25 | 5.5 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::S_RBPA_SETB | 1192.8749 | 0 | 3 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Transient Stability | SA
V::N_MLTX_xxx | 1191.3814 | 5133.7855 | 8.75 | 22.6667 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
Q_STR_32282_SMSF | 1172.0722 | 0 | 1.9167 | 0 | Limit 75% to Sun Metals SF if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, Kareeya>=2, NQLD>450&470(AVG),Ross_FN>250&270(AVG). Zero otherwise. . | Outage | System Strength | Qld
Q>CPWO_BI_INTACT | 1153.3541 | 77186.3934 | 1 | 15 | Out= 813 or 814,H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, Feedback | Outage | Thermal | Qld
F_S_DLBAT-L_L60 | 1137.7718 | 0.38 | 3.3333 | 0.16667 | Out= NIL, Dalrymple Battery (Load Component) L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++LD_N-2_G_R5 | 1131.4851 | 0 | 2.75 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V_CROWLANDS_ZERO | 1127.0144 | 0 | 0.083333 | 0 | Crowlands Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
N^N_KKLS_1 | 1116.2019 | 36.2329 | 14.5 | 2.0833 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | Voltage Stability | NSW
N::N_UTRV_2 | 1115.946 | 0 | 4.25 | 0 | Out = Upper Tumut -Ravine (6X), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
F_S_TORRB3_R60 | 1114.8693 | 0 | 1.5 | 0 | Out= NIL, Torrens B3 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V_MWWF_0_WT12 | 1079.34 | 0 | 0.083333 | 0 | Limit Murra Warra Wind Farm upper limit to 0 MW if Murra Warra wind farm turbine collector group 1 and/or 2 generating. Constraint swamp out if only turbine collector group 3 and/or 4 generating. DS only | Outage | System Strength | Vic
S>SETX_SETX_PWKN | 1050.0672 | 0 | 0.083333 | 0 | Out= One South East 275/132kV transformer O/S (i.e. TX ONLY O/S with associated TX CBs I/S), avoid O/L Penola West-KinCraig 132kV line on trip of remaining 132/275kV South East TX, Feedback | Outage | Thermal | SA
N_X_MBTE2_A & N_X_MBTE2_B | 1048.5675 | 104762.4241 | 11.0833 | 797.9167 | Out= two Directlink cables, NSW to Qld limit | Outage | Unit Zero | NSW
S>>PARS_BWPA_TWPA | 1043.7654 | 0 | 0.58333 | 0 | Out= Roseworthy - Para 132kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | Thermal | SA
F_Q++8C_R6 | 1041.2222 | 0 | 7.1667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
V::N_DDMB_xxx | 1041.1558 | 0 | 4.0833 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_WEMENSF_FLT_10 | 1036.9571 | 1049.9035 | 0.083333 | 0.083333 | Limit Wemen Solar Farm upper limit to 10 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
N_BOCORWF1_ZERO | 1036.7173 | 0 | 0.083333 | 0 | Boco Rock WF upper limit of 0 MW | Outage | Unit Zero | NSW
Q_HAMISF1_ZERO | 1033.1051 | 13302.6454 | 0.083333 | 1.0833 | Hamilton solar farm upper limit of 0 MW | Outage | Unit Zero | Qld
V_KIAMSF_FLT_90 | 1030.1577 | 0 | 0.083333 | 0 | Limit Kiamal Solar Farm upper limit to 90 MW to manage post contingent voltage oscillation | Outage | System Strength | Vic
V>S_460 | 1024.299 | 0 | 4.0833 | 0 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage | Thermal | Vic
V::N_BABE_xxx | 1011.5645 | 0 | 3.8333 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
S>NIL_NIL_SGMYSE-T2 | 999.7827 | 77.0656 | 0.25 | 0.66667 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | Thermal | SA
V:S_PA_SVC_550 | 995.0532 | 0 | 5.8333 | 0 | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage | Oscillatory Stability | Vic
T>T_NIL_BL_3C | 987.7957 | 2543.1134 | 1.9167 | 7.9167 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
N^^V_DPWG_X5_1 | 978.9133 | 0 | 4.0833 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
V_COHUNASF_ISL_0 | 975.0012 | 0 | 0.083333 | 0 | Cohuna Solar Farm upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
F_S_TORRB4_RREG | 948.1972 | 0 | 1.0833 | 0 | Out= NIL, Torrens B4 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_NSW_LD_RREG | 945.769 | 0 | 3 | 0 | Out= NIL, Liddell Power Station RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
V::N_BEKG_xxx | 939.1032 | 0 | 2.8333 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>S_460_DYN | 919.5312 | 0 | 1.8333 | 0 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage | Thermal | Vic
V::N_KTSY_xxx | 889.4807 | 0 | 0.91667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_S_TORRB3_RREG | 878.0243 | 0 | 1 | 0 | Out= NIL, Torrens B3 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++NIL_ML_L6 | 872.7038 | 5233.5314 | 135.9167 | 221.75 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
V::N_HORC_xxx | 870.2431 | 0 | 2.25 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V_GANWR_BAT_L_ISL_0 | 867.1788 | 10127.3729 | 4.4167 | 26.9167 | Gannawarra Battery (Load Component) upper limit of 0 MW to manage risk of islanding on the next contingency | Outage | Islanding - Unit | Vic
Q::N_ARSVC_AR_2L-G | 851.4563 | 555.3302 | 3.5 | 1.5833 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
N-NSNY_9GU | 850.8618 | 0 | 0.083333 | 0 | Out = Narromine South to Nyngan132 (9GU) 132 kV line, Upper limit of 52.5 on Nevertire SF, EE advice on 13/02/2020 | Outage | Other | NSW
N:V_WA_BUSA_BWRG | 847.2132 | 0 | 1.5 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage | Transient Stability | NSW
T>T_TUMBNN1_110_3 | 842.7747 | 0 | 6 | 0 | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line, avoid O/L Tungatinah to New Norfolk 110kV line on trip of Tungatinah to Meadowbank to New Norfolk No.2 110kV line, Feedback | Outage | Thermal | Tas
V>SMLBAHO1 | 823.0075 | 0 | 7.0833 | 0 | Out = Bendigo to Kerang line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of any 220kV line section between Ballarat and Horsham | Outage | Thermal | Vic
V::N_ROSM_xxx | 813.6206 | 0 | 3 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V:T_SHGT_BL_1 | 811.2862 | 272.9692 | 2 | 0.33333 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage | Other | Vic
V::N_MLMO_xxx | 802.3298 | 0 | 11.3333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V::N_DDWO_xxx | 779.3739 | 0 | 2.5 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
T_GO_300 | 777.7333 | 0 | 0.58333 | 0 | Discretionary 300 MW upper limit on total Gordon generation | Outage | Discretionary | Tas
V::S_XSEVC_MAXG | 765.0454 | 0 | 1.4167 | 0 | Out= Both South East SVC1 & SVC 2 O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
T>T_LIPM_110_2A | 763.5422 | 0 | 0.75 | 0 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line and associated CBs at Waddamana I/S, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Thermal | Tas
F_Q++ARTW_R5 | 762.6199 | 0 | 5.5 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage | FCAS | FCAS
V>>V_NIL_5 | 727.6405 | 0 | 1 | 0 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Thermal | Vic
T_T_FASH_8_N-2 | 712.98 | 11711.2915 | 0.16667 | 3.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus NOT split, Mackintosh P/S unavailable, West Coast 220/110 kV parallel open, limit all West Coast generation >= 90% of West Coast load | Outage | Other | Tas
T>T_PMWA_IMP_4D | 712.3876 | 0 | 4.9167 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V::S_BLKRG_MAXG_2 | 701.8901 | 0 | 1.75 | 0 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | Transient Stability | SA
N^^Q_LDMU_1_B1 | 689.8261 | 124.818 | 2.0833 | 1.3333 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage | Voltage Stability | NSW
F_Q++8C_R60 | 686.9751 | 4.5986 | 7.0833 | 0.16667 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
CA_BRIS_50737673_1 | 680.3033 | 0 | 3.4167 | 0 | Constraint Automation, O/L 66:LSM3:Z:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORVM2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
N_WR_30_WT-INV | 674.4556 | 51.2917 | 0.25 | 0.083333 | Limit White Rock wind/solar farm upper limit to 0 MW if number of wind turbine + inverter available exceed 30. Dispatch only. swamped out if Inverters are within the limit. | Outage | System Strength | NSW
F_MAIN++GFT_TG_R5 | 671.8792 | 52.8203 | 39.8333 | 7.5 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_ESTN+MO_TG_R60 | 657.9528 | 0 | 2.1667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 60 sec requirement for Mortlake generation loss on trip of other line | Outage | FCAS | FCAS
T>T_NIL_BL_110_5 | 643.0201 | 0 | 1.8333 | 0 | Out = Nil, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | NIL | Thermal | Tas
F_S_TORRB2_RREG | 641.6485 | 0 | 0.91667 | 0 | Out= NIL, Torrens B2 RREG Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>NIL_RBTX_RBTX_2 | 639.8669 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L of one Robertstown 132/275kV TX on trip of other Robertstown 132/275kV TX, Feedback | NIL | Thermal | SA
V_BRYBWF_ZERO | 630.8505 | 0 | 0.33333 | 0 | Berrybank Wind Farm upper limit of 0 MW | Outage | Unit Zero | Vic
S>RBTX1_RBTX2_WEMWP4 | 630.2988 | 21557.8944 | 3.8333 | 31.8333 | Out= Robertstown 275/132kV TX1, avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, | Outage | Thermal | SA
VSML_105 | 625.3624 | 0 | 1.5833 | 0 | Vic to SA on ML upper transfer limit of 105 MW | Outage | Discretionary | Vic
V^SML_BEKG_4 | 623.5697 | 468.1939 | 8.3333 | 7 | Out = Bendigo to Kerang 220kV line, avoid voltage collapse for loss of Ballarat to Waubra to Ararat 220kV line | Outage | Voltage Stability | Vic
N>>N-NIL_DPTX | 619.9105 | 8077.4937 | 0.083333 | 0.083333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL | Thermal | NSW
Q>NIL_MRTA_B | 606.0799 | 0 | 0.16667 | 0 | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line, swamp if Oakey PS runback scheme is armed or when line loading <= 5 MVA, Dispatch RHS only. | NIL | Thermal | Qld
F_T+FARE_N-2_TG_R6_2 | 604.7219 | 489.9693 | 3.4167 | 0.66667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS | FCAS
F_I+TTS_TG_R5 | 603.1347 | 0 | 89.5 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
N:V_DDSM_BWRG | 602.4983 | 0 | 0.083333 | 0 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage | Transient Stability | NSW
N::N_CTYS_2 | 601.7813 | 0 | 1.5833 | 0 | Out= Collector -Yass (3L), stability limit (Snowy-NSW) for loss of Yass-Marulan (5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage | Transient Stability | NSW
F_S_TORRB2_R6 | 584.1192 | 0 | 3.4167 | 0 | Out= NIL, Torrens B2 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
T^^V_GTSH_1 | 581.8791 | 9330.3675 | 3.1667 | 18.5 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Voltage Stability | Tas
T>T_NIL_BL_IMP_7C | 572.955 | 0 | 1 | 0 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
F_T++FASH_N-2_TG_R6 | 571.8824 | 2577.5665 | 2.5 | 4.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_T+CSGO_TG_R5 | 562.4021 | 175.951 | 18.1667 | 5.4167 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
T>T_NIL_BL_5C | 559.5568 | 180.4481 | 1.3333 | 3.4167 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Thermal | Tas
F_S_TORRB4_R6 | 532.7092 | 0 | 2.9167 | 0 | Out= NIL, Torrens B4 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N::Q_MUTW_1 | 523.6015 | 10.8683 | 2.4167 | 0.083333 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | Transient Stability | NSW
S_NIL_STRENGTH_2 | 506.9923 | 0 | 2.0833 | 0 | Maximum limit (1870 MW + Vic to SA on Heywood) for South Australian non-synchronous generation for higher number synchronous generators online for system strength requirements | NIL | System Strength | SA
F_QNV++MLMO_L60 | 506.0856 | 97.2151 | 27.3333 | 20.9167 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
N>N_LSDU_9U6_1 | 505.5706 | 0 | 1.3333 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | Thermal | NSW
S>>RBTX1_RBTX2_WEWT | 487.0387 | 2528.4867 | 1 | 1.3333 | Out= Robertstown 275/132kV TX1, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown 132/275kV TX2, Feedback | Outage | Thermal | SA
S>VMLMHNW1 | 486.9717 | 11842.9345 | 6.5833 | 22.0833 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | Thermal | SA
F_S++HYSE_L5 | 484.7436 | 531.9752 | 0.83333 | 5.0833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage | FCAS | FCAS
V>>V_BURC_5 | 481.8049 | 0 | 0.5 | 0 | Out= Buronga to Redcliffs (0X1) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage | Thermal | Vic
F_ESTN++MLMO_L60 | 461.1083 | 288.177 | 57 | 103.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
T>T_NIL_BL_IMP_7CC | 455.1487 | 202.2107 | 1.8333 | 1 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Thermal | Tas
V>>V_NIL_3 | 453.3001 | 79421.3301 | 0.58333 | 1.0833 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback. Swamp if SIPS available | NIL | Thermal | Vic
N>>V-NIL_0X1 | 451.3389 | 0.00106 | 0.58333 | 0.083333 | Out= NIL, avoid O/L Buronga to Redcliff (OX1) on Nil trip, Feedback | NIL | Thermal | NSW
N>N-NIL_TE_E1 | 446.3503 | 0 | 0.41667 | 0 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL | Thermal | NSW
V::S_BLKRG_TBSE_2 | 439.4058 | 0 | 2.1667 | 0 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | Transient Stability | SA
VT_ZERO | 439.235 | 0 | 0.16667 | 0 | Vic to Tas on Basslink upper limit of 0 MW | Outage | Interconnector Zero | Vic
F_I+ML_L6_APD | 432.7765 | 0.26 | 102.9167 | 0.41667 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
N>N-GITN_TE_C1 | 431.0752 | 0 | 3.1667 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
V::S_KHKN_MAXG | 423.7704 | 181.3606 | 0.5 | 1.6667 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
V^SML_HORC_3 | 421.5791 | 1584.9093 | 4.8333 | 0.83333 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
F_T++FARE_N-2_TG_R5 | 420.171 | 0.13055 | 3.0833 | 0.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
Q_STR_SMSF_ZERO | 418.5775 | 0 | 0.16667 | 0 | Limit 0MW to Sun Metals Solar farm for system strength requirement | Outage | System Strength | Qld
T>T_TUNN3_110_2 | 410.8426 | 0 | 2.75 | 0 | Out= Tungatinah to New Norfolk No.3 110kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
F_T+FASH_N-2_TG_R60 | 394.1398 | 305.5134 | 2.8333 | 1.5833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_X_HWSM_ROSM_xxx | 391.6242 | 0 | 1.0833 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_S_TORRB3_R6 | 370.0568 | 0 | 1.4167 | 0 | Out= NIL, Torrens B3 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N_WRWSF_ZERO | 358.455 | 0 | 1.0833 | 0 | White Rock wind farm and White Rock solar farm upper limit of zero MW | Outage | Discretionary | NSW
V^^S_TBCB94_35_SETB | 356.2593 | 0 | 1.0833 | 0 | Out= Tailem Bend 275kV CB6594 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | Voltage Stability | SA
N::Q_NIL_KC | 351.2527 | 0 | 2.5833 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL | Transient Stability | NSW
V::V_1900 | 346.2501 | 99171.4782 | 0.33333 | 1.1667 | Out=Nil, upper limit into Vic of 1900 MW | NIL | Oscillatory Stability | Vic
F_T+FARE_N-2_TG_R6_1 | 335.1434 | 184.8742 | 2.5 | 0.41667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS | FCAS
V_WETX_BANN_70 | 331.7086 | 0 | 1.3333 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr, limit Bannerton Solar Farm upper limit to 70 MW | Outage | Discretionary | Vic
V::S_NIL_TBSE_1 | 321.8602 | 0 | 0.75 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | Transient Stability | SA
V>>SML_NSWRB_11_1 | 318.6812 | 0 | 0.16667 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Wemen to Red Cliffs 220 kV line section for loss of Balranald to Buronga (X3) 220 kV line, feedback | NIL | Thermal | Vic
Q_STR_311393_SMSF | 317.9825 | 7475.5864 | 0.083333 | 12.5833 | Limit Sun Metals SF to 20% of Max capacity if Stan>=3+CalB>=1+CalC>=1+Glad>=3+Kar>=3+(Stan+Cal+Glad) >=9,NQLD>450&470(AVG),Ross_FN>250&270(AVG), Zero otherwise | Outage | System Strength | Qld
F_T+FASH2_C_TG_R60 | 317.1853 | 0 | 4.1667 | 0 | Out= Farrell to Sheffield No.2 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>V_RBNW_MWP1NWB | 316.4505 | 0 | 0.75 | 0 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Morgan Whyalla Pipeline 1 - North West Bend 132kV line on Nil trip, Feedback | Outage | Thermal | SA
QNI_SOUTH_1000_DYN | 314.4116 | 0 | 1.8333 | 0 | QLD to NSW on QNI upper transfer limit of 1000 MW, dynamic headroom, DS formulation only. | Outage | Transient Stability | Qld
F_MAIN+ML_L60_0400 | 311.1993 | 44.3764 | 3.5 | 0.91667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_S_DLBAT-L_L5 | 310.0303 | 0.38 | 3.3333 | 0.16667 | Out= NIL, Dalrymple Battery (Load Component) L5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>N-BAMB_132_OPEN_A | 304.6964 | 0 | 2.75 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | Thermal | NSW
F_QNV++MLMO_L6 | 303.7142 | 1562.8325 | 37.5833 | 19.75 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+CPP_N-2_MG_R6 | 302.8006 | 0 | 2.0833 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
VS_050 | 301.839 | 2.6163 | 0.58333 | 0.083333 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Discretionary | Vic
F_ESTN++HGML_L60 | 300.2447 | 3.65 | 32 | 1.3333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
T>T_X_TU_LE_WA_TWO_2 | 297.6903 | 0 | 0.5 | 0 | Out= both Tungatinah to Waddamana 110kV lines (direct and via Lake Echo tee), avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Thermal | Tas
SVML_080 | 289.4201 | 312.3683 | 0.66667 | 0.5 | SA to Vic on ML upper transfer limit of 80 MW | Outage | Discretionary | SA
V>>N-LTMS_1 | 279.6433 | 0 | 2.0833 | 0 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage | Thermal | Vic
S>>PARB_RBTU_RBMWP4 | 271.0556 | 0 | 0.083333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Robertstown-MWP4-Waterloo East on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
T_FARC1_2 | 268.7431 | 0 | 1.1667 | 0 | Out=Farrell - Reece 1 220KV line. Discretionary 144 MW limit on Reece 2 + Granville Harbour WF | Outage | Discretionary | Tas
F_T++FARE_N-2_TG_R60 | 262.6062 | 0 | 3 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_T+FASH2_C_RREG | 262.6055 | 0 | 1 | 0 | Out = Farrell to Sheffield No.2 line; Bastyan, John Butters, Tribute and Reece 1, 2 and Mackintosh unavailable for raise regulation | Outage | Unit Zero - FCAS | FCAS
V^^S_XPAVC_SETB | 257.8699 | 0 | 0.83333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | Voltage Stability | SA
F_T+CSGO_TG_R6_1 | 256.2599 | 2757.0265 | 4.5 | 4.25 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS | FCAS
S_LB3_0 | 252.0501 | 0 | 0.16667 | 0 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | Unit Zero | SA
V::N_HWCB_xxx | 241.4411 | 0 | 0.41667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
S_V_NIL_ROCOF | 239.2519 | 0 | 0.83333 | 0 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | ROC Frequency | SA
F_MAIN++LD_N-2_G_R60 | 239.0765 | 0 | 0.91667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
T_ROCOF_3 | 237.4438 | 600.8217 | 0.58333 | 0.41667 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL | ROC Frequency | Tas
S>>X_RBTU+CB_1 | 236.0406 | 0 | 0.91667 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) lines, Feedback | Outage | Thermal | SA
S-LBBAT-L_0 | 235.01 | 0 | 0.41667 | 0 | Discretionary upper limit for Lake Bonney Battery (Load component) of 0 MW | Outage | Unit Zero | SA
F_Q++BCDM_R60 | 224.547 | 0 | 7.9167 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_ESTN++HGTR_L60 | 223.1711 | 6.87 | 24.3333 | 1.25 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
F_T+FASH_N-2_TG_R5 | 220.1974 | 17.4321 | 9.6667 | 1.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+FARE_N-2_RREG | 217.8092 | 366.1498 | 1.1667 | 0.41667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | Unit Zero - FCAS | FCAS
F_MAIN++TTS_TG_R60 | 215.9586 | 0 | 7.4167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
Q>>CLWU_BCRG_BCCP | 213.8838 | 1181.9043 | 0.66667 | 0.5 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage | Thermal | Qld
S>NIL_NWMH1_NWMH2 | 212.2442 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on trip of North West Bend-Monash #1 132kV line, Feedback | NIL | Thermal | SA
F_I+ML_L60_0400 | 208.0117 | 83.1277 | 57.5 | 40.1667 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
CA_BRIS_507E31FE_1 | 207.5249 | 0 | 1.1667 | 0 | Constraint Automation, O/L 66:LSM3:Z:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_S++HYSE_L6_2 | 206.3564 | 0 | 4.9167 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage | FCAS | FCAS
F_Q++BCDM_R6 | 203.2908 | 0 | 8.1667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_I+TTS_TG_R6 | 200.3546 | 0 | 19.5833 | 0 | Out = Nil, Raise 6 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF, Sunraysia SF, Limondale 1 SF and Darlington Point SF due to operation of Transfer Trip Scheme (TTS) following contingency trip of line 63 | NIL | FCAS | FCAS
N>N-ARKK_CH_CB892A | 199.8356 | 0 | 0.41667 | 0 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Swamp out when all 3 directlink cable O/S, Feedback. TG formulation in PD/ST | Outage | Thermal | NSW
V^^N_CNYS_1 | 197.7762 | 0 | 0.33333 | 0 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
N::V_DDSM_MSDD | 193.002 | 0 | 1.1667 | 0 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage | Transient Stability | NSW
S>NIL_BWMP_RHBR-T | 185.4587 | 4181.1827 | 0.33333 | 0.33333 | Out= Nil, avoid O/L Redhill-Brinkworth T 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL | Thermal | SA
Q::N_30+38_AR_2L-G | 181.358 | 0 | 2.8333 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
F_I+LD_N-2_MG_R5 | 178.1278 | 0 | 4.6667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Global Raise 5 Min requirement | Outage | FCAS | FCAS
T_T_TU_105 | 174.7257 | 0 | 1.0833 | 0 | Discretionary 105 MW upper limit on Tungatinah | Outage | Discretionary | Tas
F_MAIN+TTS_TG_R60 | 171.1952 | 0 | 3.4167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
V>>N-LTWG_RADIAL_1 | 170.7486 | 0 | 0.75 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
S>NWB6022_TX2 | 169.6981 | 0 | 0.5 | 0 | Out= North West Bend CB 6022 O/S, avoid O/L North West Bend 275/132kV TX2 on trip of Robertstown-North West Bend #1 132kV line, Feedback | Outage | Thermal | SA
F_T+FASH_N-2_TG_R6_1 | 168.7479 | 62.5312 | 0.83333 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS | FCAS
S>RBMW4_TWPA_TPRS | 165.9555 | 0 | 0.16667 | 0 | Out= Robertstown - MWP4 O/S, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | Thermal | SA
F_ESTN++HGML_L6 | 165.5756 | 0.99 | 14.3333 | 0.083333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
Q::N_AR_CP1_AR_2L-G | 162.1706 | 0 | 2.0833 | 0 | Out = Armidale capacitor bank (80MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
F_T++COGT_TL_L6 | 159.1989 | 5378.0784 | 2.9167 | 50.5 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS | FCAS
F_MAIN+APD_TL_L6 | 157.98 | 2216.6918 | 14.9167 | 95.0833 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S_LBMY_2B-LB2 | 157.838 | 0 | 0.083333 | 0 | Out= Mayurra-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN), upper limit on Lake Bonney 2 WF generation constrained to 60 MW. | Outage | Discretionary | SA
F_ESTN++MLMO_L5 | 156.2711 | 32.5526 | 36.5833 | 14.1667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_MAIN+CP_N-2_MG_R60 | 148.3554 | 0 | 2 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_I+ML_L6_APD_LD | 147.999 | 2510.2806 | 97.0833 | 378.0833 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD Load excluding Portland WF | Outage | FCAS | FCAS
V::N_SMSY_xxx | 138.95 | 0 | 0.5 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
SV_100_DYN | 138.7131 | 0 | 0.16667 | 0 | SA to Victoria on Heywood upper transfer limit of 100 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Discretionary | SA
F_S_DLBAT-G_R60 | 136.0579 | 41.5233 | 3.4167 | 0.16667 | Out= NIL, Dalrymple Battery (Generation Component) R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
CA_BRIS_4F8E5761_1 | 135.53 | 0 | 0.083333 | 0 | Constraint Automation, O/L TU_NN3:LNN3:Z:110@TUNGATIN@TAS for CTG LTAB on trip of LIAPOOTA WADA PALMSTN2 220KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP1(EMPBRI) | Outage | Thermal | Constraint Automation
F_T++NIL_BLSPS_R6_4 | 135.0435 | 0 | 0.083333 | 0 | Tasmania Raise 6 sec Requirement for loss of Basslink, Segment 4, FCSPS unavailable | NIL | FCAS | FCAS
F_MAIN++ML_L6_APD_LD | 134.8281 | 5160.3279 | 32.0833 | 173.8333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage | FCAS | FCAS
T>T_FASH_2_N-2 | 134.4468 | 0 | 0.58333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.1 transformer | Outage | Thermal | Tas
Q>YLTX_DS | 134.29 | 759.6954 | 0.083333 | 0.91667 | Out = Nil, limit to Maryrorough Solar Farm to dynamic runback limit of Yarranlea 110/33kV transformer(s), DS formulation only | NIL | Thermal | Qld
N::V_MSUT | 130.5899 | 0 | 0.91667 | 0 | Out= Murray to Upper Tumut (65) line, NSW to Victoria Transient stability limit. | Outage | Transient Stability | NSW
F_T+FASH2_C_TG_R5 | 124.6149 | 0 | 8.4167 | 0 | Out= Farrell to Sheffield No.2 220kV line, Farrell 220kV bus split, Granville Harbour + Reece 1&2 + Tribute supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>>V-LTWG_RADIAL_2 | 122.5258 | 0 | 0.16667 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.1 330kV line for loss of the parallel No.2 line, 15 min ratings; Feedback. Swamp if VBB/SIPS available | Outage | Thermal | Vic
F_MAIN++CPP_N-2_MGR5 | 121.8675 | 0 | 12.3333 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V::S_RBTU_MAXG | 120.2935 | 0 | 1.1667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
F_QNV++HGML_L60 | 118.5179 | 28.78 | 6.6667 | 1.3333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_ESTN++MLMO_L6 | 113.7121 | 485.0687 | 49 | 27.5 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
V^^N_LTMS_1 | 112.3136 | 0 | 0.33333 | 0 | Out = Murray to Lower Tumut 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V>>V_KTS_TX_A2_2B_R | 110.0522 | 0 | 0.83333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Thermal | Vic
V::S_PAVC1_SETB | 108.559 | 0 | 0.5 | 0 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line. | Outage | Transient Stability | SA
F_MAIN+GFT_TG_R5 | 108.277 | 58.94 | 8 | 5.4167 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>VMLMHNW2 | 107.4404 | 0 | 0.25 | 0 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage | Thermal | SA
S_CNLK_270 | 104.3768 | 0 | 0.58333 | 0 | Out =Canowie-Mt Lock 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3 + Hornsdale battery (i.e. generation + load component)<= 270 MW | Outage | Discretionary | SA
N>>N-TW_CB5102_1 | 103.4154 | 0 | 0.33333 | 0 | Out= Tamworth 330kV CB 5102, avoid O/L Tamworth No.1 330/132 kV Tx , flow LV to HV, on trip of Armidale to Tamworth (86) line, Feedback. Nameplate rating of 150MVA is used. OM523 | Outage | Thermal | NSW
QNTE_OSCILLATE | 101.4323 | 0 | 3.3333 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Discretionary | Qld
S>MYTX1_44248OPN_LB2 | 96.6417 | 0 | 0.083333 | 0 | Out = Mayura No.1 132/33kV transformer O/S (with 33kV bus tie isolator 44248 open), Lake Bonney 2 Windfarm is constraint to a max of 60 MW | Outage | Other | SA
F_ESTN++HYMO_L60 | 96.4629 | 0 | 14 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
T>T_PMWA_IMP_4DD | 94.4088 | 0 | 0.41667 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 2 220 kV line on trip of the Palmerston to Hadspen No. 1 220 kV line with no NCSPS action, feedback | Outage | Thermal | Tas
V::S_NIL_SETB_SECP_1 | 93.9727 | 0 | 0.33333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | Transient Stability | SA
F_QNV++MLMO_L5 | 93.6315 | 1.6 | 13.0833 | 0.5 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
NSA_V_NPSD_100 | 92.8616 | 392.1172 | 0.5 | 0.5 | Newport unit >= 100 MW for Network Support Agreement | Outage | Network Support | Vic
F_MAIN++ML_L6_APD | 92.3545 | 2.74 | 10.4167 | 0.5 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS | FCAS
Q::N_LDMU_AR_2L-G | 91.651 | 0 | 0.33333 | 0 | Out = Liddell to Muswellbrook (83) line, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Transient Stability | Qld
F_Q++8C_R5 | 91.3096 | 0 | 2.1667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 5 min Requirement | Outage | FCAS | FCAS
V>>V_KTS_TX_A3_2B_R | 89.8417 | 0 | 0.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Thermal | Vic
F_MAIN++GFT_TG_R6 | 86.0092 | 200.3006 | 5.9167 | 4.1667 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL | FCAS | FCAS
F_S_DLBAT-G_R6 | 85.47 | 59.7715 | 3.4167 | 0.16667 | Out= NIL, Dalrymple Battery (Generation Component) R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
I_CTRL_ISSUE_TE | 81.9072 | 32.0542 | 2.3333 | 1.6667 | DC Link Control Issue Constraint for Terranora | Outage | Other | Other
N>N_LSDU_9U6_3 | 76.8391 | 0 | 0.58333 | 0 | Out= one of Lismore 132 to Mullumbimby 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line for trip of 9G5 (Mullumbimby to Ewingsdale) 132kV line | Outage | Thermal | NSW
F_QNV++HGTR_L60 | 76.7742 | 30.08 | 7 | 1.1667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_ESTN++HGTR_L6 | 76.07 | 1.15 | 11.0833 | 0.16667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_S_DLBAT-L_L6 | 73.3866 | 0.09 | 3.3333 | 0.16667 | Out= NIL, Dalrymple Battery (Load Component) L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
S>>NIL_BRTW_WTTP | 73.07 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | NIL | Thermal | SA
N>N-ARCH_87_TE_C1 | 71.4894 | 3037.5939 | 1.5833 | 1.5833 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | Thermal | NSW
F_T+FARE_N-2_TG_R5 | 70.9174 | 11.3494 | 6.6667 | 1.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_SMTT_xxx | 70.3636 | 0 | 1 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
F_T++CSGO_TG_R60 | 65.9599 | 1923.0864 | 0.16667 | 9.9167 | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
F_T++FASH_N-2_TG_R5 | 63.5258 | 53.39 | 8.5833 | 5.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS | FCAS
F_ESTN++HGML_L5 | 63.5196 | 4.48 | 18 | 0.83333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
N^^V_MSUT_KVCW_1 | 63.4176 | 0 | 0.5 | 0 | Out = Murray to Upper Tumut(65) and Kangaroo Valley to Capital (3W) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage | Voltage Stability | NSW
S_LBMY_2B-LB3 | 60.5732 | 0 | 0.083333 | 0 | Out= Mayurra-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN), Lake Bonney 3 constrained to 0 MW | Outage | Unit Zero | SA
V^^SML_ARWBBA_1 | 60.4998 | 0 | 0.75 | 0 | Out = Ballarat to Waubra to Ararat 220kV line (or any line section between Ballarat and Ararat), avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Voltage Stability | Vic
F_I+ML_L5_0400 | 59.67 | 96.5094 | 53.5833 | 46.75 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL | FCAS | FCAS
F_ESTN++HGTR_L5 | 58.6043 | 4.9 | 15.25 | 1.0833 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_T++CSGO_TG_R6 | 56.9453 | 3057.1809 | 0.25 | 6.8333 | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
F_MAIN+ML_L6_APD | 52.49 | 0 | 1.75 | 0 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS | FCAS
V_BA_BAT_G_ZERO | 51.5103 | 0 | 0.083333 | 0 | Ballarat Battery (Generation Component) upper limit of 0 MW | Outage | Unit Zero | Vic
S>>RBTX_BRTW_WTTP | 48.5981 | 0 | 0.083333 | 0 | Out= one Robertstown 275/132kV transformer, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | Outage | Thermal | SA
N>>N-NIL_64 | 47.0305 | 0 | 0.58333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL | Thermal | NSW
F_I+ML_L60_APD | 46.2937 | 0 | 4.6667 | 0 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
S_LB2WF_CONF | 39.8494 | 1045.4921 | 0.25 | 1.9167 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | Voltage Stability | SA
F_QNV++HGML_L6 | 39.5654 | 35.1911 | 5.4167 | 1.3333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
S^BRTW_SA_NTH | 39.2948 | 0 | 0.083333 | 0 | Out = Brinkworth-Templers West 275kV line, Manage voltage collapse in northern SA for the trip of Robertstown-Mokota 275kV line | Outage | Voltage Stability | SA
QN_1000 | 35.6801 | 0 | 0.58333 | 0 | Qld to NSW on QNI upper transfer limit of 1000 MW | Outage | Discretionary | Qld
CA_SYDS_4F1E1FC4_1 | 35.2332 | 0 | 0.16667 | 0 | Constraint Automation, O/L 85:LN85:Z:330@ARMIDALE@NSW for CTG LNPC on trip of TAMWORTH-ARMIDALE 86 330KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage | Thermal | Constraint Automation
F_ESTN+MO_TG_R5 | 34.58 | 0 | 2.6667 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line | Outage | FCAS | FCAS
V>>N-MSUT_4 | 34.2833 | 0 | 0.25 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage | Thermal | Vic
T>T_NIL_BL_110_8_1 | 33.6479 | 0.2092 | 0.083333 | 0.16667 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Thermal | Tas
F_MAIN+ML_L6_APD_LD | 32.8706 | 452.18 | 3.25 | 6.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink unable transfer FCAS | Outage | FCAS | FCAS
V^^S_PAVC_MAXG | 31.8408 | 0 | 0.083333 | 0 | Out= Para one SVC (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
N>N_LSDU_9U6_2 | 31.7989 | 0 | 0.25 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage | Thermal | NSW
S>NIL_NIL_NWMH2 | 31.2715 | 408645.2942 | 0.5 | 10.8333 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | Thermal | SA
N>>N-NIL_61 | 30.9643 | 0 | 0.083333 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) using 15 mins rating on trip of Yass to Marulan (5) line, Feedback | NIL | Thermal | NSW
F_QNV+MLMO_L60 | 28.9063 | 10.97 | 1.25 | 2.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+HYMO_L60 | 28.4268 | 0 | 1.25 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T+FARE_N-2_TG_R60 | 27.91 | 607.3474 | 0.58333 | 1.1667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
Q_STR_7C8C0K_CLRSF | 27.7858 | 0 | 0.66667 | 0 | No limit to Clare SF output if Stan>=3+Cal>=2+Glad>=2+ (Stan+Cal+Glad) >=8, NQLD>450&470(AVG),Ross_FN>250&270(AVG),60% if (Stan+Cal+Glad) >=7+Kar>2, 40% if ,NQLD>350&370(AVG),Ross_FN>150&170(AVG), Zero otherwise. | Outage | System Strength | Qld
F_QNV++HGTR_L6 | 26.66 | 19.9599 | 4.4167 | 1.1667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T++NIL_BLSPS_R60_1 | 26 | 0 | 0.083333 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS | FCAS
F_T++NIL_BLSPS_R60_4 | 26 | 0 | 0.083333 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 4, FCSPS unavailable | NIL | FCAS | FCAS
CA_BRIS_4F1FDF04_1 | 25.8033 | 0 | 0.083333 | 0 | Constraint Automation, O/L XFMR T_4@T_BEND@SA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage | Thermal | Constraint Automation
V^^N_CNLT_1 | 25.6792 | 0 | 0.083333 | 0 | Out = Canberra to Lower Tumut(07), avoid voltage collapse around Murray for loss of all APD potlines | Outage | Voltage Stability | Vic
V:SS_820_HY_TEST | 25.3533 | 140.4273 | 0.083333 | 0.58333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Oscillatory Stability | Vic
S>NIL_NIL_SGBN | 25.1428 | 11.2907 | 0.083333 | 0.16667 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | Thermal | SA
V>>V_EPTT_2B_R | 24.203 | 0 | 0.16667 | 0 | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage | Thermal | Vic
F_ESTN++HYMO_L6 | 23.95 | 0 | 8.8333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
S:V_PA_SVC_270-DS | 23.6971 | 0 | 0.083333 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW (NOTE:DS RHS ONLY) | Outage | Oscillatory Stability | SA
F_MAIN+ML_L5_0400 | 22.32 | 6.08 | 3.3333 | 0.91667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS | FCAS
F_T++CSGO_TG_R5 | 21.8434 | 60.3995 | 0.5 | 4.5833 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS | FCAS
F_MAIN+CPP_N-2_MG_R5 | 21.11 | 0 | 2 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 5 Min requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+GFT_TG_R6 | 20.79 | 78.63 | 0.33333 | 0.41667 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
F_S_DLBAT-G_R5 | 19.52 | 1.99 | 2.9167 | 0.16667 | Out= NIL, Dalrymple Battery (Generation Component) R5 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN++HYTR_L60 | 19.17 | 0 | 0.5 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS | FCAS
F_STHN++LDTW_L60 | 19.0744 | 0 | 1.3333 | 0 | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage | FCAS | FCAS
F_NVS+LDTW_L60 | 18.77 | 0 | 0.41667 | 0 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V>>N-LTYS_CH | 18.5758 | 0 | 0.16667 | 0 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
F_QNV+MLMO_L6 | 18.1918 | 194.9283 | 1.5 | 1.8333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
V::N_JNWO_xxx | 18.1564 | 0 | 0.5 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Transient Stability | Vic
V>>N-DDWO_RADIAL_1 | 17.9202 | 0 | 0.083333 | 0 | Out = Dederang to Wodonga, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Thermal | Vic
F_MAIN++TTS_TG_R5 | 15.0405 | 0 | 1.9167 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL | FCAS | FCAS
NSA_V_BDL0xxx | 14.3202 | 44685.5682 | 0.083333 | 4.0833 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Network Support | Vic
F_QNV++HGTR_L5 | 13.97 | 1.85 | 3.5833 | 0.41667 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
T_V_FCSPS_RAMP | 13.8286 | 1599.5917 | 0.33333 | 2.3333 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Ramping | Tas
N>>V_SMDD5 | 13.596 | 0 | 0.16667 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H2 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage | Thermal | NSW
V::S_BLKRG_MAXG_3 | 13.5619 | 0 | 0.083333 | 0 | Out = only one Black Range series capacitor I/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | Outage | Transient Stability | SA
F_I+ML_L5_APD | 13.43 | 0 | 4.3333 | 0 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS | FCAS
Q:N_TW330_CB5102_1 | 13.3493 | 0 | 0.083333 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW transient stability limit for trip of a Qld potline | Outage | Transient Stability | Qld
V>>N-WA_330_BUSA | 12.9116 | 0 | 0.16667 | 0 | Out= Wagga 330kV bus A, avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage | Thermal | Vic
S>NIL_NIL_MYSG-T | 12.0793 | 964.9986 | 0.083333 | 0.083333 | Out = NIL; Limit LB2 and LB3 generation to avoid OL Mayura - Snuggery T 132kV line. | NIL | Thermal | SA
S>>BWMP_BRTW_WTTP | 11.8593 | 0 | 0.083333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Brinkworth-Templers West 275kV line, Feedback | Outage | Thermal | SA
N::N_UTYS_2 | 11.8301 | 1969.4338 | 0.66667 | 8.3333 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage | Transient Stability | NSW
F_QNV+HYMO_L6 | 11.8293 | 0 | 0.91667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_WESTCOAST_LREG_0 | 11.0663 | 44.3985 | 0.41667 | 1.4167 | LREG FCAS of West Coast Generation limited to 0 MW | Outage | Unit Zero - FCAS | FCAS
F_Q_W/HOE_R5 | 11.04 | 123.2047 | 1.25 | 6 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage | Unit Zero - FCAS | FCAS
F_QNV+HGML_L60 | 10.38 | 0 | 0.5 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_WESTCOAST_RREG_0 | 10.1325 | 846.4909 | 0.25 | 1.3333 | RREG FCAS of West Coast Generation limited to 0 MW | Outage | Unit Zero - FCAS | FCAS
F_MAIN++ML_L5_0400 | 9.71 | 25.039 | 3.75 | 5.0833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_MAIN+ML_L60_APD | 9.6 | 0 | 0.083333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_QNV++HYMO_L60 | 9.46 | 0 | 0.91667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
V_V_HYMO_1 | 9.368 | 0 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line, Limit voltage unbalance at the APD 500 kV bus and Heywood 275 kV bus | Outage | Voltage Stability | Vic
F_T++BLSPS_EXP_L60_1 | 8.8917 | 11.99 | 1.25 | 2.0833 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS | FCAS
F_MAIN+TTS_TG_R5 | 8.7409 | 0 | 2.75 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink unable to transfer FCAS | NIL | FCAS | FCAS
S>>V_NIL_NIL_MW1NWB | 8.0289 | 0 | 0.083333 | 0 | Out = Nil, avoid overloading Morgan Whyalla Pump 1- North West Bend 132kV line for no contingencies, feedback | NIL | Thermal | SA
F_V_WKIEWA1_R60 | 7.89 | 0 | 0.083333 | 0 | Out= NIL, West Kiewa 1 R60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>>N-NIL_65 | 7.8018 | 0 | 0.25 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL | Thermal | NSW
F_MAIN++ML_L60_0400 | 7.5852 | 90.584 | 1.1667 | 4.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS | FCAS
F_QNV++HGML_L5 | 7.51 | 2.9113 | 3.1667 | 0.66667 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
T>T_TU_MB_NN_N-2_1 | 7.3626 | 823.3665 | 0.25 | 0.91667 | Out= Nil, Loss of both Tungatinah - Meadowbank - New Norfolk 110kV lines declared credible, avoid O/L Tungatinah to New Norfolk No.3 110kV line on trip of both Tungatinah to Meadowbank to New Norfolk 110kV lines plus Meadowbank generation. | Outage | Thermal | Tas
F_V_WKIEWA1_L60 | 6.55 | 0 | 0.25 | 0 | Out= NIL, West Kiewa 1 L60 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_QNV+HGTR_L60 | 6.473 | 0 | 0.41667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T++BLSPS_EXP_L6_1 | 6.2066 | 208.0931 | 1.25 | 2.0833 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS | FCAS
F_QNV+MLMO_L5 | 5.68 | 0.38 | 0.66667 | 0.16667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>>BWMP_RBTU_TWPA | 5.6437 | 0 | 0.16667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers West-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | Thermal | SA
F_T++NIL_ML_L5 | 5.64 | 0 | 2 | 0 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS | FCAS
N::V_MSUT_CNYS_1 | 4.6579 | 0 | 0.083333 | 0 | Out= Murray to Upper Tumut (65) and Canberra - Yass (9) 330kV lines , NSW to Victoria Transient stability limit. | Outage | Transient Stability | NSW
F_ESTN++HYTR_L6 | 4.45 | 0 | 0.41667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_MAIN++ML_L5_APD | 4.4 | 0 | 1.0833 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_MAIN++ML_L60_APD | 4.09 | 0 | 0.083333 | 0 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS | FCAS
F_Q++8E_R60 | 3.9588 | 0 | 0.16667 | 0 | Out = Sapphire to Armidale (8E) line, Qld Raise 60 sec Requirement | Outage | FCAS | FCAS
F_QNV+HGTR_L6 | 3.68 | 0 | 0.083333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+HGML_L6 | 3.49 | 0 | 0.33333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
QN_1078_OSC_AUTO | 3.3728 | 0 | 0.083333 | 0 | Upper transfer limit of 1078 MW from Qld to NSW on QNI, Active only when QNI mode cannot be monitored | NIL | Oscillatory Stability | Qld
F_QNV++HYMO_L6 | 3.0949 | 0 | 0.58333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
T_BLINK_VT_NGZ | 2.9763 | 0 | 0.083333 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow < 0, Basslink Target MW <= 0, swamped if Basslink Metered Flow > -0.1 DS only. | Outage | Other | Tas
V::S_2SE+PAVC_MAXG | 2.9578 | 0 | 0.16667 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | Transient Stability | SA
F_Q++8E_R6 | 2.8439 | 0 | 0.16667 | 0 | Out = Sapphire to Armidale (8E) line, Qld Raise 6 sec Requirement | Outage | FCAS | FCAS
F_ESTN++HYMO_L5 | 2.57 | 0 | 1.6667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_V_MBMK_L60 | 2.4 | 0 | 0.5 | 0 | Lower 60 sec Service Requirement for McKay Creek & Bogong PS set to zero due to outage of Mt Beauty to Mackay 220 kV line | Outage | Unit Zero - FCAS | FCAS
F_QNV+HGML_L5 | 2.31 | 0 | 0.33333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+HYMO_L5 | 2.306 | 0 | 0.5 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_T_FAJB_R5 | 1.8 | 0 | 0.083333 | 0 | Out=Farrell-John Butters 220KV line. R5 <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_ESTN++HYTR_L5 | 1.74 | 0 | 0.33333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage | FCAS | FCAS
F_V_WKIEWA1_R6 | 1.4 | 0 | 0.083333 | 0 | Out= NIL, West Kiewa 1 R6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
N>N-BALS_66_OPEN_A | 1.2588 | 0 | 0.083333 | 0 | Out = Any 2 66 kV lines in parallel between Lismore and Ballina that opens the 66 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | Thermal | NSW
V^^S_XPAVC_MAXG | 1.1502 | 0 | 0.083333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
F_T+GTTE_TL_L60 | 1.08 | 264.9428 | 0.5 | 21 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
S>NIL_HUWT_STBG | 1 | 0 | 0.083333 | 0 | Out = Nil; avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line [Note: Wattle PT trips when generating >=60 MW && when Dalymple Battery (i.e. both Gen and Load component) is O/S].[Note:Swamped for WTTPT<60 OR DalrB ON && WTTPT>=60] | NIL | Thermal | SA
V^^S_PAVC1_MAXG | 0.83221 | 18.2853 | 0.083333 | 0.33333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | Voltage Stability | SA
F_NVS+LDTW_L6 | 0.82 | 0 | 0.083333 | 0 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_MAIN+ML_L5_APD | 0.79 | 0 | 0.083333 | 0 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS | FCAS
F_T++NIL_BLSPS_R5 | 0.64 | 0 | 0.083333 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL | FCAS | FCAS
F_STHN++LDTW_L6 | 0.5 | 0 | 0.083333 | 0 | Out = Liddell to Tamworth (84) line, Southern Lower 6 sec Requirement | Outage | FCAS | FCAS
F_V_WKIEWA1_L6 | 0.5 | 0 | 0.083333 | 0 | Out= NIL, West Kiewa 1 L6 Requirement <= 0MW | Outage | Unit Zero - FCAS | FCAS
F_T++NIL_BLSPS_L60_1 | 0.44 | 0 | 0.083333 | 0 | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS | FCAS
F_T++NIL_BLSPS_L6_1 | 0.4 | 0 | 0.083333 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS | FCAS
F_QNV++HYMO_L5 | 0.23 | 0 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS | FCAS
F_T+GTTE_TL_L6 | 0.18 | 340.112 | 0.5 | 21.0833 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+HGTR_L5 | 0.15 | 0 | 0.083333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_QNV+MO_TG_R5 | 0.12 | 0 | 0.083333 | 0 | Out= Moorabool to Mortlake or Heywood to Mortlake line, Eastern Raise 5 min requirement for Mortlake generation loss on trip of other line, Basslink unable to transfer FCAS | Outage | FCAS | FCAS
F_Q++NIL_R5 | 0.05 | 486052.6977 | 0.41667 | 17.5833 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS | FCAS
S>HUWT_BGTX_RHBR-T | 0.01 | 50969.3059 | 0.083333 | 4.1667 | Out= Hummocks-Waterloo 132kV line, avoid O/L Redhill-Brinkworth T 132kV line on trip of Bungama 132/275kV TX, Feedback | Outage | Thermal | SA
V>>N-LTUT_M_15M | 0.00833 | 0 | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Lower Tumut to Canberra (07) trip; Feedback | Outage | Thermal | Vic
S>HUWT_NIL_STBG-T | 0.00434 | 0 | 0.25 | 0 | Out= Hummocks-Waterloo 132kV line, avoid O/L Snowtown-Bungama T 132kV line on Nil trip, Feedback | NIL | Thermal | SA

## Summary By Region
Binding Hours
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Ad-Hoc |  |  |  | 0 | 0 | 0
Constraint Automation | 24.9167 | 4.75 | 1.3333 | 8.5833 | 22.75 | 14.4167
Direction | 18.3333 | 1152.0833 | 8190.0833 | 4093.5833 | 6243.5 | 10937
FCAS | 104367.5833 | 88959.4167 | 95124.9167 | 105057.75 | 103359.8333 | 108605.1667
NSW | 2768.5 | 4260.0833 | 3057.8333 | 4993.6667 | 5560.75 | 9057.9167
Negative Residue | 46.8333 | 25.75 | 10.4167 | 24.1667 | 31.25 | 126.0833
Non-Conformance | 156.6667 | 97.3333 | 61.0833 | 93.75 | 110.5833 | 75.5
Other | 50.5833 | 311.8333 | 115.25 | 64.3333 | 48.4167 | 7.25
Outage Ramping | 251.8333 | 142.25 | 174.4167 | 475.0833 | 645.8333 | 912.5
Qld | 1756.6667 | 996.6667 | 511.3333 | 3120.5833 | 8015.5 | 4006.25
Quick | 1000.0833 | 1918.25 | 12617.6667 | 10994.8333 | 9862.0833 | 11963.75
SA | 3995.1667 | 2013.25 | 3285.75 | 3935.6667 | 4110 | 6565.9167
Tas | 895.9167 | 923.1667 | 1027.6667 | 966.5833 | 1886.6667 | 3197.8333
Vic | 6854 | 2618 | 1914.5 | 5095.75 | 6439.6667 | 8030.75
Binding Impact
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Ad-Hoc | 0 | 0 | 0 | 0 | 0 | 0
Constraint Automation | 64122.5584 | 6287.0142 | 4494.9703 | 59181.5539 | 14369.9689 | 44668.7651
FCAS | 27702893.4048 | 24018595.0767 | 11563905.7935 | 14750181.9392 | 28959781.4212 | 22909324.6631
NSW | 2981579.7124 | 3811263.7887 | 4130424.9984 | 20853119.0897 | 20558572.6087 | 70853460.552
Negative Residue | 159141.1919 | 65879.5695 | 190929.9383 | 357086.6257 | 778063.9302 | 5915845.9777
Other | 35445.6298 | 19441.5552 | 11515.5764 | 31229.546 | 199098.2389 | 13605.2418
Qld | 3412397.6405 | 1557960.0849 | 1092572.6105 | 14405785.5151 | 58969747.1872 | 29235595.5037
SA | 19175976.6502 | 19603528.2545 | 49743082.8304 | 23177002.4614 | 19911748.8298 | 32002902.6706
Tas | 3312667.8479 | 4771966.3751 | 2671514.9731 | 5630711.8908 | 7676693.2707 | 5526650.8229
Vic | 6498415.4069 | 3681628.8597 | 3495766.3104 | 19701434.9435 | 29835220.6476 | 46172027.4914
Total | 63342640.0428 | 57536550.5786 | 72904208.0013 | 98965733.5652 | 166903296.1032 | 212674081.6883
Note on A6: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Commissioning | 151.3333 | 501.9167 | 12116 | 10389.25 | 7565 | 10437.3333
FCAS - NIL | 98151.5 | 83335.5 | 89035.8333 | 86275.9167 | 87403.0833 | 97807.5
FCAS - Outage | 6213.6667 | 5623.9167 | 6087.5833 | 18781.8333 | 15954.5833 | 10797.6667
System Normal | 9089.4167 | 6047.6667 | 4947.25 | 8902 | 12236.5 | 17536.9167
Network Support | 128.3333 | 55.6667 | 210.3333 | 74.25 | 123.4167 | 49.4167
Negative Residues | 46.8333 | 25.75 | 10.4167 | 24.1667 | 31.25 | 126.0833
Outage | 7284.5833 | 5121.75 | 4817.0833 | 9302.6667 | 13833.9167 | 13369.5
Total (non-FCAS) | 16700.5 | 11752.75 | 22101.0833 | 28692.3333 | 33790.0833 | 41519.25
Binding Impact
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021
Commissioning | 1067028.2274 | 933870.4383 | 48442546.0203 | 68138620.5509 | 20610054.6861 | 29730094.3355
FCAS - NIL | 4284769.1816 | 9691374.8176 | 8309289.3932 | 10234061.3339 | 8943329.8904 | 9672529.6493
FCAS - Outage | 23418124.2233 | 14327220.2591 | 3254616.4004 | 4516120.6054 | 20016451.5307 | 13236795.0138
System Normal | 13101240.0894 | 16979263.4586 | 20382744.3293 | 37998718.3151 | 76531698.5404 | 99527702.8232
Network Support | 8878912.2779 | 965379.2057 | 30414067.7368 | 683796.7041 | 243610.7044 | 1310271.1961
Negative Residues | 159141.1919 | 65879.5695 | 190929.9383 | 357086.6257 | 778063.9302 | 5915845.9777
Outage | 13500453.0789 | 15507433.2681 | 10352560.2034 | 45175949.9811 | 60390141.5071 | 83010937.0281
Total | 64409668.2703 | 58470421.0169 | 121346754.0216 | 167104354.1161 | 187513350.7893 | 242404176.0239

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2021 Hours | 2020 Hours | Description | Type
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 314.1667 | 78.5833 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
N-Q-MNSP1 Export | N>N-NIL_LSDU | 175.8333 | 62.25 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | N_X_MBTE_3A | 157.9167 | 240.0833 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Export | N^N_CHLS_1 | 131 | 15.6667 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N>Q-NIL_757_758 | 110.0833 | 0 | Out= Nil, Avoid overloading 757 or 758 (T174 Terranora to H4 Mudgeeraba) 110kV line on trip of the other 758 or 757 (T174 Terranora to H4 Mudgeeraba line), Flow North, Feedback | NIL
N-Q-MNSP1 Export | F_Q++LDTW_R6 | 68.5 | 1.8333 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N^N-LS_SVC | 64.75 | 630.0833 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage
N-Q-MNSP1 Export | NQTE_ROC | 61 | 37.5833 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Export | N^N-89_LSTX_SVC | 52.5833 | 0 | Out= Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 40.6667 | 9.9167 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Export | N^^Q_NIL_A | 37.4167 | 6 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
N-Q-MNSP1 Export | N^^Q_MUTW_1_B1 | 37 | 3.0833 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R6 | 31.3333 | 35.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_TW_330_BUS1_B1 | 30.6667 | 0 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++LDMU_R6 | 30 | 0.75 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N^^Q_TW_330_BUS3_B1 | 25.4167 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | N^^Q_AR_VC_B1 | 14.3333 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 13.8333 | 2.0833 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N^^Q_CPP_N-2 | 13.8333 | 0 | Out= Nil, loss of all Callide C units declared credible, to prevent Voltage Collapse on loss of all Callide C units | Outage
N-Q-MNSP1 Export | N^^Q_LDTW_1_B1 | 12.4167 | 0 | Out = Liddell to Tamworth (84), avoid Voltage collapse on loss of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R5 | 11.0833 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | N^^Q_AR_330_BS1_1_B1 | 10.5833 | 0 | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R6 | 10.3333 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R60 | 9.1667 | 1.25 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | F_Q++LDMU_R5 | 8.75 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | N^^Q_ARDM_B1 | 8.3333 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^^Q_BCDM_B1 | 7.1667 | 0.083333 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 5.6667 | 29.5833 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_E_E | 5 | 0 | N-Q-MNSP1.ENERGY * 1 <= 125 (Wt = 35) | Other
N-Q-MNSP1 Export | Q>>CPST_BCRG_CLWU | 4.9167 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
N-Q-MNSP1 Export | N^^Q_AR_330_BS5_1_B1 | 4.25 | 0 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 4.25 | 1.1667 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N>>Q-LDTW_2 | 3.75 | 0 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage
N-Q-MNSP1 Export | QNTE_OSCILLATE | 3.3333 | 0 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | N>N-GITN_TE_C1 | 2.75 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R60 | 2.5 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N::Q_MUTW_1 | 2.4167 | 0.083333 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 2.3333 | 1.6667 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N::Q_NIL_KC | 2.25 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
N-Q-MNSP1 Export | F_Q++MUTW_R60 | 2.0833 | 8.0833 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-BAMB_132_OPEN_A | 2.0833 | 0 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage
N-Q-MNSP1 Export | Q>>CPST_LCCP_CLWU | 2 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R5 | 1.8333 | 2.4167 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | N^^Q_LDMU_1_B1 | 1.8333 | 1.3333 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage
N-Q-MNSP1 Export | N>N-ARCH_87_TE_C1 | 1.25 | 1.3333 | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | F_Q++LDMU_R60 | 1.1667 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement | Outage
N-Q-MNSP1 Export | N>N_LSDU_9U6_1 | 1.1667 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R5 | 1.0833 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | #R023911_001_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | N_X_MBTE2_A | 0.91667 | 38.3333 | Out= two Directlink cables, NSW to Qld limit | Outage
N-Q-MNSP1 Export | #R022167_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023092_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023353_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023625_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS1_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024053_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R022390_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R023270_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023534_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS1_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023959_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022433_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R023460_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024042_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022167_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022390_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022418_005_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022425_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022492_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022977_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N_CHLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023092_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023432_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023460_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023548_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023723_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023820_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023820_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023833_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023844_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023952_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023959_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024053_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024363_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R024378_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R024378_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | F_STHN++LDTW_L60 | 0.41667 | 0 | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-NIL_TE_E1 | 0.41667 | 0.16667 | Out= Nil, avoid Armidale to CoffsHarbour (96C) O/L on Armidale-CoffsHarbour(87) trip; Feedback, TG formulation in PD/ST | NIL
N-Q-MNSP1 Export | N>N-ARKK_CH_CB892A | 0.41667 | 0 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Swamp out when all 3 directlink cable O/S, Feedback. TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | #R022424_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R022425_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022812_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^N_CHLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022812_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^N_CHLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022945_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023335_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023340_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023353_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023548_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023656_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023746_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024010_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024325_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024389_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022400_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022400_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022418_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022433_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022437_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R022584_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022953_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^N_CHLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023285_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023292_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>N-ARTW86_1B, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R023304_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023331_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023335_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023340_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023432_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^N-LS_SVC, Effective Date: 08/05/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R023564_004_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023723_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023938_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023997_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024086_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024214_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024236_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_LDTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024236_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_LDTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024284_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024284_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024363_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R024550_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 22/06/2018, Version: 1 | Other
N-Q-MNSP1 Export | N>>Q_LDMU_B | 0.25 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage
N-Q-MNSP1 Export | #R022418_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022492_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022536_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R022581_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022689_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R022689_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R022804_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022945_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023158_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R023304_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023322_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023328_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R023391_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>>Q_LDMU_B, Effective Date: 16/07/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023534_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_AR_330_BS1_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023604_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023656_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023833_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023949_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023997_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024042_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024044_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024201_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024363_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 21/08/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024550_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 22/06/2018, Version: 1 | Other
N-Q-MNSP1 Export | NRM_NSW1_QLD1 | 0.16667 | 0 | Negative Residue Management constraint for NSW to QLD flow. | NIL
N-Q-MNSP1 Export | #R022590_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022648_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022673_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022851_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
N-Q-MNSP1 Export | #R022864_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022874_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R022969_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^N_CHLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022977_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^N_CHLS_1, Effective Date: 22/06/2020, Version: 1 | Other
N-Q-MNSP1 Export | #R022990_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B4, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023313_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023316_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023316_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023317_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023382_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>Q_LDMU_B, Effective Date: 16/07/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023391_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>>Q_LDMU_B, Effective Date: 16/07/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023746_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023789_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>N-BAMB_132_OPEN_A, Effective Date: 24/09/2015, Version: 1 | Other
N-Q-MNSP1 Export | #R023844_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023852_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023938_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R023977_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 16/07/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023990_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R023990_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
N-Q-MNSP1 Export | #R024086_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024214_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R024325_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R024549_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::Q_BWTX_KC, Effective Date: 19/01/2018, Version: 1 | Other
N-Q-MNSP1 Export | F_NVS+LDTW_L60 | 0.083333 | 0 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 233.3333 | 925.75 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 183.6667 | 46.6667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 174.9167 | 119.6667 | Out= one Directlink cable, Qld to NSW limit | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 169.0833 | 91.25 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 163.1667 | 557.0833 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 91.9167 | 5.8333 | Negative Residue Management constraint for QLD to NSW flow | NIL
N-Q-MNSP1 Import | F_Q++LDMU_L6 | 65 | 5.5 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | QNTE_ROC | 58.9167 | 30 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 54.25 | 7.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N>N-NIL_MBDU | 53.4167 | 8.8333 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 39.25 | 141.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N_NIL_TE_B | 26.8333 | 0 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 23.5833 | 8.3333 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 14.1667 | 15.4167 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | F_Q++LDMU_L5 | 13.3333 | 0.75 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 10.25 | 763.1667 | Out= two Directlink cables, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N>N-NIL_DC | 9.5833 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
N-Q-MNSP1 Import | F_Q++MUTW_L60 | 3.25 | 3.5 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_I_F | 1.4167 | 0 | N-Q-MNSP1 >= MIN(-17, InitialFlow + 80) (Wt=35) | Other
N-Q-MNSP1 Import | F_Q++ARTW_L60 | 0.91667 | 3.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | N::V_DDSM_MSDD | 0.75 | 0 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
N-Q-MNSP1 Import | #R023579_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | F_Q++LDMU_L60 | 0.58333 | 1.25 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
N-Q-MNSP1 Import | N>>N-NIL_64 | 0.58333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
N-Q-MNSP1 Import | N>N_LSDU_9U6_3 | 0.58333 | 0 | Out= one of Lismore 132 to Mullumbimby 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line for trip of 9G5 (Mullumbimby to Ewingsdale) 132kV line | Outage
N-Q-MNSP1 Import | #R022166_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023939_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022166_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023270_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023331_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023579_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023223_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023223_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024325_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022689_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022945_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R024086_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | N>>N-NIL_65 | 0.25 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL
N-Q-MNSP1 Import | N>N_LSDU_9U6_2 | 0.25 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, QLD to NSW limit | Outage
N-Q-MNSP1 Import | #R022424_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022437_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R022437_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023331_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023939_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | CA_SYDS_4F1E1FC4_1 | 0.16667 | 0 | Constraint Automation, O/L 85:LN85:Z:330@ARMIDALE@NSW for CTG LNPC on trip of TAMWORTH-ARMIDALE 86 330KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage
N-Q-MNSP1 Import | #R022304_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R023911_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | F_Q++LDTW_L60 | 0.083333 | 0.5 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 410 | 139.4167 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
NSW1-QLD1 Export | Q>>CPST_CLWU_RGLC | 95.0833 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | Q>>BCST_BCST_CLWU | 88.5 | 0 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line, avoid O/L the remaining Stanwell to Bouldercombe 848 or 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++LDTW_R6 | 72.5833 | 2.25 | Out = Liddell to Tamworth (84) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | Q>>CPWO1_CPWO2_WUGG | 65.4167 | 0 | Out= Calliope River to Woolooga (813) line Tee Gin Gin (section 1 or 2 or both), avoid O/L Calliope River to Woolooga (814) on trip of Wurdong to Teebar Creek (819) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_AR_VC_B1 | 45.8333 | 0 | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 40.6667 | 17.3333 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Export | N^^Q_NIL_A | 38.1667 | 8.8333 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
NSW1-QLD1 Export | N^^Q_MUTW_1_B1 | 37.6667 | 3.75 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage
NSW1-QLD1 Export | F_Q++MUTW_R6 | 34.4167 | 45.1667 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | F_Q++LDMU_R6 | 33.9167 | 0.75 | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS1_B1 | 33.4167 | 0 | Out= Tamworth No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | Q>>CPST_CLWU_BCST | 32.1667 | 0 | Out = 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Stanwell to Bouldercombe 849 on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS3_B1 | 27.75 | 0 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | Q>>WOPW_WOSP_WOGP_2 | 27.6667 | 0 | Out= Woolooga to Palmwoods (810) 275kV line, avoid O/L Woolooga to Gympie (748/2) 132kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | Q>>NIL_BCCP_RGLC | 20.4167 | 23 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Bouldercombe to Calliope River (812) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_CPP_N-2 | 17.5 | 0 | Out= Nil, loss of all Callide C units declared credible, to prevent Voltage Collapse on loss of all Callide C units | Outage
NSW1-QLD1 Export | F_Q++LDTW_R5 | 12.3333 | 0 | Out = Liddell to Tamworth (84) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | N^^Q_LDTW_1_B1 | 12.1667 | 0 | Out = Liddell to Tamworth (84), avoid Voltage collapse on loss of Kogan Creek generator | Outage
NSW1-QLD1 Export | F_Q++ARTW_R6 | 11.1667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_AR_330_BS1_1_B1 | 10.9167 | 0 | Out= Armidale No.1 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | F_Q++LDMU_R5 | 10.25 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | F_Q++LDTW_R60 | 10.0833 | 1.9167 | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 9.4167 | 1.9167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_ARDM_B1 | 8.75 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | F_Q++BCDM_R6 | 8.1667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_BCDM_B1 | 7.6667 | 0.25 | Out= one Bulli Creek - Dumaresq (8L or 8M) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | Q>>CPST_BCRG_CLWU | 5.75 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++8C_R6 | 5.1667 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_AR_330_BS5_1_B1 | 4.25 | 0 | Out= Armidale No.5 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | N>>Q-LDTW_2 | 3.1667 | 0.083333 | Out= Liddell-Tamworth(84), avoid O/L Liddell to Muswellbrook (83) on trip of QLD largest generation, Feedback | Outage
NSW1-QLD1 Export | Q>>NIL_CLWU_RGLC | 3.1667 | 22.9167 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Calvale to Wurdong (871) line, Feedback | NIL
NSW1-QLD1 Export | F_Q++ARTW_R60 | 2.6667 | 0.75 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_NIL_KC | 2.5833 | 0 | Out= Nil, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | NIL
NSW1-QLD1 Export | F_Q++MUTW_R60 | 2.3333 | 14.4167 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | N::Q_MUTW_1 | 2.3333 | 0.083333 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | Q>>CPST_CLWU_LCCP | 2.25 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_LDMU_1_B1 | 2.0833 | 1.3333 | Out = Liddell to Muswellbrook (83), avoid Voltage collapse on loss of Kogan Creek generator | Outage
NSW1-QLD1 Export | Q>>CPST_LCCP_CLWU | 2.0833 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders, avoid O/L Calvale to Wurdong (871) on trip of Larcom Creek to Calliope River (8859) line, Feedback | Outage
NSW1-QLD1 Export | F_Q++MUTW_R5 | 1.9167 | 2.3333 | Out = Muswellbrook to Tamworth (88) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_I_F | 1.75 | 1.9167 | NSW1-QLD1 >= MIN(-165, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Export | F_Q++LDMU_R60 | 1.4167 | 0 | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | Q>>NIL_STCP_RGLC | 1.3333 | 0 | Out= Nil, avoid O/L Raglan to Larcom Creek (8875) on trip of Stanwell to Calliope River (848+812) line, Feedback | NIL
NSW1-QLD1 Export | F_Q++ARTW_R5 | 1.25 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | F_Q++8C_R5 | 1 | 0 | Out = Armidale to Dumaresq (8C), Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | #R023625_003_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS1_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | N>>Q_LDMU_B | 0.66667 | 0 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage
NSW1-QLD1 Export | Q>>CLWU_BCRG_BCCP | 0.66667 | 0.5 | Out= Calvale to Wurdong (871), avoid O/L Bouldercombe to Calliope River (812) on trip of Bouldercombe to Raglan (811) line, Feedback | Outage
NSW1-QLD1 Export | #R022390_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023534_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS1_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023959_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022433_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023746_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024042_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 0.5 | 0.33333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | #R022390_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022418_005_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022425_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022425_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022492_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023548_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023723_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023820_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023820_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023833_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023952_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023959_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | F_Q++BCDM_R60 | 0.41667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | F_STHN++LDTW_L60 | 0.41667 | 0 | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage
NSW1-QLD1 Export | #R023548_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023656_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023746_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024010_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024389_006_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022400_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022400_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022418_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022433_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022584_003_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022891_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023285_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023292_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>N-ARTW86_1B, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023304_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023564_004_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_AR_330_BS5_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023844_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023938_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023997_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024201_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024214_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024236_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^Q_LDTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024550_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 22/06/2018, Version: 1 | Other
NSW1-QLD1 Export | F_Q++8C_R60 | 0.25 | 0.16667 | Out = Armidale to Dumaresq (8C), Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | #R022418_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022492_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022581_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022773_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022804_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023158_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023304_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023322_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023382_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>>Q_LDMU_B, Effective Date: 16/07/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023391_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N>>Q_LDMU_B, Effective Date: 16/07/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023534_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_AR_330_BS1_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023604_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023656_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023833_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023949_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023997_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024042_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024044_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024087_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^Q_ARDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024550_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N::Q_RGSW_KC, Effective Date: 22/06/2018, Version: 1 | Other
NSW1-QLD1 Export | NRM_NSW1_QLD1 | 0.16667 | 0 | Negative Residue Management constraint for NSW to QLD flow. | NIL
NSW1-QLD1 Export | #R022590_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022648_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022673_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022688_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022813_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>>Q-LDTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022851_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022851_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 22/08/2018, Version: 1 | Other
NSW1-QLD1 Export | #R022864_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022874_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R022990_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B4, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023313_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023316_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023316_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023317_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023391_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>>Q_LDMU_B, Effective Date: 16/07/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023432_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 19/01/2018, Version: 1 | Other
NSW1-QLD1 Export | #R023723_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 20/08/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023844_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023852_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_TW_330_BUS3_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023938_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R023977_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 16/07/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023990_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
NSW1-QLD1 Export | #R023990_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 06/10/2021, Version: 1 | Other
NSW1-QLD1 Export | #R024214_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^Q_TW_330_BUS1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024236_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_LDTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R024549_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::Q_BWTX_KC, Effective Date: 19/01/2018, Version: 1 | Other
NSW1-QLD1 Export | F_NVS+LDTW_L60 | 0.083333 | 0 | Out = Liddell to Tamworth (84) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
NSW1-QLD1 Import | F_Q++MUTW_L6 | 246.4167 | 1006.8333 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L6 | 203 | 57.9167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++LDTW_L6 | 187.5 | 92.75 | Out = Liddell to Tamworth (84) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | Q^^NIL_QNI_SRAR | 131.6667 | 395.4167 | Out = Nil, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | NIL
NSW1-QLD1 Import | F_Q++BCDM_L6 | 104.0833 | 35.6667 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 100 | 5.9167 | Negative Residue Management constraint for QLD to NSW flow | NIL
NSW1-QLD1 Import | F_Q++LDMU_L6 | 78.6667 | 5.75 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L5 | 62.9167 | 11 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++8C_L6 | 48.4167 | 9.3333 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++MUTW_L5 | 40.9167 | 157.6667 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 29.6667 | 154.5 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL
NSW1-QLD1 Import | Q^^N_AR_SVC_1 | 22 | 8.9167 | Out = Armidale SVC, limit QLD to NSW on QNI to avoid voltage instability on trip of Sapphire - Armidale (8E) 330 kV line | Outage
NSW1-QLD1 Import | Q::N_AR_CP2_AR_2L-G | 21.0833 | 9.4167 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++BCDM_L5 | 18.0833 | 4.75 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++LDMU_L5 | 17.4167 | 0.75 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 15.4167 | 15.5 | Out = Liddell to Tamworth (84) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++BCDM_L60 | 14.4167 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 13.5 | 27.75 | NSW1-QLD1 >= MIN(-165, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | Q::N_DM_CB_AR_2L-G | 13.1667 | 0.083333 | Out = one Dumaresq 330kV CB (5312, 5322, 5332, 5342) O/S, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++8E_L6 | 11.5 | 13 | Out = Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | N>N-NIL_DC | 7.5 | 3.75 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
NSW1-QLD1 Import | F_Q++8C_L5 | 6 | 3.25 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q:N_TW330_CB5102_OSC | 5.4167 | 6.8333 | Out= Tamworth 330kV CB 5102, Qld to NSW Oscillatory stability limit | Outage
NSW1-QLD1 Import | F_Q++8E_L5 | 5.3333 | 1.6667 | Out = Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q^N_AR_330_BS3_1 | 4.5 | 0 | Out= Armidale No.3 330kV bus, QLD to NSW voltage stability limit for trip of a Dumaresq to Armidale 330kV line 8E | Outage
NSW1-QLD1 Import | F_Q++MUTW_L60 | 3.5 | 3.5833 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | Q::N_ARSVC_AR_2L-G | 3.5 | 1.5833 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | Q:N_1078 | 3 | 2.1667 | QNI oscillatory stability limit of 1078 MW | Outage
NSW1-QLD1 Import | Q::N_30+38_AR_2L-G | 2.8333 | 0 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++8C_L60 | 2.4167 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | Q::N_AR_CP1_AR_2L-G | 2.0833 | 0 | Out = Armidale capacitor bank (80MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | QNI_SOUTH_1000_DYN | 1.8333 | 0 | QLD to NSW on QNI upper transfer limit of 1000 MW, dynamic headroom, DS formulation only. | Outage
NSW1-QLD1 Import | F_Q++ARTW_L60 | 1.75 | 3.1667 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | QNI_SOUTH_1150_DYN | 1.6667 | 8 | QLD to NSW on QNI upper transfer limit of 1150 MW, dynamic headroom, DS formulation only. | NIL
NSW1-QLD1 Import | N::V_DDSM_MSDD | 1.0833 | 0 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
NSW1-QLD1 Import | #R023437_002_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP1_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R022734_017_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint Q^^N_AR_SVC_1, Effective Date: 16/05/2019, Version: 1 | Other
NSW1-QLD1 Import | #R023802_003_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint Q:N_TW330_CB5102_OSC, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | F_Q++LDMU_L60 | 0.58333 | 1.4167 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | N>>N-NIL_64 | 0.58333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
NSW1-QLD1 Import | V::N_BYPASS_HW_SY_Q1 | 0.58333 | 0 | Out = SMTS 500kV bus, CB or SMTS bus bypass, prevent transient instability for fault and trip of HWTS-SMTS and SMTS-SYTS lines, QLD accelerates. Yallourn W1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
NSW1-QLD1 Import | #R023645_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q::N_AR330B3_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023650_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q::N_AR330B3_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023655_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint Q^N_AR_330_BS3_1, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | I_QNI_ONE_PHASE_N-2 | 0.41667 | 18.5 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage
NSW1-QLD1 Import | #R023655_005_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q^N_AR_330_BS3_1, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R023802_003_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q:N_TW330_CB5102_OSC, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | N>>N-TW_CB5102_1 | 0.33333 | 0 | Out= Tamworth 330kV CB 5102, avoid O/L Tamworth No.1 330/132 kV Tx , flow LV to HV, on trip of Armidale to Tamworth (86) line, Feedback. Nameplate rating of 150MVA is used. OM523 | Outage
NSW1-QLD1 Import | Q::N_LDMU_AR_2L-G | 0.33333 | 0 | Out = Liddell to Muswellbrook (83) line, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | #R023344_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q::N_LDMU_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023371_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q::N_LDMU_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023515_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023515_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023645_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint Q::N_AR330B3_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | N>>N-NIL_65 | 0.25 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL
NSW1-QLD1 Import | #R023291_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q::N_ARTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | CA_SYDS_4F1E1FC4_1 | 0.16667 | 0 | Constraint Automation, O/L 85:LN85:Z:330@ARMIDALE@NSW for CTG LNPC on trip of TAMWORTH-ARMIDALE 86 330KV LINE. Generated by STNET[BNECR1] Host NORREGEEMP3(EMPSYD) | Outage
NSW1-QLD1 Import | V::N_BYPASS_HW_SY_Q3 | 0.16667 | 0.25 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
NSW1-QLD1 Import | #R022716_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R022751_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R022751_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_MUTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R022761_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_ARTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R023257_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | #R023645_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q^N_AR_330_BS3_1, Effective Date: 21/08/2013, Version: 1 | Other
NSW1-QLD1 Import | #R023690_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_LDMU_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R024397_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_LDTW_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | F_Q++8E_L60 | 0.083333 | 0 | Out = Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++LDTW_L60 | 0.083333 | 0.5 | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
NSW1-QLD1 Import | Q:N_TW330_CB5102_1 | 0.083333 | 0 | Out= Tamworth 330kV CB 5102, Qld to NSW transient stability limit for trip of a Qld potline | Outage
NSW1-QLD1 Import | QN_1078_OSC_AUTO | 0.083333 | 0 | Upper transfer limit of 1078 MW from Qld to NSW on QNI, Active only when QNI mode cannot be monitored | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 1341.6667 | 1384.25 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 593.0833 | 646.1667 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 556.8333 | 477.3333 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++RREG_0220 | 213.3333 | 25.3333 | Mainland Raise Regulation Requirement greater than 200 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 113.75 | 45.5833 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 105.1667 | 56.4167 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++GFT_TG_R60 | 45.8333 | 12.8333 | Out= Nil, Raise 60 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 39.0833 | 64.5 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 28.4167 | 35.75 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
T-V-MNSP1 Export | T^V_NIL_11 | 25 | 0 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink harmonic filter, swamped if TVCC in service | NIL
T-V-MNSP1 Export | TVBL_ROC | 22.1667 | 15.5833 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Export | F_MAIN++CPP_N-2_MGR6 | 21.25 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++GFT_TG_R5 | 16.5 | 3.1667 | Out= Nil, Raise 5 min requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++CP_N-2_MGR60 | 13.5833 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T^V_NIL_9 | 8.5 | 34 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 6.4167 | 3.4167 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL
T-V-MNSP1 Export | T^V_NIL_8 | 4.5833 | 11.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | F_MAIN++TTS_TG_R60 | 4.4167 | 0 | Out = Nil, Raise 60 sec requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | T::T_HA_GT_PM_6 | 4 | 0 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following trip of remaining in-service Hadspen to George Town or Palmerston to Hadspen 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Export | F_MAIN++CPP_N-2_MGR5 | 3.9167 | 0 | Out= Nil, loss of all Callide C units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T^^V_GTSH_1 | 3.1667 | 17.8333 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 2.9167 | 19.75 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_MAIN++GFT_TG_R6 | 2 | 1.5833 | Out= Nil, Raise 6 sec requirement for a Mainland Network Event - loss of Waubra, Ararat, Crowlands, Bulgana and Murra Warra wind farms due to operation of GFT following a trip of ARTS - WBTS - BATS 220kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++LD_N-2_G_R5 | 1.5 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 1 | 0 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | F_MAIN++LD_N-2_G_R6 | 0.91667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2B_R | 0.83333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_1 | 0.75 | 0.5 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 0.75 | 0 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_T++BLSPS_EXP_L60_1 | 0.5 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A3_2B_R | 0.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
T-V-MNSP1 Export | F_MAIN++LD_N-2_G_R60 | 0.41667 | 0 | Out= Nil, loss of all Liddell Power Station units declared credible, Mainland Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++TTS_TG_R5 | 0.41667 | 0 | Out = Nil, Raise 5 min requirement for a Network Event - loss of Silverton WF, Broken Hill SF,Sunraysia SF,Limondale 1 SF and DarlingtonPoint SF due to operation of Transfer Trip Scheme (TTS) following loss of line 63, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | #R023386_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
T-V-MNSP1 Export | T_V_FCSPS_RAMP | 0.33333 | 1.9167 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage
T-V-MNSP1 Export | #R022394_006_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint T::T_HA_GT_PM_6, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Export | #R024179_019_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | TV_ZERO | 0.25 | 0 | Tas to Vic on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Export | #R023393_006_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
T-V-MNSP1 Export | #R023599_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 20/07/2021, Version: 1 | Other
T-V-MNSP1 Export | #R024179_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 10/12/2018, Version: 1 | Other
T-V-MNSP1 Export | V>>V_EPTT_2B_R | 0.16667 | 0 | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L6_1 | 0.083333 | 0 | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
T-V-MNSP1 Export | T_BLINK_VT_NGZ | 0.083333 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow < 0, Basslink Target MW <= 0, swamped if Basslink Metered Flow > -0.1 DS only. | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 672.8333 | 686.1667 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 532.9167 | 1040.4167 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 373.75 | 206.3333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 272.9167 | 51.5 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 181.0833 | 268.4167 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L6 | 123.6667 | 351.6667 | Out = Nil, Lower 6 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0210 | 118 | 86 | Mainland Lower Regulation Requirement greater than 210 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | VT_ZERO | 71.25 | 60.5 | Vic to Tas on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Import | F_T++RREG_0050 | 63.3333 | 91.3333 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_DDSM_V1 | 51.4167 | 0.16667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_MAIN++NIL_BL_L6 | 46.6667 | 1.4167 | Mainland Lower 6 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | V::N_DDSM_V2 | 45.1667 | 8.5833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SMF2_V2 | 42 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_NILxxx | 41.4167 | 33.5833 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
T-V-MNSP1 Import | V::N_MLTR_V2 | 35.0833 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_S1 | 33.8333 | 17 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 30.5 | 32.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 25.1667 | 4.5 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 22.4167 | 17.1667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_SMF2_S2 | 19.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 17.75 | 22.1667 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_HWSM_V1 | 17.1667 | 19.5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_SMF2_V1 | 16.75 | 3.9167 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | VTBL_ROC | 16.25 | 8.9167 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 15.25 | 6 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 15.0833 | 13.9167 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_DDSM_S1 | 13.6667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | T::T_NIL_3 | 13.25 | 19.9167 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line. Swamp out when Basslink export or inertia of machines exporting through Sheffield < 1850 MWs. | NIL
T-V-MNSP1 Import | V::N_HWSM_SD | 11.25 | 3.9167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_HWSM_V2 | 11 | 38.75 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V_T_NIL_BL1 | 10.8333 | 11.8333 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 10.5833 | 24.25 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_MLMO_V2 | 10.5833 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 10.4167 | 11.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_SMF2_SD2 | 10.1667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L6 | 9.75 | 6.8333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 9.1667 | 4.8333 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_APD_LD | 8.75 | 59.0833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD Load excluding Portland WF, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V::N_SMF2_SD1 | 8.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_KGRC_V1 | 7.25 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L60 | 6.25 | 9.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V^T_NIL_9 | 6 | 0 | Limit Basslink import to 350 MW (flow from Vic to Tas) under conditions of sustained low fault levels at George Town 220kV, and one or more 43 MVAr harmonic filters is out of service (Not available, Disconnector/Isolator OPEN). DS ONLY | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 5.1667 | 2 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_KGRC_S1 | 4.8333 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 4.1667 | 5.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T_BLINK_TV_NGZ | 4.0833 | 0 | Out = Nil, manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. If Basslink Metered Flow > 0, Basslink Target MW >= 0, swamped if Basslink Metered Flow < 0.1 DS only. | Outage
T-V-MNSP1 Import | V::N_MLTX_V1 | 4.0833 | 7.25 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_QNV++MLMO_L5 | 3.5833 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BABE_S1 | 3.5833 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_LTWG_S1 | 3.5833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_MLTX_S1 | 3.5833 | 0.33333 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V1 | 3.5 | 0.16667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_MLSY_S1 | 3.4167 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_LTWG_V1 | 3.0833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_MLSY_V1 | 3 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 2.9167 | 0.16667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_HYMO_S1 | 2.8333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 2.6667 | 1.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 2.4167 | 2.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_DDWO_V1 | 2.0833 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_HYSE_S1 | 1.9167 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V:T_SHGT_BL_1 | 1.9167 | 0.33333 | Out = Sheffield to George Town 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Sheffield to George Town 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V3 | 1.75 | 5.1667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S2 | 1.5 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | V::N_EPMB_V1 | 1.4167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_BEKG_V1 | 1.3333 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 1.25 | 0.33333 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HGML_L60 | 1.25 | 0.25 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HGML_L6 | 1.1667 | 0.75 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDMB_S1 | 1.0833 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 1 | 0.91667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_HYSE_V1 | 1 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_ROSM_V2 | 1 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R5 | 0.91667 | 0.16667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 0.91667 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S3 | 0.91667 | 6.9167 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | V::N_HORC_V1 | 0.91667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_ROSM_S2 | 0.91667 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 0.83333 | 1.5 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | #T-V-MNSP1_RAMP_E_F | 0.75 | 0 | T-V-MNSP1 >= MIN(0, InitialFlow + 200) (Wt=35) | Other
T-V-MNSP1 Import | V::N_HYMO_V1 | 0.75 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R024160_004_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HGML_L5 | 0.66667 | 0.083333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDSM_S2 | 0.66667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SMTT_S2 | 0.66667 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R023272_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HGTR_L5 | 0.58333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HGTR_L60 | 0.58333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_DDMB_V2 | 0.58333 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R023384_013_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024462_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 0.5 | 2.5 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++CSGO_TG_R5 | 0.5 | 2.25 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | V::N_DDMB_V1 | 0.5 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_ROSM_SD | 0.5 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | #R022281_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R023062_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023272_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023384_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023422_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R023490_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024018_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R024164_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024233_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024462_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | T_ROCOF_3 | 0.41667 | 0.33333 | Out = NIL, limit non-synchronous generation and Basslink to prevent high Rate of Change of Frequency in TAS following fault and trip of generation during periods of low TAS inertia | NIL
T-V-MNSP1 Import | V::N_DDMB_SD | 0.41667 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_LTWG_SD | 0.41667 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_X_HWSM_ROSM_V1 | 0.41667 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R022385_028_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022394_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022417_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R022417_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R023062_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023324_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023325_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023406_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023406_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024164_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024241_005_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024547_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HGTR_L6 | 0.33333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_BEKG_S1 | 0.33333 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_DDWO_S1 | 0.33333 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_JNWO_S1 | 0.33333 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R022410_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R023397_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023422_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R023795_039_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023859_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024160_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R024483_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024491_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | V::N_BABE_V1 | 0.25 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_S1 | 0.25 | 0.083333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_V2 | 0.25 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
T-V-MNSP1 Import | #R022281_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R022367_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R022385_004_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022410_004_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
T-V-MNSP1 Import | #R023074_037_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 20/04/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023333_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023397_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023505_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023505_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023506_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023795_036_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023795_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024018_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
T-V-MNSP1 Import | #R024533_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HYMO_L6 | 0.16667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HORC_S1 | 0.16667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_HWCB_V1 | 0.16667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_JNWO_V1 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_KTSY_V1 | 0.16667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | #R022385_028_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V:T_HAGT_BL_1, Effective Date: 20/10/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022394_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint T::T_HA_GT_PM_4, Effective Date: 31/07/2014, Version: 1 | Other
T-V-MNSP1 Import | #R022454_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 09/03/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023104_036_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023324_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023326_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023333_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023490_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023505_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023505_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S2, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023605_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023795_036_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R023973_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024191_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024241_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024392_046_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024491_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | #R024502_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
T-V-MNSP1 Import | F_QNV++HYMO_L5 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++HYMO_L60 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_BLSPS_R5 | 0.083333 | 0 | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
T-V-MNSP1 Import | F_T++NIL_BLSPS_R60_2 | 0.083333 | 0 | Tasmania Raise 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_Q1 | 0.083333 | 0 | Out = SMTS 500kV bus, CB or SMTS bus bypass, prevent transient instability for fault and trip of HWTS-SMTS and SMTS-SYTS lines, QLD accelerates. Yallourn W1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_Q3 | 0.083333 | 0.16667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_EPMB_S1 | 0.083333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_MLSY_SD | 0.083333 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
T-V-MNSP1 Import | V::N_SMF2_S1 | 0.083333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_SMSY_V1 | 0.083333 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_SMTT_V2 | 0.083333 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>NIL_MHNW1_MHNW2 | 1629.1667 | 123.6667 | Out= Nil, avoid O/L Monash-North West Bend #2 132kV on trip of Monash-North West Bend #1 132kV line, Feedback | NIL
V-S-MNSP1 Export | V^^N_NIL_1 | 169.4167 | 494.8333 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
V-S-MNSP1 Export | V^SML_BUDP_3 | 88.4167 | 27.0833 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_ROC_80 | 81.8333 | 71.8333 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | V>>V_DDSM_1 | 69.3333 | 0 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 60.0833 | 14.25 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | V^^N_CNUT_1 | 59.0833 | 1 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V^^SML_NSWRB_2 | 58.3333 | 49.75 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines | NIL
V-S-MNSP1 Export | S>>RBTX_WEWT_RBTX | 54.4167 | 0 | Out= one Robertstown TX, avoid O/L of remaining Robertstown 132/275kV TX on trip of Waterloo East- Waterloo 132kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SMF2_V2 | 46.1667 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WEWT | 42.9167 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V^^N_HWSM_1 | 40 | 145.4167 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V::N_DDSM_V2 | 38.6667 | 10.9167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_MLTR_V2 | 30.1667 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 30.1667 | 35.4167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-S-MNSP1 Export | V^^N_UTYS_1 | 29.4167 | 65.5833 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
V-S-MNSP1 Export | V::N_HWSM_S1 | 29.0833 | 17.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-S-MNSP1 Export | V::N_NILxxx | 25.9167 | 25.8333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-S-MNSP1 Export | V::N_DDSM_V1 | 23.8333 | 0.16667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | VSML_ZERO | 20.9167 | 39.4167 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V::N_SMF2_S2 | 20.5 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WTTP | 20 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SMF2_V1 | 17.1667 | 4.0833 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>SMLMHNW1 | 15.9167 | 1.9167 | Out = Monash-North West Bend # 1 132kV line, limit Murraylink (Vic to SA) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Export | V::N_HWSM_V1 | 13.9167 | 23.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>X_RBPA+CB_03 | 12.4167 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage
V-S-MNSP1 Export | V::N_DDSM_S1 | 12.1667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>X_NWCB6225+6021_T1 | 11.5833 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225; limit Victoria to SA on Murraylink to avoid North West Bend transformer#1 O/L on trip NWB - MWP #1132kV line.(Note: swamped when ML Sever scheme is I/S) | Outage
V-S-MNSP1 Export | VSML_FLT_150 | 11.3333 | 0 | Vic to SA on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to voltage oscillation | Outage
V-S-MNSP1 Export | V::N_HWSM_V2 | 11.25 | 45.75 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_SD2 | 10.75 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V^SML_KGRC_4 | 10.1667 | 4.1667 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage
V-S-MNSP1 Export | V::N_KGRC_V1 | 9.25 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_SD1 | 8.5833 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V^SML_BEKG_4 | 8.3333 | 7 | Out = Bendigo to Kerang 220kV line, avoid voltage collapse for loss of Ballarat to Waubra to Ararat 220kV line | Outage
V-S-MNSP1 Export | V::N_MLMO_V2 | 7.0833 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SMLBAHO1 | 7 | 0 | Out = Bendigo to Kerang line, avoid O/L or voltage collapse on Balranald to Buronga (X3) line for trip of any 220kV line section between Ballarat and Horsham | Outage
V-S-MNSP1 Export | V>>N-MSUT_2 | 6.4167 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage
V-S-MNSP1 Export | VSML_080 | 5.6667 | 3.6667 | Vic to SA on ML upper transfer limit of 80 MW | Outage
V-S-MNSP1 Export | V::N_KGRC_S1 | 5.5833 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>NIL_BWMP_TWPA | 5.0833 | 0.66667 | Out= Nil, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V^SML_HORC_3 | 4.8333 | 0.83333 | Out = Horsham to Murra Warra to Red Cliffs 220kV line OR Murra Warra to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | S>>RBTX2_RBTX1_WEWT | 4.75 | 3.8333 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage
V-S-MNSP1 Export | V>>N-NIL_HH | 4.5833 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 4.1667 | 27.4167 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | V>>S_MWP3RB_NWRB1 | 4 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L North West Bend-Roberstown #1 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V1 | 3.75 | 0.083333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_MLTX_S1 | 3.75 | 0.33333 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 3.5833 | 0.16667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_BABE_S1 | 3.5833 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_LTWG_S1 | 3.5833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_MLTX_V1 | 3.4167 | 3.9167 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>X_PARB+RB_SBUS_10 | 3.3333 | 0 | Out= Robertstown South 275kV Bus(275kV CBs ONLY O/S with associated 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Para 275kV line O/S, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HWSM_SD | 3.1667 | 3.75 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | S>>X_RBPA+CB_02 | 3.0833 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage
V-S-MNSP1 Export | V::N_LTWG_V1 | 3.0833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | VSML_030 | 2.9167 | 0 | Vic to SA on ML upper transfer limit of 30 MW | Outage
V-S-MNSP1 Export | S>>NIL_TWPA_TPRS | 2.5 | 0.58333 | Out= NIL, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | V>>N-NIL_HG | 2.5 | 0.083333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | S>>PATW_BWPA_TPRS | 2.1667 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HYMO_S1 | 2.1667 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_DDWO_V1 | 2.0833 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 2 | 0.25 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_CNRB+CB_04 | 2 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 132/275kV TX2 on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V3 | 2 | 9.4167 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | S>>BRDV_RBTU_WEWT | 1.75 | 0 | Out= Brinkworth - Davenport 275kV line, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>PATW_RBTU_TPRS | 1.75 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>X_PARB+RB_SBUS_11 | 1.75 | 0 | Out= Robertstown South 275kV Bus(275kV CBs ONLY O/S with associated 132kV CBs assumed I/S) + Robertstown TX2 + Robertstown-Para 275kV line O/S, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HYSE_S1 | 1.5833 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N-LTMS_1 | 1.5833 | 0 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage
V-S-MNSP1 Export | VSML_105 | 1.5833 | 0 | Vic to SA on ML upper transfer limit of 105 MW | Outage
V-S-MNSP1 Export | VSML_160 | 1.5 | 0 | Vic to SA on ML upper transfer limit of 160 MW | Outage
V-S-MNSP1 Export | V::N_BEKG_V1 | 1.4167 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_S2 | 1.4167 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
V-S-MNSP1 Export | S>>X_RBPA+CB_04 | 1.3333 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Templers West-Para 275kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage
V-S-MNSP1 Export | V::N_ROSM_V2 | 1.3333 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | VSML_190 | 1.3333 | 0 | Vic to SA on ML upper transfer limit of 190 MW | Outage
V-S-MNSP1 Export | S>>BWMP_TWPA_TPRS | 1.1667 | 0.33333 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_BWMP_BRTW | 1.1667 | 3.1667 | Out= Nil, avoid O/L Brinkworth-Templers West 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>X_RBTU+CB_2 | 1.0833 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) | Outage
V-S-MNSP1 Export | S>RBMW4+TX_NIL_RBTX2 | 1.0833 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, avoid O/L of remaining Robertstown 132/275kV TX on Nil trip, Feedback | NIL
V-S-MNSP1 Export | V::N_DDMB_S1 | 1 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | NRM_VIC1_SA1 | 0.91667 | 0 | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | S>>BRTX3_BWMP_WTTP | 0.91667 | 0 | Out= Brinkworth 275/132kV TX3, avoid O/L Waterloo-Templers 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_TWPA_TPRS | 0.91667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HORC_V1 | 0.91667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_SMTT_S2 | 0.91667 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2B_R | 0.83333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-S-MNSP1 Export | V^^SML_ARWBBA_1 | 0.75 | 0 | Out = Ballarat to Waubra to Ararat 220kV line (or any line section between Ballarat and Ararat), avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | #R023074_058_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023324_010_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | S>>RBTU_RBPA_WTTP | 0.66667 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_DDMB_V2 | 0.66667 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HYSE_V1 | 0.66667 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_KTSY_V1 | 0.66667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R023272_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023325_022_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint VSML_FLT_150, Effective Date: 30/10/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023384_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023393_006_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
V-S-MNSP1 Export | S>>BWMP_RBTU_WTTP | 0.58333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BEKG_S1 | 0.58333 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_DDSM_S2 | 0.58333 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HYMO_V1 | 0.58333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R022518_009_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S>>X_RBPA+CB_03, Effective Date: 03/12/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022947_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S>>PATW_BWPA_TPRS, Effective Date: 10/05/2021, Version: 2 | Other
V-S-MNSP1 Export | #R024403_065_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | S>>X_RBTU+CB_1 | 0.5 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S , avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Para 275kV line (this offloads Robertstown TX#2 132/275kV ) lines, Feedback | Outage
V-S-MNSP1 Export | V::N_ROSM_S2 | 0.5 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_ROSM_SD | 0.5 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_X_HWSM_ROSM_V1 | 0.5 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R022148_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_UTYS_1, Effective Date: 13/11/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022281_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022417_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022767_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R022916_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R023062_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023062_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023130_065_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023261_020_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023272_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023320_020_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023324_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023384_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023420_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R023422_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023490_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023740_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>>PARB_RBTU_WEWT, Effective Date: 05/08/2021, Version: 2 | Other
V-S-MNSP1 Export | #R024018_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R024164_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024233_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024235_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R024462_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | V::N_EPMB_V1 | 0.41667 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | VSML_220 | 0.41667 | 55.0833 | Vic to SA on ML upper transfer limit of 220 MW | NIL
V-S-MNSP1 Export | #R022417_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023074_058_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023113_058_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023268_020_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023271_020_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023286_035_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023310_020_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023325_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023386_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023406_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023406_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023426_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>SMLMHNW1, Effective Date: 07/05/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023450_023_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 21/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023477_020_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023512_020_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023613_023_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 21/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024038_020_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R024266_019_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | #R024345_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21-08-2013, Version: 1 | Other
V-S-MNSP1 Export | #R024403_065_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | V::N_DDWO_S1 | 0.33333 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_JNWO_S1 | 0.33333 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R022281_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022410_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023257_021_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>N-MSUT_2, Effective Date: 31/03/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023333_023_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 21/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023397_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023397_020_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023422_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023426_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>SMLMHNW1, Effective Date: 07/05/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023506_020_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023613_023_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 21/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023740_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WEWT, Effective Date: 05/08/2021, Version: 2 | Other
V-S-MNSP1 Export | #R023795_036_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023840_035_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023859_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023895_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>X_PARB+RB_SBUS_10, Effective Date: 06/08/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023973_016_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 16/07/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024035_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>RBTX1_RBTX2_WTTP, Effective Date: 06/08/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024400_065_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024491_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024547_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | V::N_BABE_V1 | 0.25 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_DDMB_V1 | 0.25 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N-MSUT_4 | 0.25 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_4C | 0.25 | 0 | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL
V-S-MNSP1 Export | #R022148_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_UTYS_1, Effective Date: 13/11/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022157_035_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R022367_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022518_009_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>>X_RBPA+CB_03, Effective Date: 03/12/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022968_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 07/05/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023261_020_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R023326_016_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>SMLBAHO1, Effective Date: 04/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023333_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023397_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023470_016_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>SMLBAHO1, Effective Date: 04/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023477_020_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023505_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023505_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023506_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023599_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 20/07/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023742_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WEWT, Effective Date: 05/08/2021, Version: 2 | Other
V-S-MNSP1 Export | #R023795_036_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023795_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023795_039_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023973_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 16/07/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024018_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-S-MNSP1 Export | #R024148_029_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024258_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>BWMP_BRTW_WTTP, Effective Date: 05/08/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024483_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024533_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | S>>BWMP_RBTU_TWPA | 0.16667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers West-Para 275kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WTTP | 0.16667 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Robertstown - Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>RBMW4_TWPA_TPRS | 0.16667 | 0 | Out= Robertstown - MWP4 O/S, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_Q1 | 0.16667 | 0 | Out = SMTS 500kV bus, CB or SMTS bus bypass, prevent transient instability for fault and trip of HWTS-SMTS and SMTS-SYTS lines, QLD accelerates. Yallourn W1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-S-MNSP1 Export | V::N_BYPASS_HW_SY_V2 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HORC_S1 | 0.16667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_JNWO_V1 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>V_EPTT_2B_R | 0.16667 | 0 | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
V-S-MNSP1 Export | #R022157_035_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R022410_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022454_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 09/03/2021, Version: 1 | Other
V-S-MNSP1 Export | #R022518_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>X_RBPA+CB_02, Effective Date: 03/12/2020, Version: 1 | Other
V-S-MNSP1 Export | #R022679_035_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R022947_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S>>PATW_BWPA_TPRS, Effective Date: 10/05/2021, Version: 2 | Other
V-S-MNSP1 Export | #R022947_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>PATW_RBTU_TPRS, Effective Date: 10/05/2021, Version: 2 | Other
V-S-MNSP1 Export | #R022996_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>NWB6022_TX1, Effective Date: 12/05/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023074_037_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023104_036_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023104_058_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023218_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R023286_035_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R023320_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023325_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_SD, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023325_022_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VSML_FLT_150, Effective Date: 30/10/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023326_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023333_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023393_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023411_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_CNUT_1, Effective Date: 13/11/2020, Version: 1 | Other
V-S-MNSP1 Export | #R023434_023_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_BEKG_4, Effective Date: 21/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023464_016_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>SMLBAHO1, Effective Date: 04/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023490_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023505_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023505_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S2, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023505_016_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>SMLBAHO1, Effective Date: 04/02/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023605_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023740_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 05/08/2021, Version: 2 | Other
V-S-MNSP1 Export | #R023742_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>PARB_RBTU_WTTP, Effective Date: 05/08/2021, Version: 2 | Other
V-S-MNSP1 Export | #R023841_036_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R023973_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024038_020_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R024148_029_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 23/09/2019, Version: 1 | Other
V-S-MNSP1 Export | #R024191_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024241_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024266_019_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S>>RBTX_WEWT_RBTX, Effective Date: 27/10/2021, Version: 2 | Other
V-S-MNSP1 Export | #R024392_046_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | #R024392_046_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-S-MNSP1 Export | N>>N-NIL_DPTX | 0.083333 | 0.083333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL
V-S-MNSP1 Export | S>>NIL_BRTW_WTTP | 0.083333 | 0 | Out= Nil, avoid O/L Waterloo - Templers 132kV on trip of Brinkworth - Templers West 275kV line, Feedback | NIL
V-S-MNSP1 Export | S>>PARS_BWPA_TWPA | 0.083333 | 0 | Out= Roseworthy - Para 132kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_BWMP_TWPA | 0.083333 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Templers West-Para 275kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>RBTU_RBPA_WEWT | 0.083333 | 0 | Out= Robertstown-Tungkillo 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_HWCB_V1 | 0.083333 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_SMF2_S1 | 0.083333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_SMTT_V2 | 0.083333 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>N-LTUT_M_15M | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Lower Tumut to Canberra (07) trip; Feedback | Outage
V-S-MNSP1 Export | V>>N-LTYS_CH | 0.083333 | 0 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage
V-S-MNSP1 Import | SVML_ZERO | 853.8333 | 908.8333 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | N^^N_NIL_3 | 709.5 | 75.0833 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL
V-S-MNSP1 Import | N^^N_NIL_2 | 630.5833 | 141.4167 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL
V-S-MNSP1 Import | SVML^NIL_MH-CAP_ON | 282.4167 | 0 | Out=NIL, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash (Note: applies when capacitor banks at Monash are available and I/S for switching.) | NIL
V-S-MNSP1 Import | V^^V_NIL_KGTS | 153.1667 | 0 | Out= Nil, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | NIL
V-S-MNSP1 Import | V>>V_NIL_18 | 125.3333 | 28.9167 | Out= Nil, avoid O/L Ararat to Waubra 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | N^^V_CNCW_1 | 107.4167 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V^^V_MLNK_KGTS | 105.5833 | 0 | Out= Murraylink, avoid voltage collapse for loss of either Crowlands - Bulgana - Horsham or Horsham - Murra Warra - Kiamal 220kV line | Outage
V-S-MNSP1 Import | SVML_ROC_80 | 100.8333 | 71.9167 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | N^^V_NIL_1 | 100.4167 | 445.25 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
V-S-MNSP1 Import | V>>V_NIL_7 | 55.5 | 11.4167 | Out = Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Red Cliffs to Wemen to Kerang 220kV line (this trips off Bannerton and Wemen solar farms), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_9 | 40.25 | 114.3333 | Out= Nil, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | NIL
V-S-MNSP1 Import | SVML_FLT_125 | 34.9167 | 3.75 | SA to Vic on ML upper transfer limit of 125 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | V>>V_NIL_14 | 26.75 | 3.75 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | SVML_FLT_130 | 19.1667 | 0 | SA to Vic on ML upper transfer limit of 130 MW to manage system stability on the next contingency due to voltage oscillation issue | Outage
V-S-MNSP1 Import | SVML^NIL_160 | 17.6667 | 51.75 | Out=NIL, SA to Vic on ML upper transfer limit of 160 MW to manage voltage collapse at Monash | NIL
V-S-MNSP1 Import | V^^V_NIL_KGTS_2 | 15.8333 | 0 | Out= Nil, Limit post-contingency flow on Wemen to Kerang 220kV line to be less than 310 MVA for loss of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF) to avoid voltage collapse | NIL
V-S-MNSP1 Import | N::N_NIL_63 | 13 | 0 | Out=Nil , limit Darlington Point to Wagga line (63) line flow to avoid voltage collapse at Darlington Point 132kV post contingency trip of line 63, Feedback | NIL
V-S-MNSP1 Import | N^^V_CTMN_1 | 10.9167 | 0 | Out = Collector - Marulan (4) or Collector - Yass (3L) or Marulan - Yass (5), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>X_RBPA+CB_01 | 9.9167 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), | Outage
V-S-MNSP1 Import | SVML_FLT_150 | 9.25 | 4.4167 | SA to Vic on ML upper transfer limit of 150 MW to manage system stability on the next contingency due to fault level issue | Outage
V-S-MNSP1 Import | S>>V_MWP3RB_RBNW1 | 6.5833 | 0 | Out= Morgan Whyalla Pump3 - Robertstown 132kV line, avoid O/L Roberstown-North West Bend 132kV line on trip of Nil trip, Feedback | Outage
V-S-MNSP1 Import | S>VMLMHNW1 | 6.5833 | 22.0833 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-S-MNSP1 Import | N^^V_LTYS_1 | 6.3333 | 0 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S:VS_PA_SVC_570 | 6.3333 | 23.1667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-S-MNSP1 Import | S>X_RBPA+CB_06 | 6.25 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage
V-S-MNSP1 Import | SVML^MH-CAP_OFF | 6.25 | 0 | Out= One or both Capacitor banks (i.e. 61 or 62) at Monash O/S or not available for switching, SA to Vic on ML upper transfer limit to manage voltage collapse at Monash. | Outage
V-S-MNSP1 Import | N^^V_MSUT_1 | 5.4167 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | V>>V_NIL_23 | 5.4167 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | S>>V_NIL_NIL_RBNW1 | 5.3333 | 0.83333 | Out = Nil, avoid overloading Robertstown-North West Bend #1 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | S>RBMW4+TX_NIL_RBTX1 | 4.5833 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, avoid O/L of remaining Robertstown 275/132kV TX on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>>X_CNRB+CB_01 | 4.25 | 0 | Out= Out= Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S), avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Para 275kV line, Feedback | Outage
V-S-MNSP1 Import | N^^V_DPWG_X5_1 | 4.0833 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | N^^V_LTMS_1 | 3.6667 | 0 | Out = Murray to Lower Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>RBTX1_RBTX2_WEMWP4 | 3.6667 | 31.25 | Out= Robertstown 275/132kV TX1, avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2, | Outage
V-S-MNSP1 Import | S>RBTX2_RBTX1_WEMWP4 | 3.5 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage
V-S-MNSP1 Import | S>V_RBNW_RBMWP3 | 2.8333 | 0 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Robertstown-Morgan Pipeline 3 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Import | V>>V_NIL_24 | 2.8333 | 0 | Out= Nil, avoid O/L Wemen to Kerang 220kV line on trip of Horsham to Bulgana to Crowlands 220kV line (this trips Bulgana and Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | V>>V_NIL_13 | 2.75 | 0 | Out= Nil, avoid O/L Red Cliffs to Wemen 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback | NIL
V-S-MNSP1 Import | S>>V_NWRB2_RBNW1 | 2.3333 | 0 | Out = North West Bend-Robertstown 132kV No2 line, limit SA-V on ML to avoid O/L of Robertstown-NWB1 132kV line | Outage
V-S-MNSP1 Import | S>>X_RBTU+CB_7 | 2.3333 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, avoid O/L Robertstown 275/132kV #1 transformer on trip of Robertstown - Para line (this offloads Robertstown TX#2 132/275kV ) | Outage
V-S-MNSP1 Import | N>>N-NIL_DPTX_2 | 1.75 | 4.25 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
V-S-MNSP1 Import | S>>V_NIL_NIL_RBMW3 | 1.4167 | 3.25 | Out = Nil, avoid overloading Robertstown-Morgan Whyalla Pump 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | S:VS_PA_SVC_420 | 1 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage
V-S-MNSP1 Import | #R023661_001_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R023880_009_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N^^V_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
V-S-MNSP1 Import | S>RB_275KV_N_BUS_1 | 0.83333 | 12.5 | Out =Robertstown 275kV North Bus(i.e. RB 275/132kV TX1, RB 275kV CBs 6616 and 6573, and RB 132kV CBs 6005 and 6188 O/S), avoid O/L MWP4-Robertstown 132kV line on trip of Robertstown 275/132kV TX2 (this offloads NWB-RB #1 132kV line). | Outage
V-S-MNSP1 Import | #R023180_001_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | CA_BRIS_50B292E2_1 | 0.75 | 0 | Constraint Automation, O/L 64:LSM2:I:330@TUMUT3@NSW for CTG LXPD on trip of LOWER TUMUT-CANBERRA 07 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage
V-S-MNSP1 Import | #R022767_001_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R023272_009_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R023716_009_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
V-S-MNSP1 Import | SVML_080 | 0.66667 | 0.5 | SA to Vic on ML upper transfer limit of 80 MW | Outage
V-S-MNSP1 Import | #R023218_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R023420_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R024345_001_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21-08-2013, Version: 1 | Other
V-S-MNSP1 Import | S>>V_RBNW_MWP1NWB | 0.58333 | 0 | Out= Robertstown-North West Bend #1 132kV line, avoid O/L Morgan Whyalla Pipeline 1 - North West Bend 132kV line on Nil trip, Feedback | Outage
V-S-MNSP1 Import | N^^V_MSUT_KVCW_1 | 0.5 | 0 | Out = Murray to Upper Tumut(65) and Kangaroo Valley to Capital (3W) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 0.5 | 10.25 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>NWB6022_TX2 | 0.5 | 0 | Out= North West Bend CB 6022 O/S, avoid O/L North West Bend 275/132kV TX2 on trip of Robertstown-North West Bend #1 132kV line, Feedback | Outage
V-S-MNSP1 Import | SVML_050 | 0.5 | 0 | SA to Vic on ML upper transfer limit of 50 MW | Outage
V-S-MNSP1 Import | V>>V_BURC_5 | 0.5 | 0 | Out= Buronga to Redcliffs (0X1) 220kV line, avoid O/L Waubra to Ballarat 220kV line on trip of Kerang to Bendigo 220kV line, Feedback | Outage
V-S-MNSP1 Import | #R022939_026_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S>RB_275KV_N_BUS_1, Effective Date: 10/05/2021, Version: 2 | Other
V-S-MNSP1 Import | #R023218_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R023406_009_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R023505_008_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | I_CTRL_ISSUE_ML | 0.33333 | 0.5 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Import | #R022916_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R023048_023_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_CTMN_1, Effective Date: 11/05/2021, Version: 1 | Other
V-S-MNSP1 Import | #R023180_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R023841_035_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R023905_028_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>RBTX2_RBTX1_WEMWP4, Effective Date: 06/08/2021, Version: 1 | Other
V-S-MNSP1 Import | S>VMLMHNW2 | 0.25 | 0 | Out=Monash-North West Bend #2 132kV line, SA-V on ML avoid overload on North West Bend-Monash #1 132kV line, feedback | Outage
V-S-MNSP1 Import | #R022679_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DPWG_X5_1, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Import | #R022939_026_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>RB_275KV_N_BUS_1, Effective Date: 10/05/2021, Version: 2 | Other
V-S-MNSP1 Import | #R022956_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R022956_023_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_BURC_5, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Import | #R023048_023_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_CTMN_1, Effective Date: 11/05/2021, Version: 1 | Other
V-S-MNSP1 Import | #R023093_021_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 31/03/2021, Version: 1 | Other
V-S-MNSP1 Import | #R023490_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R023591_018_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R023795_035_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R023804_035_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | V>>V_NIL_3 | 0.16667 | 0.83333 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback. Swamp if SIPS available | NIL
V-S-MNSP1 Import | #R022695_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S:VS_XPAVC_460, Effective Date: 07/08/2018, Version: 1 | Other
V-S-MNSP1 Import | #R022956_023_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_BURC_5, Effective Date: 20/04/2021, Version: 1 | Other
V-S-MNSP1 Import | #R023324_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R023333_008_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SVML_FLT_150, Effective Date: 19/07/2019, Version: 1 | Other
V-S-MNSP1 Import | #R023697_023_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_CTMN_1, Effective Date: 11/05/2021, Version: 1 | Other
V-S-MNSP1 Import | #R023841_035_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_FLT_125, Effective Date: 14/10/2020, Version: 1 | Other
V-S-MNSP1 Import | #R024235_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | S>NIL_NWMH1_NWMH2 | 0.083333 | 0 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on trip of North West Bend-Monash #1 132kV line, Feedback | NIL
V-SA Export | V_S_NIL_ROCOF | 326.5833 | 11.25 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 2 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Export | V_S_HEYWOOD_UFLS | 110 | 7.6667 | Out= Nil, Limit Heywood flows when SA under frequency load shedding (UFLS) is insufficient (i.e. when UFLS blocks in SA <1000 MW) to manage for double-circuit loss of Heywood IC.Note: Constraint is swamped if UFLS blocks >= 1000 MW. | NIL
V-SA Export | V_VS_LB_CAN_50 | 96.75 | 3.8333 | Limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement when SA is at risk of separation. | Outage
V-SA Export | V_MLMO_VS_LB_CAN_50 | 94.1667 | 132.4167 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit Heywood + Lake Bonney WF + Canunda WF <= 50 MW for system strength requirement. Constraint swamp out if MOPS generating. | Outage
V-SA Export | V::N_SMF2_V2 | 48.25 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V:S_600_HY_TEST | 46.9167 | 17.5833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | V::N_NILxxx | 34.4167 | 36 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-SA Export | V::S_SETB_TBSE_2 | 30.5833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::N_MLTR_V2 | 27.25 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | S>>CGTB1_TBTU_TBMO | 21.1667 | 1.5 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::N_SMF2_S2 | 19.9167 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_SMF2_V1 | 19.75 | 4.0833 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 18.9167 | 14.5833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | V::N_HWSM_S1 | 18.3333 | 15.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 18.1667 | 2.0833 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_HWSM_V2 | 13.1667 | 50.5833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | F_ESTN++MLMO_L60 | 12.9167 | 36.3333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_HWSM_V1 | 12.8333 | 25.0833 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | VS_050_DYN | 11.25 | 0 | VIC to SA on Heywood upper transfer limit of 50 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | V::N_HWSM_SD | 11.1667 | 4.3333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | F_ESTN++MLMO_L6 | 9.6667 | 4 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | V::N_KGRC_V1 | 9.25 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | F_QNV++MLMO_L6 | 8.9167 | 6.5833 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V^^S_MLSY_2 | 8.75 | 0.33333 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | V::S_TBCP1_SETB_2 | 8.5 | 0 | Out= Tailem Bend 275kV Cap Bank (Note: with both Black Range series Caps O/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V::S_SETB_MAXG_2 | 8.1667 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with both Black Range series capacitors O/S). | Outage
V-SA Export | VS_250 | 7.8333 | 1.5 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage
V-SA Export | CA_BRIS_4F1FE461_1 | 6.75 | 0 | Constraint Automation, O/L MOBTAB_1:LMOB:Z:132@T_BEND@SA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage
V-SA Export | VS_250_DYN | 6.0833 | 12.8333 | VIC to SA on Heywood upper transfer limit of 250 MW,dynamic headroom, DS formulation only. | Outage
V-SA Export | F_ESTN++HYMO_L60 | 5.8333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V:S_PA_SVC_550 | 5.8333 | 0 | Out= one Para SVC (Note: with both Black Range series caps O/S), Oscillatory stability limit for VIC to SA on Heywood upper transfer limit of 550 MW | Outage
V-SA Export | V::N_MLMO_V2 | 5.75 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_KGRC_S1 | 5.6667 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | F_ESTN++HGML_L60 | 5.5833 | 0.41667 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_ESTN++MLMO_L5 | 5.0833 | 2.1667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | V::S_XPAVC_MAXG | 4.3333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA. | Outage
V-SA Export | V::N_MLSY_S1 | 4.0833 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_MLTX_V1 | 4.0833 | 9.8333 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V>S_460 | 4.0833 | 0 | VIC to SA on Heywood upper transfer limit of 460 MW | Outage
V-SA Export | V::N_BYPASS_HW_SY_V1 | 3.6667 | 0.16667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_MLTX_S1 | 3.6667 | 0.33333 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_BABE_S1 | 3.5833 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_MLSY_V1 | 3.5833 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_LTWG_S1 | 3.5 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_LTWG_V1 | 3.0833 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | S>>TBTU_TBCG_TBMO | 3 | 4.1667 | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V_S_ROCOF | 2.75 | 0 | Out = South Australia at credible risk of separation from NEM, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 1 Hz/sec in SA immediately following separation. | Outage
V-SA Export | S>>NIL_TBTU_TBMO_1 | 2.6667 | 0.16667 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL
V-SA Export | F_QNV++MLMO_L60 | 2.5833 | 3.3333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::S_RBPA_SETB | 2.3333 | 0 | Out= Robertstown- Para 275kV line (Note: with both Black Range Series Caps I/S); Vic to SA Transient Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V::N_DDWO_V1 | 2.1667 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | #V-SA_RAMP_E_F | 2.0833 | 0.5 | V-SA <= MAX(30, InitialFlow - 30) (Wt=35) | Other
V-SA Export | S_NIL_STRENGTH_2 | 2.0833 | 0 | Maximum limit (1870 MW + Vic to SA on Heywood) for South Australian non-synchronous generation for higher number synchronous generators online for system strength requirements | NIL
V-SA Export | V^^S_SETB_TBSE_2 | 2.0833 | 0 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::N_BYPASS_HW_SY_V3 | 2 | 9.3333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | F_QNV++MLMO_L5 | 1.8333 | 0.083333 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_EPMB_V1 | 1.75 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_BLKRG_MAXG_2 | 1.75 | 0 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | F_ESTN++HYMO_L6 | 1.5833 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | V::N_HYMO_S1 | 1.5833 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | F_ESTN++HGML_L5 | 1.5 | 0.16667 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | V::N_BEKG_V1 | 1.4167 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_BYPASS_HW_SY_S2 | 1.4167 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::S_XSEVC_MAXG | 1.4167 | 0 | Out= Both South East SVC1 & SVC 2 O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | F_ESTN++HGML_L6 | 1.3333 | 0.083333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | NRM_VIC1_SA1 | 1.3333 | 0 | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | V::S_RBTU_MAXG | 1.1667 | 0 | Out= Robertstown - Tungkillo 275kV line (NOTE: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V::N_BYPASS_HW_SY_S3 | 1.0833 | 11.5833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::N_DDMB_S1 | 1 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_HYSE_S1 | 1 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_ROSM_V2 | 1 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V>S_460_DYN | 1 | 0 | VIC to SA on Heywood upper transfer limit of 460 MW, dynamic headroom, DS formulation only. | Outage
V-SA Export | #R023775_013_RAMP_F | 0.91667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | V::N_HORC_V1 | 0.91667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_KTSY_V1 | 0.91667 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_SMTT_S2 | 0.91667 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_TBCB94_35_SETB | 0.91667 | 0 | Out= Tailem Bend 275kV CB6594 OR CB6596 O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V::N_EPMB_S1 | 0.83333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_ROSM_S2 | 0.83333 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_XPAVC_SETB | 0.83333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage
V-SA Export | F_ESTN++HGTR_L60 | 0.75 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V::N_DDMB_V2 | 0.75 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_BLKRG_TBSE_2 | 0.75 | 0 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | #R023324_010_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | V::N_HYSE_V1 | 0.66667 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_X_HWSM_ROSM_V1 | 0.66667 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | #R023272_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023384_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024353_022_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 15-06-2021, Version: 1 | Other
V-SA Export | F_ESTN++HYMO_L5 | 0.58333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V::N_BEKG_S1 | 0.58333 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_DDMB_SD | 0.58333 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | #R023715_016_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R024462_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | F_ESTN++HGTR_L6 | 0.5 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | F_QNV++HGML_L60 | 0.5 | 0.083333 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V::N_DDMB_V1 | 0.5 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_KHKN_MAXG | 0.5 | 1.5 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | VS_050 | 0.5 | 0.083333 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage
V-SA Export | #R022281_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R022417_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R023062_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
V-SA Export | #R023272_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023324_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023384_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023422_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R023621_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R023702_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R024018_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R024164_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024233_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024353_022_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 15-06-2021, Version: 1 | Other
V-SA Export | #R024374_022_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 15/06/2021, Version: 1 | Other
V-SA Export | #R024462_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024547_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | F_ESTN++HGTR_L5 | 0.41667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
V-SA Export | F_QNV+MLMO_L6 | 0.41667 | 0.41667 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+MLMO_L60 | 0.41667 | 0.75 | Out = Moorabool to Mortlake (MLTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_LTWG_SD | 0.41667 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_ROSM_SD | 0.41667 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | #R022417_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R023006_014_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 01/03/2021, Version: 4 | Other
V-SA Export | #R023062_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
V-SA Export | #R023281_017_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023281_017_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023325_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023406_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023490_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024241_005_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024243_005_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S>>TBTU_TBCG_TBMO, Effective Date: 27/01/2021, Version: 1 | Other
V-SA Export | #R024438_014_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R024533_013_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | F_QNV++HGTR_L60 | 0.33333 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+HYMO_L60 | 0.33333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_BYPASS_HW_SY_V2 | 0.33333 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
V-SA Export | V::N_DDWO_S1 | 0.33333 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_HYMO_V1 | 0.33333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_JNWO_S1 | 0.33333 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_NIL_TBSE_1 | 0.33333 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S).; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | #R022281_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R022410_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
V-SA Export | #R023006_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 01/03/2021, Version: 4 | Other
V-SA Export | #R023325_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_BEKG_SD, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023397_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023406_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023422_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R023571_017_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023714_016_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023795_039_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023859_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024164_003_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024483_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024491_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | F_QNV+HYMO_L6 | 0.25 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_BABE_V1 | 0.25 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_BYPASS_HW_SY_Q1 | 0.25 | 0 | Out = SMTS 500kV bus, CB or SMTS bus bypass, prevent transient instability for fault and trip of HWTS-SMTS and SMTS-SYTS lines, QLD accelerates. Yallourn W1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
V-SA Export | V::N_BYPASS_HW_SY_S1 | 0.25 | 0.083333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
V-SA Export | V::S_KHKN_MAXG_2 | 0.25 | 0 | Out= Keith - Kincraig 132 kV line(Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | #R022454_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V_VS_MLMO_NETT, Effective Date: 14/02/2020, Version: 1 | Other
V-SA Export | #R022626_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023074_037_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 20/04/2021, Version: 1 | Other
V-SA Export | #R023277_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R023333_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023397_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023505_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023505_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023506_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023542_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^S_XPAVC_SETB, Effective Date: 01/03/2021, Version: 1 | Other
V-SA Export | #R023637_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R023713_016_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023795_036_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023795_036_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023795_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024018_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
V-SA Export | #R024243_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S>>TBTU_TBCG_TBMO, Effective Date: 27/01/2021, Version: 1 | Other
V-SA Export | #R024324_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::S_KHKN_MAXG_2, Effective Date: 01/03/2021, Version: 1 | Other
V-SA Export | #R024367_022_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 15/06/2021, Version: 1 | Other
V-SA Export | #R024436_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R024438_014_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R024462_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R024491_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024521_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R024533_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | F_QNV++HGML_L5 | 0.16667 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++HGML_L6 | 0.16667 | 0.25 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++HGTR_L5 | 0.16667 | 0 | Out = Haunted Gully to Tarrone (HGTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++HYMO_L60 | 0.16667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+HGML_L60 | 0.16667 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | F_QNV+HYMO_L5 | 0.16667 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_HORC_S1 | 0.16667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_HWCB_V1 | 0.16667 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_JNWO_V1 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_2SE+PAVC_MAXG | 0.16667 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V::S_NIL_SETB_SECP_1 | 0.16667 | 0 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | V_VS_MLMO_NETT | 0.16667 | 0.66667 | Out = Moorabool to Mortlake 500 kV line, TRTS 500kV centre CB fail timer set to zero, No.2 HYTS line CB at APD OPEN, limit post-contingent nett loss into SA to be < 150 MW | Outage
V-SA Export | #R022626_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023104_039_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023146_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint VS_050, Effective Date: 08/01/2014, Version: 1 | Other
V-SA Export | #R023320_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023326_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023333_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023405_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SMSY_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023490_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023490_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023505_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023505_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S2, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023571_017_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023605_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R023706_016_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023714_016_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V_VS_LB_CAN_50, Effective Date: 17/08/2020, Version: 1 | Other
V-SA Export | #R023841_036_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024191_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024241_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024392_046_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024392_046_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024474_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R024491_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024502_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024502_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Export | #R024502_013_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^S_MLSY_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | CA_BRIS_4F1FDF04_1 | 0.083333 | 0 | Constraint Automation, O/L XFMR T_4@T_BEND@SA for CTG LSIM on trip of TUNKIL - T_BEND #1 275KV LINE. Generated by STNET[BNECR2] Host BNEREGEEMP2(EMPBRI) | Outage
V-SA Export | F_ESTN++HYTR_L5 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | F_ESTN++HYTR_L6 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | F_ESTN++HYTR_L60 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | F_QNV++HYMO_L5 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV++HYMO_L6 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | F_QNV+HGML_L5 | 0.083333 | 0 | Out = Haunted Gully to Moorabool (HGTS-MLTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_BYPASS_HW_SY_Q3 | 0.083333 | 0.16667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::N_MLSY_SD | 0.083333 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
V-SA Export | V::N_SMSY_V1 | 0.083333 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_SMTT_V2 | 0.083333 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_NIL_MG_TB_2-DS | 0.083333 | 0 | Out =Nil(Note: with both Black Range series capacitors O/S); Vic-SA Tran. Stab limit for loss of SA largest generator with loss of Torrens Island B PS declared as credible (South East Capacitor Available). (NOTE: DS RHS ONLY) | NIL
V-SA Export | V^^S_PAVC1_MAXG | 0.083333 | 0.33333 | Out= Para one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V^^S_PAVC_MAXG | 0.083333 | 0 | Out= Para one SVC (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V^^S_XPAVC_MAXG | 0.083333 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V_V_HYMO_1 | 0.083333 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line, Limit voltage unbalance at the APD 500 kV bus and Heywood 275 kV bus | Outage
V-SA Import | SV_420_DYN | 188.4167 | 70.8333 | SA to Victoria on Heywood upper transfer limit of 420 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Import | S:V_PA_SVC_420 | 175.6667 | 363.5 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | F_S++HYSE_L60 | 104.25 | 24.3333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
V-SA Import | F_S+MLMO_TL_L60 | 56.9167 | 157.25 | Out= Moorabool to Mortlake 500kV line, SA Lower 60 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines | Outage
V-SA Import | V::N_DDSM_V1 | 55.0833 | 0.16667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Import | V::N_DDSM_V2 | 55 | 10.9167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | S:V_XPAVC_310 | 54.8333 | 26.5 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S), SA to VIC on Heywood upper transfer limit of 310 MW based on oscillatory stability. | Outage
V-SA Import | S:V_PA_SVC_270 | 45.0833 | 1.5 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW | Outage
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 31.0833 | 36.9167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-SA Import | S:V_550_HY_TEST | 29.1667 | 33.0833 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | F_S++HYSE_L6_1 | 17.6667 | 2.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | S:V_550_HY_TEST_DYN | 13.8333 | 19 | SA to VIC on Heywood upper transfer limit of 550 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | S::V_TBSE_TBSE_2 | 11.9167 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | F_S+MLMO_TL_L6_1 | 11.4167 | 2.0833 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 1 | Outage
V-SA Import | #V-SA_RAMP_I_F | 4.1667 | 2.0833 | V-SA >= MIN(-78, InitialFlow + 50) (Wt=35) | Other
V-SA Import | S:V_XPAVC_230 | 3.0833 | 0 | Out = Para SVC 1 and 2 (Note: with both or one Black Range series caps O/S), SA to VIC on Heywood upper transfer limit of 230 MW based on oscillatory stability. | Outage
V-SA Import | S:VS_PA_SVC_570 | 3 | 5.6667 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-SA Import | S>>CGTB1_TUTB_MOTB | 2.8333 | 9.6667 | Out= Cherry Gardens - Tailem Bend 275kV line, avoid O/L Mobilong - Tailem Bend 132kV on trip of Tungkillo - Tailem Bend 275kV line, Feedback | Outage
V-SA Import | F_S++HYSE_L6_2 | 2.5833 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment2 | Outage
V-SA Import | S>>NIL_CGTB_TUTB_1 | 1.5 | 0.41667 | Out= Nil, avoid O/L Tungkillo - Tailem Bend 275kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | NIL
V-SA Import | S:VS_PA_SVC_420 | 1.3333 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 420 MW | Outage
V-SA Import | F_S+MLMO_TL_L6_2 | 1.0833 | 7 | Out= Moorabool to Mortlake 500kV line, SA Lower 6 sec requirement for loss of Heywood to Tarrone to Haunted Gully to Moorabool 500kV lines, segment 2 | Outage
V-SA Import | #R024339_002_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | S_V_NIL_ROCOF | 0.83333 | 0 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Import | V>>V_KTS_TX_A2_2B_R | 0.83333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-SA Import | #R022695_002_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023393_006_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
V-SA Import | #R023503_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024007_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023493_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023816_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024225_003_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_420, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | V>>V_KTS_TX_A3_2B_R | 0.5 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-SA Import | #R023901_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023386_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
V-SA Import | #R023901_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024124_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R023493_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023599_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 20/07/2021, Version: 1 | Other
V-SA Import | #R023739_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024007_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | F_S++HYSE_L5 | 0.25 | 2.0833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
V-SA Import | #R023157_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R023671_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024124_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R024339_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | SV_100_DYN | 0.16667 | 0 | SA to Victoria on Heywood upper transfer limit of 100 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Import | V>>V_EPTT_2B_R | 0.16667 | 0 | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
V-SA Import | #R023141_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R023393_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
V-SA Import | #R023503_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023816_002_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint S:V_PA_SVC_270, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R023856_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R023856_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint SV_250, Effective Date: 21/08/2013, Version: 1 | Other
V-SA Import | #R023973_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
V-SA Import | #R024248_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S:V_XPAVC_310, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | #R024300_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | #R024309_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S_V_ROCOF, Effective Date: 12/10/2016, Version: 1 | Other
V-SA Import | S:V_PA_SVC_270-DS | 0.083333 | 0 | Out= one Para SVC (Note: with both or one Black Range series caps O/S), Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 270 MW (NOTE:DS RHS ONLY) | Outage
VIC1-NSW1 Export | N^^N_NIL_3 | 1117.5 | 86.1667 | Out= Nil, limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria | NIL
VIC1-NSW1 Export | V^^N_NIL_1 | 826.5 | 566 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
VIC1-NSW1 Export | V^^N_MSUT_1 | 178.6667 | 0 | Out = Murray to Upper Tumut (65), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V^^N_LTYS_1 | 95.5 | 0 | Out = Lower Tumut - Yass (3) 330kV line , avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V^^N_CNCW_1 | 91.9167 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>V_DDSM_1 | 86.6667 | 0 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
VIC1-NSW1 Export | V>>N-NIL_HA | 83.3333 | 15.6667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | V^^N_DPWG_X5_1 | 66.75 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V^^N_CNUT_1 | 59.8333 | 1 | Out = Canberra to Upper Tumut (01) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V^^N_HWSM_1 | 57.5833 | 144.3333 | Out = Hazelwood to South Morang 500kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_DDSM_V1 | 52.5833 | 0.16667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_V2 | 49.6667 | 10.9167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_V2 | 45 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLTR_V2 | 43.1667 | 0 | Out = Moorabool to Tarrone 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_NILxxx | 41.6667 | 31.0833 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
VIC1-NSW1 Export | V::N_HWSM_S1 | 35.0833 | 17.9167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates | Outage
VIC1-NSW1 Export | N::N_LTYS_2 | 33.1667 | 0 | Out = Lower Tumut -Yass(3), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V>>N-X_MSUT_99P_1 | 32.1667 | 0 | Out= Murray to Upper Tumut(65) and either 993 or 99P,avoid Murray to Lower Tumut(66) O/L on trip of Wagga to Lower Tumut(051) and With subsequent operation of Wagga-Yass trip scheme that will open Yass?Wagga parallel(Trip 990+991),Feedback.OM607 and OM527 | Outage
VIC1-NSW1 Export | N::N_SDUT_2 | 30.5 | 0 | Out = Upper Tumut -Stockdill(1), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V^^N_UTYS_1 | 30.4167 | 76.6667 | Out = Upper Tumut to Yass (2) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 27.6667 | 36.1667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
VIC1-NSW1 Export | V^^N_SDUT_1 | 27.5833 | 0 | Out = Stockdill to Upper Tumut (1) line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_SMF2_S2 | 20.3333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-MSUT_1 | 18.25 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Wagga to Lower Tumut(051) trip; Feedback | Outage
VIC1-NSW1 Export | N::N_CNCW_2 | 16.75 | 0 | Out= Canberra-Capital (6) line Or Capital-Kangaroo Valley (3W) line, stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage
VIC1-NSW1 Export | V::N_SMF2_V1 | 16.6667 | 4.0833 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HWSM_V1 | 14.8333 | 25.3333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_S1 | 14.0833 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-DDWO_RADIAL_2 | 13.8333 | 0 | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | V^^N_MNYS_1 | 13.0833 | 20.25 | Out = Marulan to Yass (4 or 5) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_HWSM_V2 | 12.5833 | 46.6667 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_SD2 | 11.3333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 500kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_HWSM_SD | 11.0833 | 3.9167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_MLMO_V2 | 10.8333 | 0 | Out = Moorabool to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SMF2_SD1 | 8.9167 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates, YPS G1 on 220kV. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V^^N_BADP_1 | 7.8333 | 0 | Out = Balranald to Darlington Point (X5) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>N-MSUT_2 | 7 | 0 | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Export | V^^N_DTMN_1 | 5.1667 | 0 | Out = Dapto-Marulan(8) 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V>>N-NIL_HH | 5.0833 | 0 | Out = Nil, avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V>>N-JNWO_RADIAL_2 | 4.9167 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage
VIC1-NSW1 Export | V::N_MLSY_S1 | 4.75 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_KGRC_V1 | 4.5833 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_KGRC_S1 | 4.5 | 0 | Out = Kerang to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | #VIC1-NSW1_E_E | 4.4167 | 0 | VIC1-NSW1. * 1 <= 700 (Wt = 35) | Other
VIC1-NSW1 Export | V::N_MLTX_V1 | 4.0833 | 9.6667 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_MLTX_S1 | 3.75 | 0.33333 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HG | 3.75 | 0.083333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V1 | 3.6667 | 0.16667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V^^N_BURC_1 | 3.5833 | 0 | Out = Buronga to Red Cliffs (0X1) 220kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | V::N_BABE_S1 | 3.5 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_MLSY_V1 | 3.5 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HYMO_S1 | 3.3333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | CA_BRIS_50737673_1 | 3 | 0 | Constraint Automation, O/L 66:LSM3:Z:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORVM2] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Export | V::N_LTWG_S1 | 3 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | N::N_UTRV_2 | 2.9167 | 0 | Out = Upper Tumut -Ravine (6X), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | N>>N-NIL_998 | 2.5 | 0 | Out= Nil, avoid O/L Cowra to Forbes (998) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | V::N_LTWG_V1 | 2.5 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | N>>N-NIL__H_15M | 2.4167 | 0.083333 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL
VIC1-NSW1 Export | V::N_HYSE_S1 | 2.3333 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | N>>N-NIL_67 | 1.9167 | 0 | Out= Nil, avoid O/L Collector to Marulan (4) on trip of Nil, Feedback | NIL
VIC1-NSW1 Export | N>>N-NIL_DPTX_2 | 1.75 | 3.4167 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 220kV to 330kV flow on Transformer | NIL
VIC1-NSW1 Export | V::N_EPMB_V1 | 1.6667 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S2 | 1.5833 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 500kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_DDWO_V1 | 1.5833 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_ROSM_V2 | 1.5833 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-LTMS_1 | 1.5833 | 0 | Out= Lower Tumut-Murray(66), avoid Murray to Upper Tumut (65) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-JNWO_RADIAL_1 | 1.5 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Upper Tumut (65) using 15 mins rating on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | N::N_BYCR_2 | 1.4167 | 0 | Out = Bannaby to Crookwell (61), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage
VIC1-NSW1 Export | CA_BRIS_50B292E2_1 | 1.3333 | 0 | Constraint Automation, O/L 64:LSM2:I:330@TUMUT3@NSW for CTG LXPD on trip of LOWER TUMUT-CANBERRA 07 330KV LINE. Generated by STNET[NORCR1] Host BNEREGEEMP2(EMPBRI) | Outage
VIC1-NSW1 Export | N::N_CNSD_2 | 1.3333 | 0.5 | Out = Canberra - Stockdill (3C), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V3 | 1.3333 | 9.9167 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | N::N_CTYS_2 | 1.1667 | 0 | Out= Collector -Yass (3L), stability limit (Snowy-NSW) for loss of Yass-Marulan (5) or Gullen Range to Bannaby (61) 330kV line 330kV line | Outage
VIC1-NSW1 Export | V::N_BEKG_V1 | 1.0833 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HYSE_V1 | 1.0833 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 1 | 0 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | V::N_DDMB_S1 | 0.91667 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_ROSM_S2 | 0.91667 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V^^N_UTRV_1 | 0.91667 | 0 | Out = Upper Tumut -Ravine (6X) or Ravine to Yass (2), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | #R023805_036_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S3 | 0.83333 | 10.5833 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink VIC->TAS. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_EPMB_S1 | 0.83333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HYMO_V1 | 0.83333 | 0 | Out = Heywood to Mortlake 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 0.75 | 0.083333 | Negative Residue Management constraint for VIC to NSW flow | NIL
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2B_R | 0.75 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
VIC1-NSW1 Export | #R023324_010_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023393_006_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024000_024_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V^^N_MSUT_1, Effective Date: 03/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024462_002_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | V::N_DDMB_V2 | 0.66667 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_DDSM_S2 | 0.66667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_X_HWSM_ROSM_V1 | 0.66667 | 0 | Out=Hazelwood-South Morang & Rowville-South Morang 500kV lines, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-LTWG_RADIAL_1 | 0.66667 | 0 | Out = Lower Tumut to Wagga(051), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | #R023075_036_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023272_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023384_013_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | CA_BRIS_507E31FE_1 | 0.58333 | 0 | Constraint Automation, O/L 66:LSM3:Z:330@MURRAY@VIC for CTG LXPE on trip of LOWER TUMUT-WAGGA 051 330KV LINE. Generated by STNET[NORCR4] Host BNEREGEEMP1(EMPBRI) | Outage
VIC1-NSW1 Export | V::N_SMTT_S2 | 0.58333 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | #R024554_009_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | V::N_BEKG_S1 | 0.5 | 0 | Out = Bendigo to Kerang 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_DDMB_SD | 0.5 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_HORC_V1 | 0.5 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_ROSM_SD | 0.5 | 0 | Out = Rowville to South Morang 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | #R022148_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_UTYS_1, Effective Date: 13/11/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022327_023_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_MNYS_1, Effective Date: 17/02/2021, Version: 1 | Other
VIC1-NSW1 Export | #R022417_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022763_011_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V^^N_CNLT_1, Effective Date: 03/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023062_004_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023062_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 20/04/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023272_013_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023422_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R023490_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023840_036_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024000_024_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V^^N_MSUT_1, Effective Date: 03/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024018_009_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R024164_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024233_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SMF2_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024462_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024547_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_KTSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | V>>V_KTS_TX_A3_2B_R | 0.41667 | 0 | Out = Keilor A3 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
VIC1-NSW1 Export | #R022281_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022417_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_ROSM_V2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R023105_036_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023324_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023325_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023354_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N::N_SDUT_2, Effective Date: 06/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023384_013_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023386_006_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V_EPTT_2B_R, Effective Date: 12/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023406_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023406_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024084_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024164_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_DDMB_SD, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024241_005_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024561_009_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024561_009_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | N::N_UTYS_2 | 0.33333 | 7.4167 | Out = Upper Tumut -Yass(2), stability limit (Snowy-NSW) for fault at various location between Yass and South Morang area | Outage
VIC1-NSW1 Export | N>>N-NIL_64 | 0.33333 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Dapto to Sydney South (11) line, Feedback | NIL
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_Q1 | 0.33333 | 0 | Out = SMTS 500kV bus, CB or SMTS bus bypass, prevent transient instability for fault and trip of HWTS-SMTS and SMTS-SYTS lines, QLD accelerates. Yallourn W1 on 220 kV. Constraint active for QNI flows above 900 MW southwards only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_DDMB_V1 | 0.33333 | 0 | Out = Dederang to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_KTSY_V1 | 0.33333 | 0 | Out = Keilor to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_LTWG_SD | 0.33333 | 0 | Out = Lower Tumut to Wagga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V^^N_LTMS_1 | 0.33333 | 0 | Out = Murray to Lower Tumut 330kV line, avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | #R022281_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SMTT_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022410_004_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022410_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_ROSM_S2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R023257_021_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>N-MSUT_2, Effective Date: 31/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023286_036_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023325_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_BEKG_SD, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023354_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N::N_SDUT_2, Effective Date: 06/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023397_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023422_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R023599_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2B_R, Effective Date: 20/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023973_016_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 16/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024084_009_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^^N_SDUT_1, Effective Date: 11/10/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024390_036_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024390_036_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024483_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024491_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024491_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL__A_15M | 0.25 | 0 | Out= Nil, avoid O/L Lower Tumut to Canberra (07) using 15 mins rating on trip of Upper Tumut to Stockdill (1) line, Feedback | NIL
VIC1-NSW1 Export | V>>N-MSUT_4 | 0.25 | 0 | Out= Murray-UpperTumut(65), avoid Murray to LowerTumut (66) O/L on Dederang-Wodonga(DDWO) trip; Feedback | Outage
VIC1-NSW1 Export | V^^N_CNYS_1 | 0.25 | 0 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Export | #R022148_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_UTYS_1, Effective Date: 13/11/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022327_023_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_MNYS_1, Effective Date: 17/02/2021, Version: 1 | Other
VIC1-NSW1 Export | #R022367_006_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTR_V2, Effective Date: 21/02/2020, Version: 1 | Other
VIC1-NSW1 Export | #R022968_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 07/05/2021, Version: 1 | Other
VIC1-NSW1 Export | #R022981_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N::N_CNCW_2, Effective Date: 30/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R022989_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N::N_CTYS_2, Effective Date: 30/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023074_037_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S2, Effective Date: 20/04/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023075_036_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023333_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023397_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023505_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023505_012_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BEKG_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023506_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023795_036_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023795_036_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023795_039_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023796_036_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023805_036_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023840_036_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023859_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_X_ARWBBA_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023973_016_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 16/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024018_009_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BYPASS_HW_SY_V1, Effective Date: 07/04/2017, Version: 1 | Other
VIC1-NSW1 Export | #R024047_037_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^^N_MSUT_1, Effective Date: 03/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024533_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_65 | 0.16667 | 0 | Out= Nil, avoid O/L Bannaby to Sydney West (39) on trip of Avon to Macarthur (17) line, Feedback | NIL
VIC1-NSW1 Export | V::N_BABE_V1 | 0.16667 | 0 | Out = Ballarat to Bendigo 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_S1 | 0.16667 | 0.083333 | Out=Three SMTS 500kV CBs for HWTS & SYTS line(#1 or #2), bypass for HWTS to SYTS direct line, avoid trans. instability for trip of a HWTS-SYTS or HWTS-SMTS 500kV line, SA accelerates, Basslink TAS->VIC. YPS #1 on 220kV. Only applied during Heywood SA->VIC | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_V2 | 0.16667 | 0 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_DDWO_S1 | 0.16667 | 0 | Out = Dederang - Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HORC_S1 | 0.16667 | 0 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_JNWO_V1 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N-LTYS_CH | 0.16667 | 0 | Out = Lower Tumut to Yass(3), avoid O/L Murray to Upper Tumut (65) on trip of Murray to Lower Tumut (66) line, Feedback | Outage
VIC1-NSW1 Export | V>>V_EPTT_2B_R | 0.16667 | 0 | Out = Eildon to Thomastown 220kV line, avoid pre-contingent O/L the South Morang 500/330kV (F2) transformer, Yallourn unit 1 in 220kV mode, radial mode, feedback | Outage
VIC1-NSW1 Export | #R022320_023_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_MNYS_1, Effective Date: 17/02/2021, Version: 1 | Other
VIC1-NSW1 Export | #R022454_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLMO_V2, Effective Date: 09/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R022763_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_CNLT_1, Effective Date: 03/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023104_036_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023105_036_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023116_036_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_DPWG_X5_1, Effective Date: 15/03/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023320_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023325_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023326_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023333_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023334_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N::N_CNCW_2, Effective Date: 06/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023411_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_CNUT_1, Effective Date: 13/11/2020, Version: 1 | Other
VIC1-NSW1 Export | #R023490_009_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023505_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023505_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_BEKG_S2, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023605_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_KGRC_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023795_039_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_JNWO_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023853_020_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^N_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Export | #R023973_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024191_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_DDMB_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024241_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024502_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_S1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | #R024502_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLSY_V1, Effective Date: 11/06/2021, Version: 1 | Other
VIC1-NSW1 Export | N>>N-NIL_61 | 0.083333 | 0 | Out= Nil, avoid O/L Crookwell to Bannaby (61) using 15 mins rating on trip of Yass to Marulan (5) line, Feedback | NIL
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_Q3 | 0.083333 | 0.16667 | Out=Three SMTS 500kV CBs for HWTS & SYTS line (#1 or #2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, QLD accelerates, Basslink VIC to TAS, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_HWCB_V1 | 0.083333 | 0 | Out = Hazelwood to Cranbourne No.4 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_JNWO_S1 | 0.083333 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_MLSY_SD | 0.083333 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA decelerates. Constraint active for SA flows above 500 MW VIC to SA only, swamped otherwise. | Outage
VIC1-NSW1 Export | V::N_SMF2_S1 | 0.083333 | 0 | Out = South Morang F2 500/330kV txfmr, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_SMSY_V1 | 0.083333 | 0 | Out = South Morang to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_SMTT_V2 | 0.083333 | 0 | Out = South Morang to Thomastown 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-DDWO_RADIAL_1 | 0.083333 | 0 | Out = Dederang to Wodonga, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-LTUT_M_15M | 0.083333 | 0 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Lower Tumut to Canberra (07) trip; Feedback | Outage
VIC1-NSW1 Export | V^^N_CNLT_1 | 0.083333 | 0 | Out = Canberra to Lower Tumut(07), avoid voltage collapse around Murray for loss of all APD potlines | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 114.8333 | 534.75 | Out = Nil, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | NIL
VIC1-NSW1 Import | N^^V_CNCW_1 | 113.3333 | 19.1667 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DDSM1 | 72.4167 | 74 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 23.75 | 22 | Negative Residue Management constraint for NSW to VIC flow | NIL
VIC1-NSW1 Import | N^^V_NIL_ARWBBA | 21.6667 | 38.9167 | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | NIL
VIC1-NSW1 Import | N^^V_CTMN_1 | 14.3333 | 0 | Out = Collector - Marulan (4) or Collector - Yass (3L) or Marulan - Yass (5), avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_LTYS_1 | 9.3333 | 0 | Out = Lower Tumut - Yass(3), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N>>V_SMDD6 | 5.6667 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H3 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
VIC1-NSW1 Import | N^^V_MSUT_1 | 5.4167 | 0 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_DPWG_X5_1 | 4.0833 | 0 | Out = DarlingtonPt to Wagga(63) and Darlington Point to Balranald (X5) off loaded, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_LTMS_1 | 3.6667 | 0 | Out = Murray to Lower Tumut 330 kV line, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_LTWG_1 | 3.6667 | 0 | Out = Lower Tumut to Wagga 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_GRYS_1 | 3.5833 | 0 | Out = Gullen Range to Yass (3J), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V-LTWG_RADIAL_1 | 1.9167 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.2 330kV line for loss of the parallel No.1 line, 15 min ratings; Feedback. Swamp if VBB/SIPS available | Outage
VIC1-NSW1 Import | N:V_WA_BUSA_BWRG | 1.5 | 0 | Out= Wagga 330kV A Bus, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage
VIC1-NSW1 Import | N^^V_BUDP_1 | 1.3333 | 15.5 | Out = Buronga to Balranald (X3) or Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N::V_DDSM_MSDD | 0.91667 | 0 | Out= Dederang to South Morang line, NSW to Victoria Transient stability limit for the trip of Murray - Dederang (67 or 68) line | Outage
VIC1-NSW1 Import | N::V_MSUT | 0.91667 | 0 | Out= Murray to Upper Tumut (65) line, NSW to Victoria Transient stability limit. | Outage
VIC1-NSW1 Import | #R023880_009_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N^^V_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Import | N^^V_SMTXF2_1 | 0.83333 | 4.1667 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | #R022680_013_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_LTWG_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R023716_009_RAMP_F | 0.66667 | 0 | Hard Ramping constraint for constraint N^^V_LTMS_1, Effective Date: 29/07/2021, Version: 1 | Other
VIC1-NSW1 Import | #R023205_011_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R022157_011_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | N>>V-NIL_0X1 | 0.5 | 0.083333 | Out= NIL, avoid O/L Buronga to Redcliff (OX1) on Nil trip, Feedback | NIL
VIC1-NSW1 Import | N^^V_MSUT_KVCW_1 | 0.5 | 0 | Out = Murray to Upper Tumut(65) and Kangaroo Valley to Capital (3W) 330kV lines, avoid voltage collapse at Southern NSW for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | #R023995_003_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | V::V_1900 | 0.33333 | 1 | Out=Nil, upper limit into Vic of 1900 MW | NIL
VIC1-NSW1 Import | V>>V_NIL_3 | 0.33333 | 0.83333 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback. Swamp if SIPS available | NIL
VIC1-NSW1 Import | #R023048_023_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_CTMN_1, Effective Date: 11/05/2021, Version: 1 | Other
VIC1-NSW1 Import | #R023205_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R024403_028_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_BUDP_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R024509_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 18/03/2021, Version: 1 | Other
VIC1-NSW1 Import | V>>V_NIL_4C | 0.25 | 0 | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL
VIC1-NSW1 Import | #R022679_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DPWG_X5_1, Effective Date: 20/04/2021, Version: 1 | Other
VIC1-NSW1 Import | #R022680_013_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_LTWG_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R022789_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R023048_023_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_CTMN_1, Effective Date: 11/05/2021, Version: 1 | Other
VIC1-NSW1 Import | #R023093_021_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 31/03/2021, Version: 1 | Other
VIC1-NSW1 Import | #R024152_013_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N^^V_LTWG_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | N>>V_SMDD5 | 0.16667 | 0 | Out = Dederang to South Morang 330 kV line, avoid O/L the DDTS H2 330/220 kV txfmr on trip of the remaining Dederang to South Morang 330 kV line, feedback | Outage
VIC1-NSW1 Import | V>>V-LTWG_RADIAL_2 | 0.16667 | 0 | Outage = Lower Tumut to Wagga 330kV line, avoid overload Murray to Dederang No.1 330kV line for loss of the parallel No.2 line, 15 min ratings; Feedback. Swamp if VBB/SIPS available | Outage
VIC1-NSW1 Import | #R022487_021_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 06/11/2019, Version: 1 | Other
VIC1-NSW1 Import | #R023697_023_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_CTMN_1, Effective Date: 11/05/2021, Version: 1 | Other
VIC1-NSW1 Import | #R024509_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 18/03/2021, Version: 1 | Other
VIC1-NSW1 Import | N::V_MSUT_CNYS_1 | 0.083333 | 0 | Out= Murray to Upper Tumut (65) and Canberra - Yass (9) 330kV lines , NSW to Victoria Transient stability limit. | Outage
VIC1-NSW1 Import | N:V_DDSM_BWRG | 0.083333 | 0 | Out=Dederang to South Morang line, NSW to Victoria Transient stability limit, for the trip of Bayswater to Regentville (31) line | Outage
VIC1-NSW1 Import | N>>N-NIL_DPTX | 0.083333 | 0.083333 | Out = Nil, avoid Darlington Point Tx3 or Tx4 O/L on trip of the other, managing 330kV to 220kV flow on Transformer | NIL

## Outages
Constraint Set ID | 2021 Days | 2020 Days | Description
S-PA_VC1 | 305.9444 | 162.1701 | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
N-MBTE_1 | 146.9965 | 333.1493 | Out= one Directlink cable
V-DDMB | 138.9097 | 0.079861 | Out=Dederang to Mount Beauty 220kV line
V-ELAINEWF_ZERO | 99.1806 | 0.48958 | Elaine Wind Farm upper limit of 0 MW
N-PKWL_94K | 57.9861 | 48.1562 | Out = Parkes to Wellington (94K) 132kV line
S-PATI | 51.5972 | 5.8715 | Out= Para to Torrens Island 275kV line
T-BLINK_NGZ | 50.6424 | 0 | Manage Basslink 5 minute reversal time, ensure Basslink target does not change sign in a single DI. DS only
V-HWJL4_R | 42.8368 | 2.2951 | Out = Hazelwood to Jeeralang No.4 220kV line OR Hazelwood to Jeeralang No.4 line No.4 bus 220kV CB, Radial Mode
I-ML_ZERO | 42.8299 | 41.1007 | Limit Murraylink to zero in either direction
S-SE_132KV_BUS | 41.9514 | 4.2326 | Out = ONLY One South East 132 kV bus (i.e. either East or West 132kV bus WITH/WITHOUT associated CBs)
V-DDSM | 41.8715 | 6.9306 | Out = Dederang to South Morang (DDTS-SMTS) 330 kV line
V-MSSGG_TX | 35.2917 | 0 | Out = One Murray to Guthega 330/132kV Tx
V-HWSM | 32.5521 | 83.1806 | Outage = Hazelwood to South Morang 500kV line
S-PA_VC1_BC-2CP | 30.2743 | 1.9236 | Out= One Para SVC (Note: with both Black Range series caps O/S)
Q-810_PARALLEL_CLOSE | 29.9549 | 0.375 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV network intact
S-PLTX2 | 29.4792 | 0.89583 | Out = Port Lincoln 33/132kV TX2 OR CB4342 O/S; (Note: for Port Lincoln 33kV CB 4637 OPEN or CLOSED)
S-SE_TX_1 | 28.2604 | 4.1319 | Out = One South East 275/132kV transformer (NOTE: associated CBs I/S)
S-X_BC_CP | 27.0069 | 35.2986 | Out = both Black Range series capacitors bypassed
N-AR_CP2 | 23.3611 | 2.9653 | Out = Armidale Capacitor Bank (120 MVAr)
S-CGTI | 23.3299 | 50.2083 | Out= Torrens Island to Cherry Gardens 275kV line
N-MUTW_88 | 22.7292 | 59.1007 | Out = Muswellbrook to Tamworth (88) line
V-HYTX_M12 | 22.1736 | 1.2292 | Out = Heywood (HYTS) M1 or M2 500/275 kV txfmr
F-T-GTTE | 21.5694 | 114.7465 | Out = one George Town to Temco 110kV line OR loss of both Georgetown to Temco 110 kV lines or all Temco load declared credible
N-LDTW_84 | 20.316 | 5.3889 | Out = Liddell to Tamworth (84) 330kV line
V-X_RORT1_SMF2_R | 19.3542 | 0 | Out = Rowville to Richmond No.1 220kV line and South Morang 500/330kV (F2) transformer, radial mode
N-LTYS_03 | 19.316 | 0.33681 | Out= Lower Tumut - Yass (3) 330kV line
Q-X_BCCP_BCST | 18.4896 | 0 | Out= 812+848 (H67 Calliope River to H10 Bouldercombe to H29 Stanwell) 275 kV feeders
I-MSUT | 17.566 | 0 | Out= Murray - Upper Tumut (65) line
V-STOCKYH_ZERO | 16.9479 | 0 | Stockyard Hill wind farm upper limit of 0 MW
S-SECB6161 | 16.4375 | 0 | Out = South East 132kV CB6161 ONLY O/S
S-RBPA | 16.3507 | 0 | Out= Robertstown - Para 275 kV line (Note: with both Black Range series caps I/S)
V-X_HWTS_A1_A_R | 15.4583 | 7.1111 | Out= Hazelwood A1 and either A2 or A3 or A4 500/220kV transformers, Radial Mode
Q-CPWO_813 | 15.4167 | 0 | Out = H67 Calliope River to H5 Woolooga 275kV line (813) feeder Tee Gin Gin (section 1 or 2 or both)
S-X_PA_VC_2 | 15.2639 | 3.3021 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps I/S)
Q-OAKEY1SF_ZERO | 15.1806 | 0 | Oakey 1 Solar Farm upper limit of 0 MW
Q-OAKEY2SF_ZERO | 15.1806 | 0 | Oakey 2 Solar Farm upper limit of 0 MW
N-AR_TX | 15.0312 | 1.1076 | Out= Armidale No.3 or 6 330/132kV transformer
S-X_2DV_SYNCON | 14.934 | 0 | Out = 2 x Davenport O/S (NOTE: ONLY INVOKE Prior to commissioning of both Roberstown syn cons)
N-BU-SCON2-3 | 14.5486 | 40.5799 | Out= Buronga Syncon 2-3, SCON2 and SCON3 are associated with Darlington Point SF
S-MH_CAP | 14.309 | 0 | Out= One or both Capacitor banks (i.e. capacitors 61 or 62) at Monash O/S or not available for switching.
N-CHLS_89 | 14.0347 | 4.1354 | Out= Coffs Harbour - Lismore (89) 330kV line
N-X_MBTE_3 | 13.8021 | 34.0382 | Out= all three Directlink cables
I-VS_050 | 13.7639 | 8.5035 | Victoria to SA on VicSA upper transfer limit of 50 MW
N-SDUT_1 | 13.4097 | 0.034722 | Out= Stockdill to Upper Tumut (1) line
N-AR_VC1 | 13.4097 | 2.3229 | Out = Armidale SVC
N-ARTW_86 | 13.1528 | 4.1215 | Out = Armidale to Tamworth (86) line
S-TB_CB6594 | 12.7257 | 0.20486 | Out= Tailem Bend 275kV CB6594 ONLY O/S (Note: all other 275kV CBs and lines at Tailembend I/S),(Note: with both Black Range series caps I/S)
Q-BSNE | 12.25 | 0 | Out = any one of either 834, 8846, or 8847 275kV fdr H20 Broadsound - H11 Nebo
N-X_ARKK_CH_CB892A | 11.8924 | 3.5938 | 966 (Armidale to Koolkhan) 132kV line O/S and Coffs Harbour CB 892A opened - Arrangement 1 - see OM521
S-RB_TX2 | 11.4618 | 0 | Out = Robertstown #2 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
T-LIWY | 11.3333 | 0 | Out=Liapootah-Wayatinah 220KV line
Q-CPWO_BI_INTACT | 11.0903 | 7.8299 | Out= 813 or 814, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines for Boyne Island bus is intact, Feedback
N-DPWG_63_X5 | 10.9653 | 2.7326 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
T-BUSH_220_WCP_OPEN | 10.8924 | 2.4097 | Out = Burnie to Sheffield No.1 220kV line O/S, West Coast 110/220KV parallel open, either 110 kV CB at Hampshire open or parallel opened at Farrell, Burnie 110 kV bus NOT split
Q-BC_275BUS_CB | 10.5035 | 0 | Out = one 275kV bus or one or more 275kV CB at H010 Bouldercombe
S-NWRB | 10.4375 | 4.309 | Out= Robertstown-North West Bend #1 132kV line
Q-COLTX | 10.3021 | 0 | Out = Collinsville North T1 or T2 132/33 kV transformer
S-MWP3RB | 10.2361 | 0 | Out = Morgan Whyalla Pipeline Pump No.3 - Robertstown 132kV line O/S, (Note: for Murraylink runback I/S or O/S).
S-KHKN | 10.2257 | 21.8611 | Out = Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S)
N-X_MBTE_2 | 10.066 | 144.6354 | Out= two Directlink cables
V-WETS_BTX | 10.0208 | 0 | Out = Wemen 220/66kV B1 or B2 txfmr
Q-OKYOKYSF | 9.8889 | 0 | Derating of 33kV Cable from Oakey(T189) substation to Oakey solar farms
S-PGPP | 9.7188 | 6.8056 | Out= Parafield Gardens West-Pelican Point 275kV line(with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S).
Q-BCST | 9.5625 | 0 | Out = 848 or 849 H10 Bouldercombe to H29 Stanwell 275 kV line
S-DVTX | 9.3819 | 23.4132 | Out= One Davenport 275/132kV TX O/S
N-LS_VC1 | 9.2431 | 97.7049 | Out= Lismore SVC
N-DM_CB | 9.1215 | 0 | Out = Dumaresq 330kV CB 8M2 or 8C2
F-I_ML_APD | 8.9375 | 0.041667 | Out=Nil, Dymanic FCAS for APD Load Event
Q-WRWK | 8.9167 | 1.0139 | Out = 8902 (H39 Woree - H60 Walkamin) 275kV line or Woree (H39) 275/132kV 2T Transformer
T-FAJB | 8.6736 | 1.6736 | Out=Farrell-John Butters 220KV line
I-VS_250 | 8.1875 | 8.5139 | Victoria to SA on VicSA upper transfer limit of 250 MW
S-PATU | 7.8958 | 43.5938 | Out = Para to Tungkillo 275 kV line(Note: with both Black Range series caps I/S)
S-LFPP_PELPT | 7.8333 | 0.70486 | Out = Pelican Point to Lefevre 275kV line outage(Note: with both Black Range series capacitors I/S), trip of Pelican Point - Parafield Gardens West 275kV line resulting in loss of Pelican Point and Snapper Point PS a credible event.
Q-CLBCON_7356 | 7.7014 | 0.35764 | Out= 7356 T194 Columboola to T200 Condamine PS 132kV line
S-RB_TX1 | 7.6493 | 0.0034722 | Out =Robertstown #1 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
S-X_BWMP+MPPA | 7.3646 | 5.1528 | Out = Blyth West- Munno Para 275kV line and Munno Para-Para 275kV (i.e. with Blyth West CB8002 OPEN & Blyth West tripping scheme I/S)
S-X_RBPA+CB6574+75 | 7.2708 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575
N-LDMU_83 | 7.1424 | 0.49306 | Out = Liddell to Muswellbrook (83) line
Q-CLWU | 6.9931 | 0.51042 | Out = 871 H24 Calvale to H40 Wurdong 275kV line
V-X_HG_ML_TR | 6.7049 | 0.39236 | Out = Haunted Gully to Moorabool and Haunted Gully to Tarrone 500kV lines, MOPS 500kV centre CB fail timer set to zero, APD-HYTS No.1 500kV line offloaded at APD
S-PARS | 6.566 | 0 | Out= Roseworthy - Para 132kV line
V-MLMO | 6.5278 | 14.8785 | Out = Moorabool to Mortlake (MLTS-MOPS) No. 2 500 kV line, TRTS 500kV centre CB fail timer set to zero, APD-HYTS No.2 line offloaded
N-BU-SCON1 | 6.3403 | 5.9826 | Out= Buronga Syncon 1, SCON1 is associated with Finley SF
S-TBCP1_BC-2CP | 6.3403 | 0 | Tailem Bend 275 kV capacitor O/S, (Note: with both BlackRange Series Caps O/S)
S-X_WTTP+CB | 6.3229 | 2.441 | Out = Templers - Waterloo 132kV line with associated critical line CBs O/S (i.e. Waterloo CB 7025 & CB7024 O/S)
N-WELLSF1_ZERO | 6.3229 | 0 | Wellington solar farm upper limit of 0 MW
Q-CMTX | 6.2465 | 5.9167 | Out = Clermont T1 or T2 132/66 kV transformer
S-RBMWP4 | 5.9965 | 0 | Out= Robertstown -MWP4 O/S, (Note: MWP4 SF remains connected via Waterloo East)
V-KTTX_A3_R | 5.8681 | 0.41319 | Outage = Keilor 500/220kV A3 transformer, Radial
V-BEKG | 5.4306 | 2 | Outage = Bendigo to Kerang 220kV line
N-X_MSUT_CNYS | 5.3785 | 0 | Out = Murray - Upper Tumut (65) and Canberra - Yass (9) 330kV lines
S-BC_CP | 5.3472 | 0.46528 | Out = either one of Black Range series capacitors bypassed,
F-I_ML_APD_LOAD | 5.3299 | 20.0799 | Out=Nil, Dynamic FCAS for APD Load Event, excluding Portland WF
N-LTWG_RADIAL | 5.1424 | 0.47917 | Out= Lower Tumut - Wagga (051) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
N-WAGGA_330_BUSA | 5.1424 | 0 | Out=Wagga 330kV bus A. Wagga-Yass 132kV network split, X5 opened and with 2 Yass Transformer in service
N-BADP | 5.1146 | 0 | Out = Balranald to Darlington Point (X5) 220kV line
N-BABU | 5.1076 | 0 | Out = Balranald to Buronga (X3) 220kV line
N-X_BABU_BADP | 5.0764 | 0.42361 | Out = Balranald to Buronga (X3) and Balranald to Darlington Point (X5) 220kV lines
N-MPWW_ONE | 5.0104 | 4.0799 | Outage of Mt. Piper to Wallerawang (70 or 71) 330kV line
I-BCDM_ONE | 4.9028 | 1.2986 | Out = one Bulli Creek to Dumaresq (8L or 8M) line
V-EPMB | 4.8576 | 10.5 | Outage = Eildon to Mt Beauty 220kV line
N-ARTW_85 | 4.5938 | 0.079861 | Out = Armidale to Tamworth (85) line
N-CNSD_3C | 4.559 | 0.034722 | Out= Canberra to Stockdill (3C) line
N-DMSR_8J | 4.441 | 0.875 | Out= Dumaresq to Sapphire (8J) line
Q-SRMB_3 | 4.3819 | 0 | Out= Susan River to Maryborough 66kV line section 3 (M020/3)
N-ARDM_8C | 4.3542 | 0.54861 | Out= Armidale to Dumaresq (8C) line
F-T-CSGO | 4.0347 | 2.4618 | Out = one Chapel St to Gordon 220kV line, FCAS Requirements
T-CSGO | 4.0347 | 2.2326 | Out = One Chapel St to Gordon 220kV line
N-X_MSUT_993_99P | 4.0174 | 0 | Out = Murray to Upper Tumut(65) 330kV line And either 993 (Wagga330 to Gadaraor) or 99P(Gadara to Tumut132) 132kV line
S-MHNW_2 | 3.9236 | 0.010417 | Out = Monash to North West Bend line 2, (Note: Murraylink runback scheme can be I/S or O/S)
V-KG_WE_RC | 3.9167 | 1.3507 | Outage = Kerang to Wemen to Red Cliffs 220 kV line section, entire line section
V-KTTX_A2_OR_A4_R | 3.6181 | 8.0451 | Outage = Keilor 500/220kV A2 or A4 transformer, Radial
V-MLSY_NOEMTT_R | 3.5903 | 2.9583 | Out = One Moorabool to Sydenham 500 kV line, EMTT scheme not armed, Radial mode
Q-H11NE_SVC | 3.5625 | 7.0174 | Out= H11 Nebo SVC OOS
S-BRTX3 | 3.5174 | 0.79861 | Out= Brinkworth 275/132kV TX3 transformer (with/without associated CBs 6530 & 6528& 6093 & 6068 OPEN).
S-X_RBMWP4+RBTX | 3.441 | 0 | Out= Robertstown - MWP4 + one 275/132kV RBTX O/S, (Note: MWP4 SF remains connected via Waterloo East)
N-UTYS_2 | 3.434 | 51.8299 | Out= Upper Tumut to Yass (2)
Q-WR_VC | 3.4201 | 0.30903 | Out= H39 Woree 132 kV SVC
V-KGTS_SVC | 3.4201 | 8.7222 | Out = Kerang 220kV SVC
S-BRBG | 3.4062 | 1.4271 | Out = Brinkworth to Redhill to Bungama 132kV lines (Note: outage also takes out Clements Gap Windfarm).
N-BAMB_132_OPEN | 3.3194 | 1.4965 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path.
N-TW_330_CB5102 | 3.3194 | 0.38194 | Out= Tamworth 330kV CB 5102
Q-OKYTX3 | 3.3056 | 0 | Out= Oakey 110/33kV transformer (T3)
Q-MB_66_CB_E352 | 3.2014 | 0 | Out = Maryborough(T59) 66kV CB E352
N-TW_330_BUS3 | 3.1424 | 0 | Out= Tamworth No.3 330kV bus
N-TW_330_BUS1 | 3.1389 | 0 | Out= Tamworth No.1 330kV bus
I-BL_ZERO | 3.1042 | 2.5174 | Limit Basslink to zero in either direction
N-PK_TX | 3.059 | 0.38542 | Out = One Parkes 132/66kV Transformer
S-PLTX3 | 3.059 | 0.29861 | Out = Port Lincoln 33/132kV TX3 (Note: with CB4636 & CB4543 OPEN) O/S; (Note: for Port Lincoln 33kV CB 4637 CLOSED)
I-JNWO_RADIAL | 2.9792 | 1.8715 | Out = Jindera to Wodonga (060) line, Wagga-Yass 132kV network Split, X5 opened, 63 energised or de-energised
Q-RSWR | 2.9653 | 0.055556 | Out= 8966(H13 Ross to H39 Woree) 275kV line or Woree (H39) 275/132kV 1T Transformer
Q-LVDS | 2.9549 | 0.15278 | Out =7150 (H15 Lilyvale to T35 Dysart tee Norwich Park) 132kV line
N-X_89_LSTX_SVC | 2.8924 | 0 | Outage of Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode
N-GITN_96R | 2.8715 | 4.3194 | Out= Glen Innes to Tenterfield (96R) line
S-BRDV | 2.8368 | 22.125 | Out = Brinkworth - Davenport 275 kV line
N-X_MSUT_KVCW | 2.7812 | 0 | Out = Murray - Upper Tumut (65) line and Kangaroo Valley to Capital (3W) 330kV line
V-VBB_L_ZERO | 2.7674 | 0 | Victorian Big Battery (Load Component) upper limit of 0 MW
Q-SRMB | 2.6667 | 1.9965 | Out= Susan River to Maryborough 66kV line section 2 (M020/2)
Q-YL_CB4412 | 2.6632 | 1.7257 | Out = T10 Yarranlea 110kV CB 4412
N-WRWSF_ZERO | 2.5972 | 0 | Upper limit of zero MW on total generation of White Rock wind and solar farms
N-DP_TIETX | 2.5139 | 1.0972 | Out= DarlingtonPt 330/220/33 kV tie Tx (#3 or #4)
S-HALWF2_0 | 2.4965 | 0 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW
S-TBSE_BC-2CP | 2.4688 | 0 | Out - one South East-Tailembend 275kV line (Note: with both Black Range series caps O/S)
V-MLTX_A1_R | 2.4549 | 1.8958 | Out= Moorabool A1 500/220kV transformer, Radial Mode
V-HYMO | 2.4375 | 0 | Out = Heywood to Mortlake (HYTS-MOPS) No. 2 500 kV line
Q-BS_275_CB_3 | 2.4236 | 5.2014 | Out = one or more 275kV CB (CB88312 or CB88472)at H20 Broadsound
S-HUBG | 2.3889 | 3.2951 | Out= Hummocks-Bungama 132kV line (Note: this offloads Snowtown WF)
T-PMWA | 2.3681 | 0.32639 | Out = Palmerston to Waddamana 110kV line; suitable for associated CBs at WA either open or close
S-HUWT | 2.3194 | 2.1562 | Out= Hummocks-Waterloo 132kV line
S-MHNW_1 | 2.2986 | 5.9583 | Out = Monash to North West Bend line 1, (Note: Murraylink runback scheme can be I/S or O/S)
S-BRTW | 2.2951 | 6.309 | Out= Brinkworth- Templers West 275kV line
N-FBPK_94U | 2.2778 | 2.6979 | Out = Forbes to Parkes (94U) 132kV line
N-LSDU_9U6 | 2.2188 | 1.1979 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L on the remaining 132kV line, Feedback
V-KGWT | 2.1944 | 0 | Outage = Kerang to Wemen 220 kV line section
N-STWF1_ZERO | 2.1597 | 2.4271 | Silverton wind farm upper limit of 0 MW
S-RBTU | 2.125 | 0 | Out= Robertstown - Tungkillo 275 kV line (Note: Line ONLY O/S with associated line CBs I/S); (NOTE: with both Black Range series caps I/S)
S-X_PA_VC_2_BC-2CP | 2.0625 | 0 | Out = Para SVC 1 and 2 (Note: with both Black Range series caps O/S)
S-X_RBTU+CB | 2.0347 | 0 | Out= Robertstown-Tungkillo 275kV line and Robertstown 275kV CBs 6571 & 6572 O/S, (Note: with Both Black Range series caps I/S)
S-NWRB2 | 2.0069 | 0.82986 | Out = North West Bend to Robertstown No.2 132kV line O/S
Q-KSP1_ZERO | 1.9549 | 0.29514 | Kidston solar farm upper limit of 0 MW
Q-CCHW_RAMP_ZERO | 1.9132 | 0 | Ramp Clare, Collinsville, Hamilton and Whitsunday Solar farms to zero and hold at zero.
S-PA_W_BUS_R | 1.9062 | 0.63542 | Out= Para 275kV West bus Right section(i.e.CBs 6601,8033,6510,6514 6542,6541, TX8 O/S),(NOTE: BW-MP 275kV line will also be taken O/S as per Electranet's OI 5.17 issued 19/07/2017),(Note: with both Para SVC 1 & 2 inservice and connected to Para East bus)
V-DDWO_RADIAL | 1.8958 | 0.27778 | Out = Dederang to Wodonga 330kV line O/S. TL63 330kV line and X5 opened. See OM 526 and OM 608
N-ARIV_96N | 1.8819 | 0.54861 | Out = Armidale to Inverell (96N) 132kV line
T-CTHLWF_ZERO | 1.8403 | 0 | Wild Cattle Hill Wind Farm upper limit of 0 MW
N-CRWF1_ZERO | 1.8333 | 0 | Crudine Ridge wind farm upper limit of 0 MW
N-UTRV_6X | 1.7569 | 0 | Out= Upper Tumut to Ravine (6X) 330kV line
Q-ST_275BUS_CB | 1.75 | 0.31944 | Out = one 275kV bus or one or more 275kV CB at H29 Stanwell
S-CGTB1 | 1.7049 | 0.33681 | Cherry Gardens to Tailem Bend 275kV line O/S (NOTE: with both Black Range series caps I/S)
N-LTUT_64_15M | 1.6354 | 0.31597 | Out= Lower to UpperTumut (64), 15/30_min ratings for 65, 66 lines auto-switch on prior loading
I-LTMS | 1.5799 | 0 | Out= Lower Tumut - Murray (66) line
Q-EMLV_6067 | 1.5729 | 0.50694 | Out= 6067 Emerald to Lilyvale 66kV line with Emerald SF offloaded
S-X_SEVC2+PAVC | 1.5382 | 0 | Out= Both South East SVC1 & SVC 2 + one Para SVC O/S, (Note: with both Black Range series caps I/S)
N-LPSW30+RGSW38 | 1.5312 | 0.72569 | Out = Liverpool to Sydney West (30) + Regentville to Sydney West (38) 330 kV lines
N-TARALGAWF_ZERO | 1.5035 | 1.4826 | Taralga WF upper limit of 0 MW
N-AR_330_BS1 | 1.441 | 0 | Out= Armidale No.1 330kV bus
S-X_CNRB+CB | 1.3715 | 0 | Out = Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S(Note:both Black Range series capacitors I/S)
V-CROWLANDS_ZERO | 1.3403 | 0 | Crowlands Wind Farm upper limit of 0 MW
T-HAPM_220 | 1.3333 | 0.27778 | Out = One Hadspen to Palmerston (No.1 or No.2) 220kV line
Q-RRSF1_ZERO | 1.2118 | 0.51389 | Ross River solar farm upper limit of 0 MW
Q-SMHAU | 1.1701 | 0.45486 | Out = 879 (H35 Strathmore to H91 Haughton) 275kV line
N-AR330BS3 | 1.1424 | 0 | Out= Armidale 330kV Bus Section #3
I-HYSE | 1.0938 | 0 | Outage = Heywood to South East 275kV line
T-TU_MB_NN2 | 1.0903 | 0.40278 | Out= Tungatinah to Meadowbank to New Norfolk No.2 110kV lines
I-BURC | 1.066 | 0.29167 | Out = Buronga to Red Cliffs (0X1) 220kV line
T-TU_MB_NN1 | 1.0486 | 0.40625 | Out= Tungatinah to Meadowbank to New Norfolk No.1 110kV line
N-ARCH_87 | 1.0451 | 2.7292 | Out= Armidale - Coffs Harbour (87) 330kV line
N-ARSR_8E | 1 | 0.78472 | Out= Armidale Sapphire (8E) line
N-AR_330_BS5 | 1 | 0 | Out= Armidale No.5 330kV bus
V-SMSY | 0.95486 | 1.5521 | Out = Either South Morang-Sydenham 500 kV line, Radial mode
V-BA_BAT_G_ZERO | 0.92708 | 0.70486 | Ballarat Battery (Generation Component) upper limit of 0 MW
S-RBPA_BC-2CP | 0.92361 | 0 | Out= Robertstown - Para 275 kV line (Note: both Black Range series caps O/S)
V-RCTS_TX_1B | 0.92361 | 0 | Out= Red Cliffs 1B 220/66kV transformer
N-MOREESF1_ZERO | 0.92014 | 0 | Moree Solar Farm upper limit of 0 MW
Q-RSKID_7158 | 0.91319 | 0 | Out = 7158 (H13 Ross to T77 Kidston) 132 kV Feeder
N-GOONSF1_ZERO | 0.91319 | 1.4167 | Goonumbla solar farm upper limit of 0 MW
S-LFTI | 0.91319 | 0 | Out= Torrens Island-Lefevre 275kV line (with TIPS 66kV East and West buses tied, with all 66kV feeders in western 66kV network I/S)
V-EPTT_R | 0.90625 | 4.8785 | Outage = Eildon to Thomastown 220kV line, Radial
V-MURRAWR_ZERO | 0.89931 | 0.14931 | Murra Warra wind farm upper limit of 0 MW
S-DVLK | 0.89931 | 3.1215 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitors I/S)
V-AR_WB_BA | 0.86111 | 1.3854 | Out = Ararat to Waubra to Ballarat 220kV lines OR any 220kV line section between Ballarat and Ararat. Waubra wind farm disconnected/off
T-FARC1 | 0.83681 | 0.44792 | Out=Farrell-Reece 1 220KV line
V-SMTS_BYPASS_HW_SY | 0.79514 | 4.2535 | Outage = SMTS 500kV bus or CB outages or SMTS bus bypass that creates risk of HWTS-SMTS and SMTS-SYTS combined line trip, Radial or Parallel
Q-LVCM | 0.74653 | 0.59028 | Out =7153 (H15 Lilyvale to T71 Clermont) 132kV line
N-IVWR-9U4 | 0.73611 | 0 | Out = Inverell to White Rock (9U4) 132kV line
V-HOTS_SVC | 0.72569 | 0.5625 | Out = Horsham 220kV SVC
T-TUNN3 | 0.72569 | 0 | Out = Tungatinah to New Norfolk No.3 110kV line
S-PATW | 0.72222 | 2.4722 | Out = Para - Templers West 275kV line
N-BOCORWF1_ZERO | 0.71181 | 0 | Boco Rock WF upper limit of 0 MW
S-MWPS4-PV_0 | 0.70139 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 4 PV generation of 0 MW
N-BODWF1_ZERO_WT | 0.69097 | 0 | Bodangora wind farm upper limit of 0 MW and 0 Wind Turbine
N-AR_CP1 | 0.69097 | 0.58333 | Out = Armidale Capacitor Bank (80 MVAr)
I-SVML_080 | 0.65278 | 0.034722 | SA to Vic on ML upper transfer limit of 80 MW
T-SH_TX_WCP_OPEN | 0.63194 | 1.3021 | Out = one Sheffield 220/110kV transformer, West Coast 110/220 kV parallel open
V-KIAMAL_SC | 0.61806 | 0.16667 | Outage = Kiamal Syncon, 7422B and RC2A closed
N-KKLS_967 | 0.61458 | 0.47222 | Out= Koolkhan to Lismore (967) 132kV line
V-ROSM | 0.60764 | 0 | Outage = Rowville to South Morang 500kV line
S-CNLK | 0.60069 | 0 | Out= Canowie-Mt Lock 275kV line (Note: with both Black Range series caps I/S)
Q-H13RS_SVC | 0.58681 | 1.2604 | Out= H13 Ross 275 kV SVC
S-NWCB6021+6225 | 0.58333 | 0 | Out = North West Bend 132 kV circuit breakers CB6021 and CB6225(Note: this takes out North West Bend-Monash #1 132kV line).(Note: for Murraylink runback scheme I/S or O/S and Sever scheme I/S or O/S)
V-BRYBWF_ZERO | 0.57986 | 0 | Berrybank Wind Farm upper limit of 0 MW
T-GTSH | 0.57986 | 5.1562 | Out = One George Town to Sheffield 220kV line
V-SMTT2 | 0.55903 | 0 | Out= South Morang to Thomastown No. 2 220 kV line
V-MBMK | 0.55903 | 0.75 | Outage of Mt Beauty to Mackay 220 kV line
S-BGDV | 0.54514 | 11.625 | Out= Davenport-Bungama 275kV line, (i.e. with Blyth West CB8001 OPEN & Blyth West trip scheme I/S)
Q-SMCK | 0.54167 | 0.44097 | Out = 8906 (H35 Strathmore to H87 Crush Creek) 275kV line
Q-NQ_275BUS_CB | 0.53819 | 0.22917 | Out = one 275kV Bus or one or more 275kV CB at north of Calvale and Calliope River resulting loss of two 275kV feeders in the next contingency.
V-EL_BUS2 | 0.52083 | 0 | Out = Elaine No.2 220kV bus
S-KHKN_BC-2CP | 0.49653 | 0 | Out = Keith - Kincraig 132 kV line (Note: with both Black Range series caps O/S)
V-X_HY_MO_ML | 0.45486 | 0 | Out = Heywood to Mortlake to Moorabool No.2 500kV lines
V-X_WETS_BTX | 0.45139 | 0.18056 | Out = Wemen 220/66kV B1 and B2 txfmr
N-CNYS_9 | 0.44792 | 4.2465 | Out = Canberra - Yass (9)
V-ARCW | 0.44444 | 0.37153 | Out = Ararat to Crowlands 220kV line
V-EL_BUS1 | 0.43403 | 0 | Out = Elaine No.1 220kV bus
V-KTSY_R | 0.43056 | 0.72222 | Outage = Keilor to Sydenham 500kV line, Radial mode
N-FINLYSF1_ZERO_INV | 0.43056 | 0 | Finley solar farm upper limit of 0 MW and 0 Inverter
S-RB_275KV_N_BUS | 0.42708 | 5.1944 | Out =Robertstown North 275kV Bus (this offloads Robertstown TX1) O/S, (NOTE:with RBTX1 132kV CBs 6005 & 6188 O/S)
V-BABE | 0.42014 | 0 | Outage = Ballarat to Bendigo 220kV line
S-BLNBH_0 | 0.41667 | 0 | Out = Belalie - North Brown Hill 275kV line O/S (i.e. North Brown Hill WF <= 0 MW)
S-MWPS3-PV_0 | 0.41667 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 3 PV generation of 0 MW
V-KIAMAL_SC_220CB | 0.41319 | 0 | Outage = Kiamal Syncon, 7422B and RC2A open
S-TBSE | 0.40972 | 0 | Out - one South East-Tailembend 275kV line (Note: with one Black Range series caps I/S)
V-HYCB_210_213 | 0.40278 | 0.33333 | Out = Heywood (HYTS) 500 kV CB 210 or 213
Q-X_BSNE_NE_275BUS | 0.40278 | 0 | Out = 834 or 8846 or 8847 (H20 Broadsound to H11 Nebo) 275kV line and Nebo (H11) 275kV no 1 or no 2 Bus
V-KMRC | 0.39583 | 0.49653 | Out = Kiamal to Red Cliffs 220kV line
S-MYTX1_44248OPEN | 0.39583 | 0 | Out = Mayura No.1 132/33kV transformer (with 33kV bus tie isolator 44248 open)
N-GNNDHSF1_ZERO_INV | 0.38889 | 0 | Gunnedah solar farm upper limit of 0 MW and 0 Inverter
S-DVEM | 0.37153 | 0 | Out = Davenport - Emeroo #1 132kV line (Note: With/Without associated line CBs)
N-X_TW_330_BUS3-5 | 0.36111 | 0 | Out= Tamworth No.3 and No.5 330kV bus
S-RBTU_BC-2CP | 0.35417 | 0 | Out= Robertstown - Tungkillo 275 kV line (Note: Line ONLY O/S with associated line CBs I/S); (NOTE: with both Black Range series caps O/S)
S-X_RBPA+RBTX1 | 0.35069 | 0 | Out=Robertstown-Para 275kV line+ Robertstown 132/275 kV TX1 O/S (Note: with both Black Range series caps I/S)
Q-BS_275_BUS | 0.34028 | 0 | Out = one of the 275kV Bus H20 Broadsound
Q-EMERASF1_ZERO | 0.33681 | 0.22917 | Emerald Solar Farm upper limit of 0 MW
S-X-RBTX2+6572+6575 | 0.32986 | 10.5 | Out= Robertstown South 275kV Bus (Note: this offloads Robertstown TX2) O/S,(NOTE:with RBTX2 132kV CBs 6148 & 6149 I/S);
Q-BCNE_821 | 0.31597 | 11.1181 | Out = 821 275kV fdr H10 Bouldercombe - H11 Nebo
F-S_DLBAT-G_ZERO | 0.30903 | 0.14236 | Dalrymple Battery (Generation Component) FCAS <= 0MW
F-S_DLBAT-L_ZERO | 0.30903 | 0.14236 | Dalrymple Battery (Load Component) FCAS <= 0MW
N-STWF1_ZERO_WT | 0.30903 | 0 | Silverton wind farm upper limit of 0 MW and 0 Wind Turbine
N-BROKENH1_ZERO_INV | 0.30903 | 0 | Broken Hill solar farm upper limit of 0 MW and 0 Inverter
N-BODWF1_ZERO | 0.30208 | 0.89931 | Bodangora wind farm upper limit of 0 MW
T-GTHA | 0.29861 | 0.38542 | Out = One George Town to Hadspen 220kV line
N-AR_132BUS_1_CB892A | 0.29514 | 0 | Out= Armidale No.1 132kV Bus and Coffs Harbour CB 892A
S-HALWF_0 | 0.29514 | 0 | Discretionary upper limit for Hallett Wind Farm generation of 0 MW
N-WR_TTS | 0.29167 | 0 | Out = White Rock Generation Transfer Trip Scheme
Q-RGBYRSF1_ZERO | 0.28819 | 0 | Rugby Run Solar Farm upper limit of 0 MW
Q-YARANSF1_ZERO | 0.28125 | 0 | Yarranlea Solar Farm upper limit of 0 MW
V-DUNDWF3_ZERO | 0.27431 | 0.027778 | Dundonnell wind farm 3 upper limit of 0 MW
V-DUNDWF1_ZERO | 0.27431 | 0.027778 | Dundonnell wind farm 1 upper limit of 0 MW
V-DUNDWF2_ZERO | 0.27431 | 0.027778 | Dundonnell wind farm 2 upper limit of 0 MW
V-BA_EL_ML | 0.27431 | 0 | Out = Ballarat to Elaine to Moorabool 220kV line
N-X_BALS_66_OPEN | 0.27083 | 0.39583 | Out = Any 2 66 kV lines in parallel between Lismore and Ballina that opens the 66 kV path.
S-X-RBTX1+6616+6573 | 0.26736 | 14.1736 | Out =Robertstown North 275kV Bus (this offloads Robertstown TX1) O/S, (NOTE:with RBTX1 132kV CBs 6005 & 6188 I/S)
S-TBTU | 0.26389 | 0.30903 | Out= Tailem Bend - Tungkillo 275kV line (Note: WITH/WITHOUT associated line CBs I/S), (NOTE: with both Black Range series caps I/S)
N-MOREESF1_ZERO_INV | 0.26389 | 0 | Moree Solar Farm upper limit of 0 MW and 0 Inverter
S-LBMY_2B | 0.26042 | 0 | Out= Mayura-Lake Bonney WF 2B 33kV line (OR Mayura CB4565 and CB4674 OPEN)
Q-SMSPL | 0.26042 | 0.059028 | Out = 7457 (H35 Strathmore to T242 Springlands) 132kV line O/S
T-X_TU_LE_WA_TWO | 0.25694 | 0 | Out = Both Tungatinah to Waddamana 110kV lines (No. 1 line via Lake Echo tee and No. 2 direct line)
S-TBSF1_0 | 0.24653 | 0.5625 | Discretionary upper limit for Tailem Bend (Coorong) Solar PV of 0 MW
S-X_SE_SVC | 0.24653 | 0.12153 | Out= Both South East SVC1 & SVC 2 O/S, (Note: with both Black Range series caps I/S)
Q-STBS | 0.23958 | 0.34028 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
S-WE_MWP4_RB | 0.22917 | 0.74653 | Out = Robertstown - MWP4 - Waterloo East 132kV line (Note: MWP4 Solar Farm is offloaded) O/S
N-CNLT_07 | 0.22222 | 2.5382 | Out= Canberra - Lower Tumut (07) 330kV line
Q-YARRAN_RTU | 0.21528 | 0 | Out = Yarranlea or Yarranlea North RTU, limit Maryrorough SF to 10 MW and Yarranlea SF to 37MW
F-WESTCOAST_REG_0 | 0.21528 | 0.35069 | Regulation FCAS of West Coast Generation limited to 0 MW
Q-LV_275_CB | 0.20139 | 0 | Out = one or more Lilyvale (H15) 275kV CB (CB8502,CB5412,CB5012,CB5422) O/S
Q-MEWF1_ZERO | 0.19792 | 0.052083 | Mt Emerald Wind Farm upper limit of 0 MW
Q-LVTX | 0.19444 | 0 | Out = Lilyvale 275/132 kV transformer T1 or T2
Q-X_YLTX_YLTX | 0.19097 | 0 | Out = both Yarranlea 110/33 kV Transformers and Maryrorough SF is only connected to Torrington 110KV via 33kV network ,supplying up to 5MW
Q-BS_275_CB_2 | 0.17708 | 0 | Out = one or more 275kV CB (CB8562, CB 8332) at H20 Broadsound
I-CTRL_ISSUE_ML | 0.16667 | 1.1424 | DC Link Control Issue Constraint for Murraylink
F-T-COGT | 0.16319 | 6.691 | Out = one Comalco to George Town 220kV line OR loss of both Comalco to Georgetown 220 kV lines or all Comalco potlines declared credible
N-CRWASF1_ZERO | 0.14931 | 0 | Corowa solar farm upper limit of 0 MW
N-NSNY-9GU | 0.14236 | 0 | Out = Narromine South to Nyngan132 (9GU) 132 kV line
I-QN_1000 | 0.13889 | 0 | Qld to NSW on QNI limited to 1000 MW, includes constraint with dynamic headroom
V-HYTR | 0.11806 | 1.2604 | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line
S-MWPS2-PV_0 | 0.11111 | 0 | Discretionary upper limit for SA WATER Morgan Whyalla Pump Station 2 PV generation of 0 MW
I-SV_100 | 0.10764 | 0 | SA to Victoria on VicSA upper transfer limit of 100 MW
T-TU_105 | 0.10417 | 0 | Discretionary 105 MW upper limit on Tungatinah
N-COLWF01_ZERO | 0.10417 | 0 | Collector wind farm upper limit of 0 MW
I-CTRL_ISSUE_TE | 0.083333 | 0.059028 | DC Link Control Issue Constraint for Terranora
S-NWB_CB6022 | 0.072917 | 0 | North West Bend CB6022 ONLY O/S, Murraylink runback scheme I/S or O/S, Murraylink sever scheme I/S or O/S (NOTE: DO NOT INVOKE if Murraylink Interconnector is O/S)
Q-YLMR_733/1_734/1 | 0.069444 | 25.1736 | Out=733/1 or 734/1 (T10 Yarranlea to H14 Middle Ridge) 110kV
Q-DDSF1_ZERO | 0.065972 | 0 | Darling Downs solar farm upper limit of 0 MW
S-DVLK_BC-2CP | 0.065972 | 0 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitorsO/S)
S-DLBAT-G_0 | 0.055556 | 0 | Discretionary upper limit for Dalrymple Battery (generation component) of 0 MW
S-DLBAT-L_0 | 0.055556 | 0 | Discretionary upper limit for Dalrymple Battery (Load component) of 0 MW
V-X_HWSM_ROSM | 0.052083 | 0 | Out = One Hazelwood to South Morang and Rowville to South Morang 500kV lines
I-BL-FCSPS_NO_ACTION | 0.048611 | 0.076389 | Constrains Basslink transfers to levels where no FCSPS action is required for loss of Basslink
Q-HRHAUSF_8913 | 0.048611 | 0 | Out = 8913 (H91 Haughton River - Haughton SF) 275kV feeder
V-MTMERCER_ZERO | 0.045139 | 1.4618 | Mt Mercer Windfarm upper limit of 0 MW
I-SVML_050 | 0.041667 | 0 | SA to Vic on ML upper transfer limit of 50 MW
T-FCSPS_RAMP | 0.041667 | 0.090278 | Ramp down Basslink for outage of FCSPS
Q-HASMME_ZERO | 0.038194 | 2.0208 | Discretionary upper limit of 0MW on Haughton Solar Farm, Sun Metal Solar Farm and Mt Emerald Windfarm
V-HWCB4 | 0.038194 | 0.15625 | Outage = Hazelwood to Cranbourne No.4 500kV line
Q-CLARESF1_ZERO | 0.03125 | 0 | Clare solar farm upper limit of 0 MW
Q-RSCH | 0.020833 | 0.90278 | Out= 857 or 858 (H13 Ross to H32 Chalumbin) 275kV line
Q-LILYSF1_ZERO | 0.020833 | 0 | Lilyvale Solar Farm upper limit of 0 MW
V-WKPS12_ZERO | 0.0069444 | 0 | Discretionary upper limit for West Kiewa Hydro 1 & 2 aggregate Generation of 0 MW

## Outage stats
NSP / Year | Unplanned | Short Notice | ≤ 30 days | ≤ 3 months | ≤ 6 months | ≤ 9 months | > 9 months
APT 2017 | 20 | 33 | 5 | 4 | 0 | 0 | 0
2018 | 21 | 74 | 15 | 2 | 0 | 1 | 0
2019 | 17 | 58 | 24 | 1 | 0 | 0 | 0
2020 | 13 | 23 | 13 | 2 | 0 | 0 | 0
2021 | 13 | 23 | 13 | 2 | 0 | 0 | 0
ElectraNet 2017 | 281 | 687 | 907 | 326 | 77 | 23 | 0
2018 | 417 | 863 | 973 | 765 | 31 | 8 | 0
2019 | 352 | 852 | 1077 | 687 | 142 | 6 | 0
2020 | 269 | 654 | 958 | 599 | 219 | 21 | 0
2021 | 269 | 654 | 958 | 599 | 219 | 21 | 0
Essential E 2017 | 4 | 28 | 61 | 0 | 0 | 0 | 0
2018 | 8 | 5 | 29 | 0 | 0 | 0 | 0
2019 | 4 | 17 | 39 | 0 | 0 | 0 | 0
2020 | 3 | 22 | 62 | 1 | 0 | 0 | 0
2021 | 3 | 22 | 62 | 1 | 0 | 0 | 0
Powerlink 2017 | 1796 | 5071 | 11266 | 195 | 0 | 0 | 0
2018 | 2020 | 5841 | 13383 | 222 | 0 | 0 | 0
2019 | 2040 | 5250 | 8042 | 2154 | 180 | 0 | 0
2020 | 1897 | 6642 | 8078 | 3903 | 247 | 51 | 44
2021 | 1946 | 6623 | 8087 | 3906 | 247 | 51 | 44
AusNet 2017 | 316 | 1484 | 1208 | 80 | 0 | 0 | 0
2018 | 304 | 1467 | 970 | 54 | 0 | 0 | 0
2019 | 364 | 1387 | 1588 | 69 | 0 | 0 | 0
2020 | 370 | 1128 | 1689 | 67 | 10 | 1 | 0
2021 | 373 | 1128 | 1692 | 67 | 10 | 1 | 0
TasNetworks 2017 | 89 | 472 | 602 | 208 | 53 | 15 | 47
2018 | 171 | 577 | 637 | 109 | 47 | 19 | 63
2019 | 198 | 500 | 1069 | 223 | 47 | 0 | 70
2020 | 108 | 1231 | 890 | 321 | 60 | 31 | 26
2021 | 108 | 1231 | 890 | 321 | 60 | 31 | 26
TransGrid 2017 | 277 | 911 | 1365 | 740 | 95 | 5 | 16
2018 | 326 | 820 | 1730 | 502 | 19 | 1 | 0
2019 | 327 | 1066 | 1868 | 827 | 10 | 0 | 0
2020 | 411 | 1061 | 1635 | 811 | 30 | 2 | 0
2021 | 418 | 1084 | 1638 | 820 | 39 | 2 | 0

## NEM Changes
PROJECT | DATE | REGION | NOTES
Ravine Substation | 2021-01-09 | NSW | Ravine Substation has been cut into the existing Upper Tumut - Yass (02) 330 kV Line to form the following circuits: Upper Tumut - Ravine 6X 330 kV Transmission Line, Ravine - Yass 2 330 kV Transmission Line
SA Water Morgan Whyalla Pump Station 4 PV | 2 February 2021 | SA | New Generator
Corowa Solar Farm | 9 February 2021 | NSW | New Generator
SA Water Morgan Whyalla Pump Station 1 PV | 9 February 2021 | SA | New Generator
SA Water Morgan Whyalla Pump Station 2 PV | 9 February 2021 | SA | New Generator
Berrybank Wind Farm | 16 February 2021 | Victoria | New Generator
Marulan 330/132kV No 3 Transformer | 2021-02-17 | NSW | Replacement transformer for No.4 330/132 kV transformer
Winton Solar Farm | 30 March 2021 | Victoria | New Generator
Mackay GT | 1 April 2021 | Qld | Deregistered Generator
Gangarri Solar Farm | 13 April 2021 | Qld | New Generator
Adelaide Desalination Plant 11 MW PV | 20 April 2021 | SA | New Generator
Adelaide Desalination Plant Battery 7.76 MW - Gen Component | 20 April 2021 | SA | New Battery
Adelaide Desalination Plant Battery 7.76 MW - Load Component | 20 April 2021 | SA | New Battery
Keilor Terminal Station 100 Mvar 220kV Reactor | 2021-04-21 | Victoria | At Keilor terminal station the 100 MVAr 220 kV reactor was commissioned. Market noticce 84614 says 21st April?
Bango 999 Wind Farm | 25 May 2021 | NSW | New Generator
Junee Solar Farm | 25 May 2021 | NSW | New Generator
Wagga North Solar Farm | 8 June 2021 | NSW | New Generator
Kennedy Solar Farm | 22 June 2021 | Qld | New Generator
Kennedy Wind Farm | 22 June 2021 | Qld | New Generator
Gunnedah Solar Farm | 29 June 2021 | NSW | New Generator
Bulgana Battery (Generation Component) | 1 July 2021 | Victoria | New Battery
Bulgana Battery (Load Component) | 1 July 2021 | Victoria | New Battery
MLTS - VBB 220 kV cable | 2021-07-03 | Victoria
Wandoan South Bess (Generation Component) | 6 July 2021 | Qld | New Generator
Wandoan South Bess (Load Component) | 6 July 2021 | Qld | New Generator
Stockyard Hill Wind Farm | 8 July 2021 | Victoria | New Generator
Suntop Solar Farm | 27 July 2021 | NSW | New Generator
Victorian Big Battery (Generator Component) | 27 July 2021 | Victoria | New Battery
Victorian Big Battery (Load Component) | 27 July 2021 | Victoria | New Battery
Davenport synchronous condensers | 2021-08-05 | SA
Mannum Adelaide Pumping Station No 2 Mapl2 (Palmer) -13.70 Mw Pv Generation | 10 August 2021 | SA | New Generator
Armidale No 3 330 kV 50 MVAr Capacitor | 2021-08-19 | NSW | At Armidale substation the No 3 330 kV 50 MVAr Capacitor
Armidale No 4 330 kV 50 MVAr Capacitor | 2021-08-19 | NSW | At Armidale substation the No 4 330 kV 50 MVAr Capacitor
Armidale No 5 330 kV 125 MVAr Capacitor | 2021-08-19 | NSW | At Armidale substation the No 5 330 kV 125 MVAr Capacitor
Dumaresq 8L2A 330kV Circuit Breaker | 2021-09-16 | NSW | At Dumaresq substation the 8L2A 330 kV circuit breaker was commissioned
Smartwires - Vic - NSW | 2021-09-19 | Victoria | At Wodonga 330 kV substation Smartwires FACTS devices were commissioned on Jindera - Wodonga 060 330 kV line.
Tamworth 330 kV No 5112 Circuit Breaker | 2021-09-22 | NSW | At Tamworth a new 330 kV bus section circuit breaker CB 5112 was commissioned
Dumaresq No 1 330 kV 125 MVAr Capacitor | 2021-09-29 | NSW | At Dumaresq substation the No 1 330 kV 125 MVAr capacitor was commissioned
Dumaresq No 2 330 kV 125 MVAr Capacitor | 2021-09-29 | NSW | At Dumaresq substation the No 2 330 kV 125 MVAr capacitor was commissioned
Torrens Island A Unit 1 | 30 September 2021 | SA | Deregistered Generator
Hillston Solar Farm | 5 October 2021 | NSW | New Generator
Robertstown No.1 and No.2 synchronous condensers | 2021-10-11 | SA
Demand Response – Enel X NSW | 24 October 2021 | NSW | New WDR
Demand Response – Enel X Vic | 24 October 2021 | Victoria | New WDR
Wallgrove Battery - Gen Component | 26 October 2021 | NSW | New Battery
Wallgrove Battery - Load Component | 26 October 2021 | NSW | New Battery
Sebastapol Solar Farm | 2 November 2021 | NSW | New Generator
Port Latta double tee | 2021-11-05 | Tasmania
Bolivar Battery 3.08 Mw - Gen Component | 16 November 2021 | SA | New Battery
Bolivar Battery 3.08 Mw - Load Component | 16 November 2021 | SA | New Battery
Bolivar Pv 8.25 Mw | 16 November 2021 | SA | New Generator
Western Downs Solar Farm | 16 November 2021 | Qld | New Generator
Davenport - Port Patterson North 275 kV line | 2021-12-06 | SA | Davenport - Port Patterson North 275 kV line was commissioned
Canunda Wf (Mw) | 9 December 2021 | SA | Change of registration - dispatch obligations on existing plant
Lake Bonney 1 Wf (Mw) | 9 December 2021 | SA | Change of registration - dispatch obligations on existing plant
Wattle Pt Wf (Mw) | 9 December 2021 | SA | Change of registration - dispatch obligations on existing plant
Dr Enelx V2 | 10 December 2021 | Victoria | New Generator - WDR
Lincoln Gap Stage 2 Wf (Mw) | 14 December 2021 | SA | New Generator
Haugton synchronous condenser | 2021-12-15 | Qld
Keilor Terminal Station 100 Mvar 220kV Reactor | 2021-12-17 | Victoria | At Keilor terminal station the 100 MVAr 220 kV reactor was commissioned on 220 kV Bus 2
Musselroe GCS | 2021-12-20 | Tasmania
Snapper Point Power Station | 21 December 2021 | SA | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.