## Details
COMMISSIONING TEST PLAN | [7 empty] | USER INSTRUCTIONS
FACILITY DETAILS
[8 empty] | 1 | This spreadsheet must be completed and submitted to Market Operations to be regarded as a valid request for a Commissioning Test Plan for a Facility.
Market Participant: | Vinalco
[8 empty] | 2 | Data entry is restricted to the areas shaded yellow and green (yellow being mandatory), which have built-in automatic checks to validate entered data.
Facility: | Muja_G1
[8 empty] | 3 | The following fields are mandatory: Market Participant, Facility, Email Address, Start and End Trading Days, Purpose of Test and Test Description. The Commissioning Test Plan will not be accepted by System Management unless these fields are completed.
Contact Details: |  | Operational |  |  | Commercial
| Email | muja.stageaboperators@synergy.net.au |  |  | pgower@vinalcoenergy.com.au
| Mobile |  |  |  | 0438788344 |  |  | 4 | For Commissioning Tests exceeding one Trading Day, please make copies of the 'DDMMYYYY' worksheet. The worksheet will automatically rename when entering the Trading Day of test within the Details worksheet.
| Phone | 97816511 |  |  | 94241771
Fax
[8 empty] | 5 | Details within the 'DDMMYYYY' worksheet (Commissioning Test Schedule) are also mandatory and required in order for the Commissioning Test Plan to be accepted by System Management.
Fuel Types: | Fuel "1" |  |  | Fuel "2" |  | Fuel "3"
| oil |  |  | coal |  |  |  | 6 | Separate Commissioning Test Plan templates are required to be completed for each Facility registered in the Wholesale Electricity Market.
TEST DETAILS | [7 empty] | 7 | Please email all completed Commissioning Test Plan templates to Market Operations; market.operations@westernpower.com.au
Associated Outage No: | [8 empty] | Commissioning Test Plan template v1.0
| START |  |  |  | END
Commissioning Test Period: | Trading Day |  | Trading Interval |  | Trading Day |  | Trading Interval
| 2014-02-14 |  | 8:00 |  | 2014-02-18 |  | 7:30
Purpose of Test: | 1. Testing and Tuning of controls associated with Boiler, Turbine and Generator Electrical systems. 2. Performance / Capability testing of new and refurbished Boiler and Turbine plant.
Test Description | 1. Progressive load raising over several days, with hold points for controls testing and tuning. 2. Load ramping over various ranges for fine tuning of the controls. 3. Testing of Ancillary Services facilities (AGC, frequency response, etc). 4. Testing of responses to contingency events including boiler and turbine runbacks.
System Under Test: | 1. Muja Unit 2 Unit and Electrical controls. 2. Muja Unit 2 Boiler, Turbine and associated plant systems.
Contingency Plan: | Each test will be conducted under close operator supervision, with plans in place specific to each test. These will include placing control loops to Manual and holding load ramps.

## 14022014
| COMMISSIONING TEST SCHEDULE | [7 empty] | COMMISSIONING TEST SCHEDULE PROFILES
TIME |  | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
Date of test | Interval start time | Active Power (MW) | Reactive Power (MVAr) | oil coal or Combination | Low, Medium or High | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
2014-02-14 | 8:00 | 0 | 0
2014-02-14 | 8:30 | 0 | 0
2014-02-14 | 9:00 | 0 | 0
2014-02-14 | 9:30 | 0 | 0
2014-02-14 | 10:00 | 10 | 1 | OIL & COAL | high |  |  | First Synchronisation
2014-02-14 | 10:30 | 10 | 1 | OIL & COAL | high
2014-02-14 | 11:00 | 15 | 1 | OIL & COAL | high
2014-02-14 | 11:30 | 15 | 1 | OIL & COAL | high
2014-02-14 | 12:00 | 15 | 1 | OIL & COAL | high
2014-02-14 | 12:30 | 15 | 1 | Coal | high
2014-02-14 | 13:00 | 15 | 2 | Coal | high
2014-02-14 | 13:30 | 15 | 2 | Coal | high
2014-02-14 | 14:00 | 15 | 2 | Coal | high
2014-02-14 | 14:30 | 15 | 2 | Coal | high
2014-02-14 | 15:00 | 15 | 2 | Coal | high
2014-02-14 | 15:30 | 15 | 2 | Coal | high
2014-02-14 | 16:00 | 15 | 2 | Coal | high
2014-02-14 | 16:30 | 15 | 2 | Coal | high
2014-02-14 | 17:00 | 15 | 2 | Coal | high
2014-02-14 | 17:30 | 15 | 2 | Coal | high
2014-02-14 | 18:00 | 15 | 2 | Coal | high
2014-02-14 | 18:30 | 15 | 2 | Coal | high
2014-02-14 | 19:00 | 15 | 2 | Coal | high
2014-02-14 | 19:30 | 15 | 2 | Coal | high
2014-02-14 | 20:00 | 15 | 2 | Coal | high
2014-02-14 | 20:30 | 15 | 2 | Coal | high
2014-02-14 | 21:00 | 15 | 2 | Coal | high
2014-02-14 | 21:30 | 10 | 2 | Coal | high
2014-02-14 | 22:00 | 10 | 2 | Coal | high
2014-02-14 | 22:30 | 5 | 2 | Coal | high
2014-02-14 | 23:00 | 5 | 2 | Coal | high
2014-02-14 | 23:30 | 2 | 2 | Coal | high |  |  | Turbine overpeed tests
2014-02-15 | 24:00
2014-02-15 | 24:30
2014-02-15 | 25:00
2014-02-15 | 25:30
2014-02-15 | 26:00
2014-02-15 | 26:30
2014-02-15 | 27:00
2014-02-15 | 27:30
2014-02-15 | 28:00
2014-02-15 | 28:30
2014-02-15 | 29:00
2014-02-15 | 29:30
2014-02-15 | 30:00
2014-02-15 | 30:30
2014-02-15 | 31:00
2014-02-15 | 31:30
| Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
| 2014-02-14 | 2014-02-18 |  | oil | Low | C1 | S1
|  |  |  | coal | Medium | C2A | S2
[5 empty] | High | C2B | S3
|  |  |  | oil & coal |  | C3A | S4
[6 empty] | C3B | S5
[6 empty] | C4 | S6
[6 empty] | C5 | S7
[6 empty] | C6 | S8
[6 empty] | C7 | S9
[6 empty] | C8 | S10
[6 empty] | C9 | S11
S12
S13

## 15022014
| COMMISSIONING TEST SCHEDULE | [7 empty] | COMMISSIONING TEST SCHEDULE PROFILES
TIME |  | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
Date of test | Interval start time | Active Power (MW) | Reactive Power (MVAr) | oil coal or Combination | Low, Medium or High | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
2014-02-15 | 8:00 | 0 | 0
2014-02-15 | 8:30 | 0 | 0
2014-02-15 | 9:00 | 0 | 0
2014-02-15 | 9:30 | 0 | 0
2014-02-15 | 10:00 | 5 | 1 | OIL & COAL | high
2014-02-15 | 10:30 | 5 | 1 | OIL & COAL | high
2014-02-15 | 11:00 | 10 | 1 | OIL & COAL | high
2014-02-15 | 11:30 | 10 | 1 | OIL & COAL | high
2014-02-15 | 12:00 | 15 | 1 | OIL & COAL | high
2014-02-15 | 12:30 | 15 | 1 | Coal | high
2014-02-15 | 13:00 | 15 | 2 | Coal | high
2014-02-15 | 13:30 | 20 | 2 | Coal | high
2014-02-15 | 14:00 | 20 | 2 | Coal | high
2014-02-15 | 14:30 | 20 | 2 | Coal | high
2014-02-15 | 15:00 | 20 | 2 | Coal | high
2014-02-15 | 15:30 | 20 | 2 | Coal | high
2014-02-15 | 16:00 | 20 | 2 | Coal | high
2014-02-15 | 16:30 | 10 | 2 | Coal | high
2014-02-15 | 17:00 | 0 | 0 |  |  |  |  | Desynch
2014-02-15 | 17:30 | 0 | 0
2014-02-15 | 18:00 | 0 | 0
2014-02-15 | 18:30 | 0 | 0
2014-02-15 | 19:00 | 0 | 0
2014-02-15 | 19:30 | 0 | 0
2014-02-15 | 20:00 | 0 | 0
2014-02-15 | 20:30 | 0 | 0
2014-02-15 | 21:00 | 0 | 0
2014-02-15 | 21:30 | 0 | 0
2014-02-15 | 22:00 | 0 | 0
2014-02-15 | 22:30 | 0 | 0
2014-02-15 | 23:00 | 0 | 0
2014-02-15 | 23:30 | 0 | 0
2014-02-16 | 24:00 | 0 | 0
2014-02-16 | 24:30 | 0 | 0
2014-02-16 | 25:00 | 0 | 0
2014-02-16 | 25:30 | 0 | 0
2014-02-16 | 26:00 | 0 | 0
2014-02-16 | 26:30 | 0 | 0
2014-02-16 | 27:00 | 0 | 0
2014-02-16 | 27:30 | 0 | 0
2014-02-16 | 28:00 | 0 | 0
2014-02-16 | 28:30 | 0 | 0
2014-02-16 | 29:00 | 0 | 0
2014-02-16 | 29:30 | 0 | 0
2014-02-16 | 30:00 | 0 | 0
2014-02-16 | 30:30 | 0 | 0
2014-02-16 | 31:00 | 0 | 0
2014-02-16 | 31:30 | 0 | 0
| Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
| 2014-02-14 | 2014-02-18 |  | oil | Low | C1 | S1
|  |  |  | coal | Medium | C2A | S2
[5 empty] | High | C2B | S3
|  |  |  | oil & coal |  | C3A | S4
[6 empty] | C3B | S5
[6 empty] | C4 | S6
[6 empty] | C5 | S7
[6 empty] | C6 | S8
[6 empty] | C7 | S9
[6 empty] | C8 | S10
[6 empty] | C9 | S11
S12
S13

## 16022014
| COMMISSIONING TEST SCHEDULE | [7 empty] | COMMISSIONING TEST SCHEDULE PROFILES
TIME |  | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
Date of test | Interval start time | Active Power (MW) | Reactive Power (MVAr) | oil coal or Combination | Low, Medium or High | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
2014-02-16 | 8:00 | 0 | 0
2014-02-16 | 8:30 | 0 | 0
2014-02-16 | 9:00 | 0 | 0
2014-02-16 | 9:30 | 0 | 0
2014-02-16 | 10:00 | 0 | 0
2014-02-16 | 10:30 | 0 | 0
2014-02-16 | 11:00 | 0 | 0
2014-02-16 | 11:30 | 0 | 0
2014-02-16 | 12:00 | 0 | 0
2014-02-16 | 12:30 | 0 | 0
2014-02-16 | 13:00 | 0 | 0
2014-02-16 | 13:30 | 10 | 1 | Coal | high
2014-02-16 | 14:00 | 15 | 1 | Coal | high
2014-02-16 | 14:30 | 20 | 2 | Coal | high
2014-02-16 | 15:00 | 27.5 | 2 | Coal | high
2014-02-16 | 15:30 | 27.5 | 2 | Coal | high | C2A |  | WPC Witness Tests
2014-02-16 | 16:00 | 27.5 | 2 | Coal | high | C2B |  | WPC Witness Tests
2014-02-16 | 16:30 | 27.5 | 60 | Coal | high | C6 |  | WPC Witness Tests
2014-02-16 | 17:00 | 27.5 | 60 | Coal | high |  | S5 | WPC Witness Tests
2014-02-16 | 17:30 | 27.5 | -20 | Coal | high | C7 |  | WPC Witness Tests
2014-02-16 | 18:00 | 27.5 | -20 | Coal | high |  | S6 | WPC Witness Tests
2014-02-16 | 18:30 | 27.5 | 2 | Coal | high
2014-02-16 | 19:00 | 27.5 | 2 | Coal | high
2014-02-16 | 19:30 | 27.5 | 2 | Coal | high
2014-02-16 | 20:00 | 27.5 | 2 | Coal | high
2014-02-16 | 20:30 | 27.5 | 2 | Coal | high
2014-02-16 | 21:00 | 27.5 | 2 | Coal | high
2014-02-16 | 21:30 | 27.5 | 2 | Coal | high
2014-02-16 | 22:00 | 27.5 | 2 | Coal | Medium
2014-02-16 | 22:30 | 27.5 | 2 | Coal | Medium
2014-02-16 | 23:00 | 27.5 | 2 | Coal | Medium
2014-02-16 | 23:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 24:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 24:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 25:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 25:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 26:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 26:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 27:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 27:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 28:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 28:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 29:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 29:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 30:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 30:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 31:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 31:30 | 27.5 | 2 | Coal | Medium
| Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
| 2014-02-14 | 2014-02-18 |  | oil | Low | C1 | S1
|  |  |  | coal | Medium | C2A | S2
[5 empty] | High | C2B | S3
|  |  |  | oil & coal |  | C3A | S4
[6 empty] | C3B | S5
[6 empty] | C4 | S6
[6 empty] | C5 | S7
[6 empty] | C6 | S8
[6 empty] | C7 | S9
[6 empty] | C8 | S10
[6 empty] | C9 | S11
S12
S13

## 17022014
| COMMISSIONING TEST SCHEDULE | [7 empty] | COMMISSIONING TEST SCHEDULE PROFILES
TIME |  | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
Date of test | Interval start time | Active Power (MW) | Reactive Power (MVAr) | oil coal or Combination | Low, Medium or High | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
2014-02-17 | 8:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 8:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 9:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 9:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 10:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 10:30 | 35 | 2 | Coal | high
2014-02-17 | 11:00 | 35 | 2 | Coal | high
2014-02-17 | 11:30 | 40 | 2 | Coal | high
2014-02-17 | 12:00 | 40 | 2 | Coal | high
2014-02-17 | 12:30 | 42 | 2 | Coal | high
2014-02-17 | 13:00 | 42 | 2 | Coal | Medium
2014-02-17 | 13:30 | 42 | 2 | Coal | Medium
2014-02-17 | 14:00 | 42 | 2 | Coal | Medium
2014-02-17 | 14:30 | 42 | 2 | Coal | Medium
2014-02-17 | 15:00 | 42 | 5 | Coal | Medium |  | S10 | WPC Witness tests
2014-02-17 | 15:30 | 42 | 5 | Coal | Medium |  | S10 | WPC Witness tests
2014-02-17 | 16:00 | 42 | 5 | Coal | Medium |  | S10 | WPC Witness tests
2014-02-17 | 16:30 | 42 | 5 | Coal | Medium |  | S10 | WPC Witness tests
2014-02-17 | 17:00 | 42 | 5 | Coal | Medium |  | S13 | WPC Witness tests
2014-02-17 | 17:30 | 42 | 5 | Coal | Medium |  | S13 | WPC Witness tests
2014-02-17 | 18:00 | 42 | 2 | Coal | Medium
2014-02-17 | 18:30 | 42 | 2 | Coal | Medium
2014-02-17 | 19:00 | 42 | 2 | Coal | Medium
2014-02-17 | 19:30 | 27.5 | 2 | Coal | Medium
2014-02-17 | 20:00 | 27.5 | 2 | Coal | Medium
2014-02-17 | 20:30 | 27.5 | 2 | Coal | Low
2014-02-17 | 21:00 | 27.5 | 2 | Coal | Low
2014-02-17 | 21:30 | 27.5 | 2 | Coal | Low
2014-02-17 | 22:00 | 27.5 | 2 | Coal | Low
2014-02-17 | 22:30 | 27.5 | 2 | Coal | Low
2014-02-17 | 23:00 | 27.5 | 2 | Coal | Low
2014-02-17 | 23:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 24:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 24:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 25:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 25:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 26:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 26:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 27:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 27:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 28:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 28:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 29:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 29:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 30:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 30:30 | 27.5 | 2 | Coal | Low
2014-02-18 | 31:00 | 27.5 | 2 | Coal | Low
2014-02-18 | 31:30 | 27.5 | 2 | Coal | Low
| Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
| 2014-02-14 | 2014-02-18 |  | oil | Low | C1 | S1
|  |  |  | coal | Medium | C2A | S2
[5 empty] | High | C2B | S3
|  |  |  | oil & coal |  | C3A | S4
[6 empty] | C3B | S5
[6 empty] | C4 | S6
[6 empty] | C5 | S7
[6 empty] | C6 | S8
[6 empty] | C7 | S9
[6 empty] | C8 | S10
[6 empty] | C9 | S11
S12
S13

## 18022014
| COMMISSIONING TEST SCHEDULE | [7 empty] | COMMISSIONING TEST SCHEDULE PROFILES
TIME |  | NET OUTPUT |  | FUEL MIX | TRIP RISK | SPECIFIC TESTS |  | COMMENTS
Date of test | Interval start time | Active Power (MW) | Reactive Power (MVAr) | oil coal or Combination | Low, Medium or High | Technical Rule, Table A11.1 | Technical Rule, Table A11.2
2014-02-18 | 8:00 | 45 | 2 | coal | Medium
2014-02-18 | 8:30 | 45 | 2 | coal | Low
2014-02-18 | 9:00 | 50 | 2 | coal | Medium
2014-02-18 | 9:30 | 50 | 2 | coal | Low
2014-02-18 | 10:00 | 55 | 2 | coal | Medium
2014-02-18 | 10:30 | 55 | 2 | coal | Medium | C2A |  | WPC witness tests
2014-02-18 | 11:00 | 55 | 2 | coal | Low | C2B |  | WPC witness tests
2014-02-18 | 11:30 | 55 | 47 | coal | Low | C6 |  | WPC witness tests
2014-02-18 | 12:00 | 55 | 47 | coal | Low |  | S5 | WPC witness tests
2014-02-18 | 12:30 | 55 | -12 | coal | Low | C7 |  | WPC witness tests
2014-02-18 | 13:00 | 55 | -12 | coal | Low |  | S6 | WPC witness tests
2014-02-18 | 13:30 | 55 | 2 | coal | Low | C9 |  | WPC witness tests
2014-02-18 | 14:00 | 55 | 2 | coal | Low |  | S13 | WPC witness tests
2014-02-18 | 14:30 | 55 | 2 | coal | Low
2014-02-18 | 15:00 | 55 | 2 | coal | Low
2014-02-18 | 15:30 | 55 | 2 | coal | Low
2014-02-18 | 16:00 | 55 | 2 | coal | Low
2014-02-18 | 16:30 | 55 | 2 | coal | Low
2014-02-18 | 17:00 | 55 | 2 | coal | Low
2014-02-18 | 17:30 | 55 | 2 | coal | Low
2014-02-18 | 18:00 | 55 | 2 | coal | Low
2014-02-18 | 18:30 | 55 | 2 | coal | Low
2014-02-18 | 19:00 | 55 | 2 | coal | Low
2014-02-18 | 19:30 | 55 | 2 | coal | Low
2014-02-18 | 20:00 | 55 | 2 | coal | Low
2014-02-18 | 20:30 | 55 | 2 | coal | Low
2014-02-18 | 21:00 | 55 | 2 | coal | Low
2014-02-18 | 21:30 | 55 | 2 | coal | Low
2014-02-18 | 22:00 | 55 | 2 | coal | Low
2014-02-18 | 22:30 | 55 | 2 | coal | Low
2014-02-18 | 23:00 | 55 | 2 | coal | Low
2014-02-18 | 23:30 | 55 | 2 | coal | Low
2014-02-19 | 24:00 | 55 | 2 | coal | Low
2014-02-19 | 24:30 | 55 | 2 | coal | Low
2014-02-19 | 25:00 | 55 | 2 | coal | Low
2014-02-19 | 25:30 | 55 | 2 | coal | Low
2014-02-19 | 26:00 | 55 | 2 | coal | Low
2014-02-19 | 26:30 | 55 | 2 | coal | Low
2014-02-19 | 27:00 | 55 | 2 | coal | Low
2014-02-19 | 27:30 | 55 | 2 | coal | Low
2014-02-19 | 28:00 | 55 | 2 | coal | Low
2014-02-19 | 28:30 | 55 | 2 | coal | Low
2014-02-19 | 29:00 | 55 | 2 | coal | Low
2014-02-19 | 29:30 | 55 | 2 | coal | Low
2014-02-19 | 30:00 | 55 | 2 | coal | Low
2014-02-19 | 30:30 | 55 | 2 | coal | Low
2014-02-19 | 31:00 | 55 | 2 | coal | Low
2014-02-19 | 31:30 | 55 | 2 | coal | Low
| Start Date | End Date |  | Fuel Mix | Trip Risk | TR Table A11.1 | TR Table A11.2
| 2014-02-14 | 2014-02-18 |  | oil | Low | C1 | S1
|  |  |  | coal | Medium | C2A | S2
[5 empty] | High | C2B | S3
|  |  |  | oil & coal |  | C3A | S4
[6 empty] | C3B | S5
[6 empty] | C4 | S6
[6 empty] | C5 | S7
[6 empty] | C6 | S8
[6 empty] | C7 | S9
[6 empty] | C8 | S10
[6 empty] | C9 | S11
S12
S13