## Index
National Transmission Network Development Plan (NTNDP)
Electronic Material – Consolidated summary 2013 Annual Planning Report (APR) augmentations
This supplement provides:
* A consolidated summary of the augmentations proposed by each JPB in their 2013 APRs and how the main grid augmentations relate to the NTNDP
Please note that the data format may need to be adjusted in order to view the data to the level of fidelity required. For example, you may need to format the cell to a more appropriate number of decimal places in some cases as desired.
Index Table
Tab Name | Content Description
Powerlink 2013 APR Projects | List of projects from the 2013 Powerlink APR1
TransGrid 2013 APR Projects | List of projects from the 2013 TransGrid APR2
AEMO 2013 APR Projects | List of projects from the 2013 AEMO Victorian APR3
ElectraNet 2013 APR Projects | List of projects from the 2013 ElectraNet APR4
Transend 2013 APR Projects | List of projects from the 2013 Transend APR5
1 | Powerlink. Available http://www.powerlink.com.au/About_Powerlink/Publications/Annual_Planning_Reports/Documents/2013/Annual_Planning_Report_2013_(complete_report).aspx
2 | TransGrid. Available http://www.transgrid.com.au/network/np/Documents/Annual%20Planning%20Report%202013.pdf
3 | AEMO. Available http://www.aemo.com.au/Electricity/Planning/~/media/Files/Other/planning/VAPR2013/Victorian_Annual_Planning_Report_2013_v2.ashx
4 | ElectraNet. Available http://www.electranet.com.au/assets/Reports-and-Papers/TAPR2013-Final-28June2013final.pdf
5 | Transend. Available http://www.transend.com.au/download/D13-28653

## Powerlink 2013 APR Projects
2013 APR Reference | Transmission Development | Limitation Addressed | 2013 APR Project Status | 2013 APR Anticipated Timing | 2013 APR Indicative Cost ($ million) | 2012 APR Reference | 2013 NTNDP | Map Reference (if applicable) | Augmentation Type
Section 5.2.1 | Construct new Strathmore–Bowen North 132 kV line. | Voltage and thermal limitations in the Bowen area. | Proposed. | Timing subject to customer commitment. | Not stated. | Section 5.2.2 | Local supply need based on future loads (uncommitted) - not within the 2013 NTNDP scope. |  | Local Network
Section 5.2.1 | String second circuit of a double circuit Stanwell–Broadsound 275 kV line. | Power transfer capability into northern Queensland is limited by thermal ratings or voltage stability limitations. Network limitations impacting reliability are not forecast to occur within the five-year outlook. Growing levels of transmission congestion are forecast with increases in demand requiring northern Queensland generators to be constrained on. | Proposed. | Timing subject to customer commitment. | Not stated. | Section 5.2.2 | Limitations of power transfer capability into NQ have been identified in the 2013 NTNDP. | T-Q1 | Main Grid
Section 5.2.1 | Following the string of the second circuit of a double circuit Stanwell–Broadsound 275 kV line, voltage and thermal limitations may reoccur. Options to address the emerging limitations could vary depending on the level of load commitment. • installation of shunt capacitors • SVC at existing northern Queensland substations • Establish substations to sectionalise CQ–NQ grid sections • installation of series capacitors on the CQ–NQ grid sections, and/or • the construction of new transmission lines. | There have been several proposals for large mining and metal processing or other industrial loads in northern Queensland. These loads include large coal mine developments in Galilee Basin, expansion or development of coal mines and upstream liquefied natural gas (LNG) processing load in the Bowen Basin. The development status of these loads is not yet at the stage that they can be included (either wholly or in part) in the medium economic forecast of the APR. These loads could be up to 1,670MW. Thermal and voltage limitations will occur if even a portion of these new loads commit. | Proposed. | Timing subject to customer commitment. | Not stated. | Section 5.2.3 | Possible future project subject to customer commitment- not captured in the 2013 NTNDP. | T-Q1 | Main Grid
Section 5.2.1 | Install new Pioneer Valley 100 MVA 132/66 kV transformer to replace existing 40 MVA 132/66 kV transformer. | Supply to the Pioneer Valley area. | Committed. | Summer 2013/14 | Not stated. | Section 5.2.2 and Section 3.2 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.2.2 | Establishment of two new 132kV feeder bays at Pioneer Valley Substation to turn-in the Nebo to Mackay 132kV circuit. | Voltage control in the Mackay area. | Proposed. | Summer 2015/16 | 3 - 5 | Section 5.2.2 | This local voltage control assessment is not within the 2013 NTNDP scope. However, in the 2013 NSCAS assessment, the proposed project was considered to provide additional reactive power support. |  | Local Network
Section 5.2.1 | Supply to Bowen Basin coal mining area. Recommended Solution: 1. install two 132kV capacitors at Dysart Substation and one 132kV capacitor at Moranbah and Newlands substations by summer 2013/14; and 2. network support services, with Energy Developments Limited (EDL), between 2014 and 2016. | Voltage and thermal limitations in the Bowen Basin coal mining area due to potential mining growth. Following the recommended augmentations voltage and thermal limitations are forecast to reoccur from summer 2016/17. A possible solution to the identified limitations is to install a second 275/132kV transformer at Strathmore Substation and construction of a 132kV transmission line, capable of 275kV upgrade, from Nebo Substation to the Moranbah area. | Committed. | 2013/14 to 2016 | Network solution - 12.3 Network support - 11.5 | Section 5.2.2 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.2.1 | Supply to Bowen Basin coal mining area. Options include: • installation of a second 275/132kV transformer at Strathmore Substation; and • construction of a 132kV transmission line (capable of 275kV upgrade) from Nebo Substation to the Moranbah area | Following the recommended augmentations above voltage and thermal limitations are forecast to reoccur from summer 2016/17. | Proposed. | Summer 2016/17 | Not stated. | Section 5.2.4 | This limitation does not arise in the 2013 NTNDP as uncommitted customer loads are not modelled. However, the limitations are likely to appear if significant load growth occurs in the Bowen Basin area. |  | Local Network
Section 5.2.1 | Install a 132 kV capacitor bank at Proserpine Substation. | Voltage control in Proserpine area. | Proposed. | Summer 2017/18 | 2 - 4 | Section 5.2.2 | This local voltage control assessment is not within the 2013 NTNDP scope. However, in the 2013 NSCAS assessment, the proposed project was considered to provide additional reactive power support. |  | Local Network
Section 5.2.2 | Construct new Calvale–Stanwell 275 kV double circuit line. | Thermal limitations on the transfer capability between Central West and Gladstone regions. | Committed. | Summer 2013/14 | Not stated. | Section 5.2.3 and Section 3.2 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.2 | Connect third Lilyvale–Blackwater 132 kV line. | Thermal limitations in the Blackwater area during a critical contingency. | Committed. | Summer 2012/13 | Not stated. | Section 5.2.3 and Section 3.2 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.2.3 | Build Western Down–Halys 275 kV lines and Western Down and Halys 275 kV substations. | Voltage, transient and thermal limitations across the Bulli to South West Queensland grid section. | Committed. | Summer 2013/14 | Not stated. | Section 5.2.4 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.3 | Construct Columboola–Wandoan South 275 kV line, Columboola–Western Downs 275 kV line, Wandoan South 275 kV substation, and Columboola 275 kV substation. | Thermal limitations due to new industrial load growth. | Committed. | From Winter 2013 to Winter 2014 | Not stated. | Section 5.2.4 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.3 | Installation of a combination of capacitor banks and a SVC or construction of 275kV transmission lines in the Surat Basin. | Following the recent commitment of additional load by multiple proponents, voltage stability limitations may occur during critical contingencies on the network supplying the Surat Basin north west area. | Proposed. | Summer 2016/17 | Not stated. | Section 5.2.4 | Dynamic voltage stability assessment is not within the 2013 NTNDP scope. However, in the 2013 NSCAS assessment, the proposed project was considered to provide additional dynamic reactive power support. | T-Q3 | Main Grid
Section 3.2 | Install new Wondoan 132/66 kV transformer. | Supply to the Wondoan area. Following deferral of a number of new load developments on the Ergon Energy network Powerlink and Ergon Energy have suspended work on this connection. | Suspended. |  | Not stated. | Section 5.2.4 | Local supply/network need - not within the 2013 NTNDP scope. |  | Local Network
Section 5.2.4 | Increase of central Queensland to south Queensland transfer limit. Possible solutions include: • Construct additional 275 kV transmission line between central and southern Queensland • Augment QNI and/or Terranora Interconnector • Special protection Scheme to increase power transfer capability | Following a credible contingency, there may be insufficient generation within southern Queensland and via northerly power transfers from QNI and Directlink to allow AEMO to return the power system within the Queensland region to a secure state while maintaining reliable supply to all customers. Under these conditions, the maximum power transfer between central and southern Queensland and between New South Wales (NSW) and Queensland is limited by transient instability. | Proposed. | Summer 201718 (timing subject to generation commitment) | 170 - 360 | Section 5.2.5 | Limitations between CQ and SQ could arise under certain generation dispatch scenarios and outage conditions. | T-Q2 | Main Grid
Section 5.2.4 | Improvement of supply within the southern Brisbane area. Options include: • Establishment of a Larapinta 275/110 kV substation and Rocklea 275kV bus and 275/110kV transformer augmentation • Establishment of a Nudgee 275/110 kV substation and establishment of a Larapinta 275/110 kV substation • Establish Upper Kedron 275/110 kV substation and Larapinta 275/110 kV Substation establishment | Thermal limitations in the Energex 110 kV network, followed by thermal limitations in the Rocklea 275/110 kV transformers, and 275 kV and 110 kV network supplying this area are forecast to occur. Energex and Powerlink are jointly reviewing the credible options identified in the RFI taking into account the impact of the revised load forecast on the timing of network limitations. | Proposed. | Timing for Powerlink limitations are beyond the five-year APR outlook. The actual timing of the forecast limitations may be influenced by ongoing joint planning with Energex. | 70 - 128 | Section 5.2.5 | DNSP supply need based on future load growth and sub transmission network limitations - the 2013 NTNDP analysis indicates network congestion in the SEQ zone as demand continues to increase. |  | Local Network
Section 5.2.4 | Improvement of supply within the southern Brisbane area. The 275 kV network including the circuit from Blackwall to South Pine. | With demand growth, thermal limitations are forecast to occur during a critical contingency in the 275 kV network that includes the Blackwall–South Pine 275 kV circuit. | Deferred. | Timing for Powerlink limitations are beyond the five-year APR outlook. The actual timing of the forecast limitations may be influenced by ongoing joint planning with Energex. |  | Section 5.2.5 | Limitation arises in the 2013 NTNDP expansion plan. | T-Q4 | Main Grid
Section 5.2.4 | Reinforcement of supply within southern Brisbane, CBD, and eastern suburbs area. | Thermal limitations during critical network conditions. | Proposed. | Timing beyond the five-year APR outlook. | Not stated. | Section 5.2.5 | Limitation arises in the 2013 NTNDP expansion plan. | T-Q5 | Main Grid
Section 5.2.4 | Augment supply to the South East Queensland area by building a new 500 kV Halys–Blackwall double circuit line (initially operated at 275 kV). | Voltage and thermal limitations in the south east Queensland network. | Proposed. | Timing beyond the five-year APR outlook. | Not stated. | Section 5.2.5 | Limitations between SEQ and SWQ could arise if large amount of new generation currently modelled in SEQ is located in SWQ. | T-Q6 | Main Grid
Section 5.2.4 | Modification of transformer connection arrangements at South Pine substation. | Supply to the north Brisbane area. | Proposed. | Timing beyond the five-year APR outlook. | Not stated. | Section 5.2.5 | Local network reconfiguration - not within the 2013 NTNDP scope. |  | Local Network
Section 5.2.4 | Install two new Ashgrove West 80 MVA 110/33 kV transformers to replace existing 60 MVA 110/33 kV transformers. | Supply to the Ashgrove West area. | Committed. | Summer 2013/14 | Not stated. | Section 5.2.5 and Section 3.2 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.5 | Kumerunga substation replacement. | Condition based replacement. | Proposed. | Summer 2017/18 | 10 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Cairns 132/22 kV transformer replacement. | Condition based replacement. | Proposed. | Winter 2018 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Ross Reactor replacement | Condition based replacement. | Proposed. | Summer 2014/15 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Ingham South 132/66 kV transformer replacement. | Condition based replacement. | Proposed. | Winter 2018 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Garbutt 132/66 kV transformer replacement. | Condition based replacement. | Proposed. | Summer 2018/19 | 15 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Townsville South substation Replacement. | Condition based replacement. | Proposed. | Summer 2018/19 | 15 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Collinsville to Proserpine 132 kV line replacement. | Condition based replacement. | Proposed. | Winter 2016 | 20 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Mackay substation replacement. | Condition based replacement. | Proposed. | Summer 2016/17 | 25 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Nebo substation replacement. | Condition based replacement. | Proposed. | Summer 2018/19 | 30 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Moura substation replacement. | Condition based replacement. | Proposed. | Summer 2015/16 | 25 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Rockhampton substation replacement. | Condition based replacement. | Proposed. | Winter 2016 | 20 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Blackwater substation replacement. | Condition based replacement. | Proposed. | Summer 2016/17 | 15 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Callide A substation replacement. | Condition based replacement. | Proposed. | Summer 2016/18 | 30 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Bouldercombe substation replacement. | Condition based replacement. | Proposed. | Summer 2017/18 | 30 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Lilyvale 132/66kV transformer replacement. | Condition based replacement. | Proposed. | Summer 2017/19 | 20 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.6 | Baralaba substation replacement. | Condition based replacement. | Proposed. | Winter 2018 | 35 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.7 | Dysart substation replacement. | Condition based replacement. | Proposed. | Summer 2018/19 | 35 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Loganlea 110/33kV transformer replacement. | Condition based replacement. | Proposed. | Summer 2017/18 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.5 | Mudgeeraba substation replacement. | Condition based replacement. | Proposed. | Winter 2018 | 60 | Section 5.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement

## TransGrid 2013 APR Projects
2013 APR Reference | Transmission Development | Limitation Addressed | 2013 APR Project Status | 2013 APR Anticipated Timing | 2013 APR Indicative Cost ($ million) | 2012 APR Reference | 2013 NTNDP | Map Reference (if applicable) | Augmentation Type
Section 5.2.1 | Armidale SVC: Power Oscillation Damping Control Comprehensive testing of the installed power oscillation damping control facility expected to be completed in 2013. | Increase capacity of the QNI interconnector | Committed. | 2013 | Not stated. | Section 5.2.1 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.2 | Western Sydney Supply Project: • Sydney to Holroyd double circuit 330kV lines • New Holroyd and Rookwood Rd substations • Two 330kV cables between Holroyd and Rookwood Rd | Increase capacity of supply to Inner Sydney metropolitan area. | Committed. | Early 2014 | Not stated. | Section 5.2.2 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.3 | Upper Tumut Switching Station Rehabilitation Replacement of high voltage equipment and secondary systems | Condition based replacement. | Committed. | 2014 | Not stated. | Section 5.2.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 5.2.4 | Supply to the Lower Mid North Coast: • Single circuits between Tomago and Tarro area • Double 132kV circuit Tarro to Stroud • 132kV circuits Tomago to Stroud and Tomago Brandy Hill | Increase transmission capacity to Lower Mid North Coast. | Committed. | Late 2013 | Not stated. | Section 5.2.9 Second stage of the project is not being considered at this stage after new demand forecasts. | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.5 | Reinforcement of Supply within the Sydney Inner Metropolitan Area: • 330kV cable link Beaconsfield and Haymarket | Relieve limitations within inner Sydney metropolitan area. | Committed. | 2013 | Not stated. | Section 5.2.2 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.6 | Voltage Control in the Snowy area: • 3x150MVAr reactors in Yass and Murray substations | NSCAS capability gap in southern NSW. | Committed. | Mid 2014 | Not stated. |  | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.7 | Sydney South-Beaconsfield West 330 kV Cable 41 Capacity, Sydney South Works Rearranging the 330 kV busbar at Sydney South to provide operational flexibility of the Sydney South series reactors to allow switching to restrict the flow on 41 cable during a critical contingency event | Reduction Sydney South-Beaconsfield West 330 kV Cable 41 capacity | Committed. | Summer 2016/17 | Not stated. | Section 5.3.6 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.10 | Committed Transformer Replacements and Upgrades • Replace No.1 and No. 2 330/132 kV transformers at Wallerang • Replace 330/132 kV transformer at Sydney East • Replace three 132/33 kV transformers at Yanco • Replace two 132/33 kV transformers at Griffith • Replace three 45 MVA 132/66 kV transformers at Narrabri with two 60 MVA transformers released from Coffs Harbour • Replace two of three 330/132 kV transformers at Newcastle. One 330/132 kV transformer to be permenantly retired • Replace No.1 132/66 kV transformer at Yass | Condition based replacement. | Committed. | 2014 Early 2014 2014 2015 July 2013 2013, and Lat e 2016 December 2013 | Not stated. | Section 5.3.13 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.2.11 | Committed Capacitor Bank Replacements and Upgrades: • New 200MVAr Cap Bank at Sydney South • 80MVAr to 120MVAr upgrade at Canberra • New 80MVAr cap bank at Yass | Maintain adequate power transfer and voltage control capability. | Committed. | Late 2013 2014 2014 | Not stated. | Section 5.3.14 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.3.1 | Redevelopment of Orange 132/66 kV Substation: • Remove 132kV equipment • Replace 66kV equipment • New 66kV capacitor | Condition based replacement. | Committed. | 2017 | Not stated. | Section 5.3.2 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.3.2 | Development of Southern Supply to the ACT: • Establish Wallaroo switching station • Establish 330kV circuits from Wallaroo to Yass and to Canberra • Connect to Canberra-Williamsdale line at Wallaroo | To meet requirement of the Act government. | Committed. | Within five years. | Not stated. | Section 5.3.3 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.3.3 | Supply to the Forster/Tuncurry Area: • Development of 132/66kV substation • Connection to Tomago-Taree 132kV line | Increase capacity. | Committed. | Dependant on changes in load forecast. | Not stated. | Section 6.1.3 Regulatory process has been completed | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.3.4 | Development of real-time monitoring capabilities of selected transmission lines | Increase thermal capability of selected lines under certain conditions | Committed. | Progressively through 2014 | Not stated. | Not referred. | No impact on 2013 NTNDP studies |  | Main Grid
Section 5.3.5 | Works to enable Essential Energy to establish a 132/66 kV substation in the Kew and Laurieton areas | Condition based issues in backup supply | Committed. | 2013/14 | Not stated. | Section 6.3.9 | Limitations in the distribution networks - not within the 2013 NTNDP scope. |  | Local Network
Section 5.3.6 | Reinforcement of Voltage Control in Northern NSW: • 2x200 MVAr Cap banks at Armidale | Capacity of the Northern NSW and South Western Queensland network to facilitate power transfer between QLD and NSW | Committed. | Within five years. | Not stated. | Section 5.2.3 | Capacitors required to increase QLD-NSW transfer capability. The least cost modelling did not identify the need to increase the QLD-NSW transfer capability. | T-N1 | Main Grid
Section 6.3.12 | Supply to Far North NSW: • Uprate the Armidale–Coffs Harbour 132 kV line (96C) to a conductor operating temperature of 100ºC (completed May 2011); • Construct a new 330 kV line between Dumaresq 330 kV Switching Station and Lismore 330/132 kV Substation; • Provide reactive equipment at Lismore and Dumaresq; and • Provide 330 kV switchgear at Dumaresq and Lismore to connect the new line and the reactive equipment. | Supply to the far north coast area of NSW is limited by the thermal ratings of the 132 kV lines on outage of the Armidale–Coffs Harbour 330 kV line. | Proposed. | Not within 5-years. | Not stated. | Section 5.3.1 | Limitation in the northern NSW 132 kV network arises in the 2013 NTNDP expansion plan during 2023-24 to 27-28. | T-N2 | Main Grid
Section 6.2.6 | Supply to the Tomerong/Nowra Area: • Construction of a new 330/132 kV substation; • Construction of a short section of double circuit 330 kV transmission line from the new substation to TransGrid’s Kangaroo Valley to Capital Wind Farm line west of the substation; • Construction of short sections of 132 kV transmission line from the new substation to Endeavour Energy’s 132 kV lines to the east; • Connections to enable the new 330 kV and 132 kV circuits to be formed; | To meet supply limitations in the Tomerong/Nowra area. | Proposed. | Within 5-years. | Not stated. | Section 5.3.4 | Local supply issue - not captured in the 2013 NTNDP. | T-N4 | Main Grid
Section 6.3.4 | Capacity of the Marulan–Avon, Marulan–Dapto and Kangaroo Valley–Dapto Lines. It is necessary to uprate the Marulan–Avon, Marulan–Dapto and Kangaroo Valley–Dapto 330 kV lines to accommodate higher flows to the Sydney/Wollongong area from the south of NSW. | To accommodate higher flows to the Sydney/Wollongong area from the south of NSW due to possible development of generation in southern NSW. | Proposed. | Not within 5-years. | Not stated. | Section 5.3.7 | The need to increase rating of Marulan – Avon, Marulan – Dapto and Kangaroo Valley – Dapto Lines does not arise during the NTNDP outlook period. | T-N5 | Main Grid
Section 6.3.11 | Supply to Southern Sydney. Three conceptual network options to address the immediate system needs are: • Development of an additional single circuit connection between Kemps Creek and Liverpool; • Development of an additional single circuit connection between Kemps Creek and Sydney South; and • Uprating of the Sydney West–Liverpool and Kemps Creek–Sydney South transmission lines through the use of high temperature conductors. | The Sydney West-Liverpool, Kemps Creek-Sydney South, Wallerawang-Sydney South, and Wallerawang-Ingleburn 330 kV lines | Proposed. | Not within 5-years. | Not stated. | Section 6.1.1 | The need to increase supply to southern Sydney does not arise during the NTNDP outlook period. | T-N6 T-N8 | Main Grid
Section 6.3.11 | Supply to Southern Sydney. Two additional circuits between Kemps Creek/Sydney West and Sydney South. | Supply to the greater Sydney area following a forced outage of one of a 330 kV circuit under high system load conditions. | Proposed. | Not within 5-years. | Not stated. | Section 6.1.1 | The need to increase supply to southern Sydney does not arise during the NTNDP outlook period. | T-N6 | Main Grid
Section 6.1.1 | Capacity of the Snowy to Yass/Canberra 330 kV System. At this stage the preferred option may comprise the combination of: • The implementation of a system protection scheme; and • Either the upgrading of the No. 01 and No. 02 330 kV lines or the installation of power flow control plant at Yass and/or Canberra. • One new 200 MVAr 330 kV capacitor bank at Canberra; and • One new 120 MVAr 132 kV capacitor bank at Canberra. | Capability for the import of power from the south at Snowy and Uranquinty or from Victoria. | Proposed. | Within 5-years. | Not stated. | Section 6.1.2 | The need to increase capacity of the network to import power from the Snowy region, or Uranquinty, or from Victoria does not arise in the NTNDP outlook period. | T-N10 | Main Grid
Section 6.1.2 | Voltage Levels at Kangaroo Valley Preliminary investigations indicate there are three viable augmentation options: • A new 330 kV shunt reactor at Kangaroo Valley; • A new 330 kV shunt reactor at the new Tomerong site (expected late 2015); and • Uprating the Kangaroo Valley transformer bushings for +10% over voltage. | High voltage in the Canberra–Kangaroo Valley system during periods of light load. | Proposed. | Within 5-years. | Not stated. | Section 6.1.5 | The need for reactive power plant in the Snowy region is addressed in the NSCAS section of the 2013 NTNDP. |  | Local Network
Section 6.1.3 | Supply to the Gunnedah, Narrabri and Moree Areas. Options available to address these limitations include: • Construction of a 132 kV line from Tamworth to Gunnedah possibly on the route of the recently dismantled Tamworth–Gunnedah 66 kV line No. 875; • Construction of a 330 kV line (initially operating at 132 kV) from Tamworth to the Narrabri area; • Construction of a 330 kV line from Dumaresq to a new 330/132 kV substation near Moree; • Uprating of 132 kV lines in the area; and • Demand management and/or local generation. | The capacity of the transmission system supplying the Gunnedah, Narrabri and Moree areas is limited by thermal constraints on outage of critical 132 kV lines. Expanded mines in the Gunnedah area have been proposed. Should those proceed, the limitations would be exacerbated. | Proposed. | Within 5-years. | Not stated. | Section 6.1.6 | The transmission system supplying the Moree area may need upgrading if there is a significant load growth in the area. |  | Local Network
Section 6.1.4 | Murraylink Runback Control System. | The capability of Murraylink to transmit power from Victoria into South Australia. | Proposed. | Within 5-years. | Not stated. | Section 6.1.8 | NSW Murraylink runback scheme was designed to facilitate VIC import from NSW, and VIC to SA transfer via Murraylink. NSW runback scheme is not operational due to issues related to the communication links. AEMO will follow up with TransGrid and APA(owner of Murraylink) on issues related to the runback scheme. |  | Main Grid
Section 6.1.5 | Smart Grid Applications Smart Grid Applications. | TransGrid aims to maximise the capability of the existing network through the use of non-network alternatives, deferring as much as possible any large-scale network developments. | Proposed. | Within 5-years. | Not stated. | Section 6.1.9 | There is a significant potential gain in implementing smart grid solutions. AEMO will work with TransGrid to ensure that the impact of any future smart gird developments is considered in future network development plans. |  | Local Network
Section 6.1.6 | Supply to the Sydney Inner Metropolitan Area. A number of options are presently being investigated, including provision of one or more 330 kV circuits to the inner metropolitan area from: • Sydney South; • Sydney East; • Sydney North; and • Rookwood Road. At this stage installation of a new 330 kV cable from Rookwood Road to Beaconsfield West is expected be the most cost effective option. | There are four factors impacting the ability of the network to supply the forecast demand in this area: • Planned retirement of a number of 132 kV cables within Ausgrid’s network that are approaching the end of their serviceable lives. • De-rating of Sydney South-Beaconsfield West 330 kV cable. • De-rating of Ausgrid 132kV cables. • Forecast load growth within the Sydney inner metropolitan area. | Proposed. | Within 5-years. | Not stated. | Section 6.1.11 | Due to the noted cable derating and retirement issues, it is likely that there is a need to augment supply to the Sydney metropolitan area. | T-N7 | Main Grid
Section 6.1.8 | Increase the bay ratings at Newcastle 330/132 kV Substation for lines 960 and 961 Removal of secondary systems limitations. | Secondary systems limitations. | Proposed. | 2015 | 0.15 | Section 6.1.12 | The need to increase bay ratings at the Newcastle substation does not arise during the NTNDP outlook period. |  | Asset Replacement
Section 6.1.9 | Burrinjuck 132 kV Substation renewal Condition based renewal. | Condition based replacement. | Proposed. | 2016 | 11 | Section 6.1.13 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Canberra 330/132 kV Substation No. 2 transformer Condition based replacement. | Condition based replacement. | Proposed. | 2016 | 13 | Section 6.1.13 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Cooma–Munyang 132 kV line rebuild Condition based replacement. | Condition based replacement. | Proposed. | 2016 | 10 | Section 6.1.13 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Coffs Harbour–Koolkhan line (#96H) pole replacements Condition based replacement. | Condition based replacement. | Proposed. | 2016 | 15 | Section 6.1.13 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Uranquinty–Yanco line (#99F) pole replacements Condition based replacement. | Condition based replacement. | Proposed. | 2016 | 7 | Section 6.1.13 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.7 | Supply to Beryl Options to relieve the limitation include: • Installation of additional capacitors at Beryl or within Essential Energy’s network supplied from Beryl; • Establishment of a second Wellington– Beryl 132 kV line, possibly utilising part of the route of an existing Essential Energy 66 kV line; • Establishment of a 330/132 kV substation near Beryl, supplied from the Wollar – Wellington 330 kV line; or • Demand management or local generation. At this stage, the preferred option is the establishment of a 330/132 kV substation near Beryl. | During outages of the Wellington–Beryl 132 kV line at times of high load, unacceptably low voltages can occur at Beryl. | Proposed. | Within 5-years. | Not stated. | Section 6.2.1 | The transmission system supplying the Beryl area may need upgrading if there is a significant load growth in the area. |  | Local Network
Section 6.3.13 | Supply to Mudgee Essential Energy has proposed to convert the tee connection to a loop-in connection. | To meet reliability and security requirements for the supply to Mudgee. | Proposed. | Not within 5-years. | Not stated. | Section 6.2.2 | The transmission system supplying the Mudgee area may need upgrading if there is a significant load growth in the area. |  | Local Network
Section 6.2.1 | Supply to Tumut/Gadara An expansion of the Visy mill at Gadara has been completed. The need to augment supply to the area will be determined in consultation with Visy and in consideration of the level of service it requires. | An expansion of the Visy mill at Gadara has been completed. The need to augment supply to the area will be determined in consultation with Visy and in consideration of the level of service it requires. | Proposed. | Within 5-years. | Not stated. | Section 6.2.3 | The transmission system supplying the Gadara area may need upgrading if there is a significant load growth in the area. |  | Local Network
Section 6.2.2 | NSW to Queensland Transmission Capacity. The Project Specification Consultation Report includes the following augmentation options: • Series compensation of the interconnecting 330 kV lines between Armidale, Dumaresq and Bulli Creek; • Line series compensation and a second Armidale SVC; • A new SVC at Armidale; • Augmentations to protection systems to improve line fault clearing times; • A second HVAC interconnection at 330 kV between Bayswater and the Queensland Western Downs; • A new Armidale–Dumaresq–Bulli Creek HVAC 330 kV development; • A second HVAC interconnection at 500 kV; • A HVDC back-to-back scheme in QNI; and • A braking resistor in the Hunter Valley. | Capacity of the Northern NSW and South Western Queensland network to facilitate power transfer between QLD and NSW | Proposed. | Within 5-years. | Not stated. | Section 6.2.4 | The least cost modelling does not identify the need to increase the NSW-QLD transfer capability. | T-N1 | Main Grid
Section 6.3.5 | Loading of the Wallerawang–Sydney South/Ingleburn 330 kV Lines. TransGrid proposes to review the potential loading conditions and rating of the terminal equipment to determine the need for uprating of the plant. | The double circuit 330 kV line (circuits 76 and 77) from Wallerawang across the Blue Mountains to Sydney South and Ingleburn can be heavily loaded at times of high western and northern generation. There is potential for the loading on the line to reach the rating of the terminal equipment under future generation development scenarios. | Proposed. | Not within 5-years. | Not stated. | Section 6.2.5 | The need to increase the capability of the Wallerawang – Sydney South/Ingleburn 330 kV lines does not arise during the NTNDP outlook period. | T-N6 | Main Grid
Section 6.2.3 | Yass–Bannaby and Yass–Marulan 330 kV Lines: The preferred short-term network development option for upgrading the power transfer capability is the upgrading of the existing No. 61 line to higher thermal rating. Relatively minor work on a limited number of spans is required. | Capability for the import of power from the south at Snowy and Uranquinty or from Victoria. Capability for the export of power to Victoria. | Proposed. | Within 5-years. | Not stated. | Section 6.2.6 | The need to increase the capability of the Yass – Bannaby and Yass – Marulan 330 kV lines does not arise during the NTNDP outlook period. | T-N10 | Main Grid
Section 6.2.3 | Yass–Bannaby and Yass–Marulan 330 kV Lines: • A 500 kV link from the Bannaby area to Yass which could be formed by reconstructing one of a number of 330 kV single circuit lines; • A 500 kV link from Yass to the Wagga area; and • Further interconnection development from the Wagga area to Victoria. | Capability for the import of power from the south at Snowy and Uranquinty or from Victoria. Capability for the export of power to Victoria. | Proposed. | Within 5-years. | Not stated. | Section 6.2.6 | The need to increase the capability of the Yass – Bannaby and Yass – Marulan 330 kV lines does not arise during the NTNDP outlook period. | T-N10 | Main Grid
Section 6.2.4 | Tamworth and Armidale 330 kV Switchyards - It is proposed to develop new 330 kV switchyards with a breaker and- a-half arrangement to make these switchyards compatible with other major main system switchyards. These developments would be staged over the middle part of the decade. | The existing busbar arrangements are considered to have a lower level of reliability than is required for this critical part of the NSW system. | Proposed. | Within 5-years. | Not stated. | Section 6.2.8 | The need to increase reliability at the Tamworth and Armidale switch yards was not assessed in the 2013 NTNDP. |  | Asset Replacement
Section 6.2.5 | Supply to the Darlington Point Area. TransGrid is considering a number of options: • Development of the 330 kV network to the Darlington Point area; • Reactive support; • Development of the 330 kV network to the Finley area; • Development of the 220 kV network from the Victorian system, across the Murray River, to support the area; • Further development of the 132 kV system in the area; • Non-network support such as load reduction at times of high load or embedded generation; and • Extension of the 500 kV system south from the Wagga area, which may form part of an interconnection with Victoria such as via NEMLink. At this stage a 330 kV line development between Wagga and Darlington Point is the preferred network augmentation. | Reliability of supply to the Darlington Point Area. | Proposed. | Within 5-years. | Not stated. | Section 6.2.9 | Even though this limitation is not within the 2013 NTNDP scope, the need to augment the supply to the Darlington point area was observed. The need and timing will depend on local demand growth. |  | Local Network
Section 6.2.7 | Tumut 132/66 kV Substation switch bays One 66 kV switch bay. | Possible distribution augmentation. | Proposed. | Within 5-years. | Not stated. | Section 6.2.10 | Limitations in the distribution networks - not within the 2013 NTNDP scope. |  | Local Network
Section 6.2.7 | Wellington 330/132 kV Substation switch bays One 132 kV switch bay and a short section of double circuit line construction. | Possible distribution augmentation. | Proposed. | Within 5-years. | Not stated. | Section 6.2.10 | Limitations in the distribution networks - not within the 2013 NTNDP scope. |  | Local Network
Section 6.2.7 | Lismore 330/132 kV Substation switch bays Two 132 kV switch bays. | Possible distribution augmentation. | Proposed. | Within 5-years. | Not stated. | Section 6.2.10 | Limitations in the distribution networks - not within the 2013 NTNDP scope. |  | Local Network
Section 6.2.7 | Vineyard 330/132 kV Substation switch bays 132 kV switch bays. | Possible distribution augmentation. | Proposed. | Within 5-years. | Not stated. | Section 6.2.10 | Limitations in the distribution networks - not within the 2013 NTNDP scope. |  | Local Network
Section 6.2.7 | Wagga North 132/66 kV Substation switch bays 132 kV switch bay. | Possible distribution augmentation. | Proposed. | Within 5-years. | Not stated. | Section 6.2.10 | Limitations in the distribution networks - not within the 2013 NTNDP scope. |  | Local Network
Section 6.2.9 | Canberra Capacitor: A new 120 MVAr 132 kV bank and a new 200 MVAr 330 kV bank associated with an upgrade of the Snowy to Yass/Canberra system, see Section 6.1.2. | Capability for the import of power from the south at Snowy and Uranquinty or from Victoria. | Proposed. | Within 5-years. | Not stated. | Section 6.2.12 | The need to increase capacity of the network to import power from the Snowy region, or Uranquinty, or from Victoria was does not arise during the NTNDP outlook period. | T-N10 | Main Grid
Section 6.3.1 | Hunter Valley–Tamworth–Armidale 330 kV System: TransGrid is considering upgrading the Liddell–Tamworth 330 kV lines to a higher design temperature. | Supply to Northern NSW. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.1 | The need to increase the capacity of the Hunter Valley – Tamworth – Armidale 330 kV lines does not arise during the NTNDP outlook period. | T-N3 | Main Grid
Section 6.3.1 | Hunter Valley–Tamworth–Armidale 330 kV System: In the longer term it is planned to replace some of the single circuit 330 kV lines with double circuit 330 kV or 500 kV lines. Whilst a 330 kV system development may provide adequate capability here is potential for extension of the 500 kV system north of the Hunter Valley and extension of this system into Queensland to provide a high level interconnection development. | Supply to Northern NSW. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.1 | The need to increase the capacity of the Hunter Valley – Tamworth – Armidale 330 kV lines doe not arise during the NTNDP outlook period. | T-N3 | Main Grid
Section 6.3.2 | Kemps Creek 500/330 kV Transformer Augmentation: Replacing the fixed ratio transformers with transformers with on-load tap changing facilities. | The voltage levels on the 330 kV system in the Sydney area. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.2 | Detailed reactive power studies were not conducted in the 2013 NTNDP. | T-N7 | Main Grid
Section 6.3.2 | Kemps Creek 500/330 kV Transformer Augmentation: There is a future need for additional 500/330 kV transformer capacity in Sydney. This may be achieved by additional transformers at Kemps Creek or at other sites. The need for additional transformers was identified in most scenarios in the 2010 NTNDP. | Supply to the Sydney area. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.2 | The need to increase supply into the Sydney area does not arise within the NTNDP outlook period. | T-N7 | Main Grid
Section 6.3.3 | Further Development of Supply to the Newcastle–Sydney–Wollongong Area: • A 500 kV line between Bannaby and Sydney, which is the most effective solution to both line rating and voltage control issues under a large set of future scenarios of load and generation development; and • A 500 kV line between the Hunter Valley and the coast via the Newcastle area, which is the preferred development for generation expansion scenarios that lead to significantly increased power flow from the north of the State towards Sydney | Supply to the Newcastle – Sydney – Wollongong area. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.3 | The need to increase capability main circuits in the Newcastle – Sydney – Wollongong area does not arise during the NTNDP outlook period. | T-N5 T-N8 | Main Grid
Section 6.3.6 | Supply to Sydney East Conversion of the line which is operated at 132 kV to its design 330 kV operation. | Supply to Sydney East. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.4 | The need to increase supply to the Sydney East supply point does not arise during the NTNDP outlook period. | T-N7 | Main Grid
Section 6.3.7 | NSW–South Australia Interconnection: There is potential for the development of a direct interconnection between South Australia and NSW. This interconnection could be developed as a 500 kV AC link or a HVDC link or a combination of both. | Market benefits in allowing transfer capacity between NSW and SA. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.5 | The least cost modelling does not identify the need to increase interconnector capability between NSW and VIC. |  | Main Grid
Section 6.3.8 | NSW – Victoria Interconnection: • Upgrading of Victorian lines and transformers, SVC installation and a braking resistor to improve the Victorian export capability; • Reactive support in the Jindera area, line series compensation of the Lower Tumut – Wagga – Jindera system or other power flow control devices to improve the Victorian import capability; and • Major 330 kV line development to provide a significant increase in the Victorian import capability | Market benefits in increasing transfer capacity between NSW and VIC. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.6 | The least cost modelling does not identify the need to increase interconnector capability between NSW and VIC. |  | Main Grid
Section 6.3.9 | Capacity of the Connections between the Central Coast Power Stations. A rearrangement of 330 kV connections in the Central Coast system and installation of a line series reactor is identified in the 2010 NTNDP to address line loading limitations under three of the ten NTNDP scenarios. | Overloading of circuits in the central coast area. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.7 | The 2013 NTNDP analysis indicates that the main NSW network may need augmenting following the retirement of significant levels of generation. If there is a large scale retirement on the central coast then the lines between Liddell and the Newcastle area may need upgrading. | T-N9 | Main Grid
Section 6.3.10 | Supply to the Albury Area: • Provision of an additional 132 kV line between Jindera and Albury; • Installation of capacitors at Albury or within Essential Energy’s 132 kV and 22 kV networks supplied from Albury; and • Demand management and local generation. | Supply to the Albury area. | Proposed. | Not within 5-years. | Not stated. | Section 6.3.8 | The need to increase supply into the Albury area does not arise during the NTNDP outlook period. |  | Local Network
Section 6.1.8 | Install point on wave switching control on 30 capacitor circuit breakers To avoid mal-operation and failure of customer equipment. | To avoid mal-operation of capacitors and failure of customer equipment. | Proposed. | From 2015 | 4 | Not referred. | Quality of supply issue - not within the 2013 NTNDP scope. |  | Local Network
Section 6.1.9 | Sydney North – Sydney East 132 kV transmission line (#959/92Z) tower life extension Condition based renewal. | Condition based replacement. | Proposed. | 2017 | 7 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Tomago – Stroud 132 kV transmission line (#96F) pole replacements Condition based renewal. | Condition based replacement. | Proposed. | 2017 | 7 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Burrinjuck – Tumut 132 kV transmission line (#992) low spans remediation Condition based renewal. | Condition based replacement. | Proposed. | 2017 | 9 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Canberra - to Upper Tumut (#1) and Upper Tumut to Yass (#2) 330 kV transmission lines remediation Condition based renewal. | Condition based replacement. | Proposed. | 2017 | 20 | Not referred. | Condition based renewals - emerging limitations of these main grid lines do not arise in the 2013 NTNDP expansion plan. |  | Asset Replacement
Section 6.1.9 | Yass – Marulan 330 kV (#4 and #5) transmission lines remediation Condition based renewal. | Condition based replacement. | Proposed. | 2016 | > 5 | Not referred. | Condition based renewals - emerging limitations of these main grid lines do not arise in the 2013 NTNDP expansion plan. |  | Asset Replacement
Section 6.1.9 | ANM 132 kV Substation secondary systems replacement Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 7 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Armidale Reactor Replacement Armidale 330/132 kV Substation No.2 reactor condition based replacement. | Condition based replacement. | Proposed. | 2017 | 5 | Not referred. | This condition based renewal is not within the 2013 NTNDP scope. However, in the 2013 NSCAS assessment, this reactor was assumed to be available for service. |  | Asset Replacement
Section 6.1.9 | Beryl 132/66 kV Substation secondary systems replacement Condition based replacement. | Condition based replacement. | Proposed. | 2018 | 8 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Buronga 220 kV Substation secondary systems replacement Condition based replacement. | Condition based replacement. | Proposed. | 2018 | 7 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Canberra 330/132 kV Substation rebuild Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 95 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Deniliquin 132/66 kV Substation secondary systems replacement Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Forbes 132/66 kV Substation rebuild Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 30 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Forbes No.1 and No.2 132/66 kV transformer replacement Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 8 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Haymarket 330/132 kV Substation secondary system replacement Condition based replacement. | Condition based replacement. | Proposed. | 2016 | 8 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Kangaroo Valley 330 kV Substation secondary system replacement Condition based replacement. | Condition based replacement. | Proposed. | 2016 | 5 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Munmorah 330 kV Substation rebuild Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 29 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Murrumburrah 132/66 kV Substation secondary system replacement Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Tamworth 330/132 kV Substation No.2 transformer replacement Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 12 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 6.1.9 | Taree 132/66/33 kV Substation secondary system replacement Condition based replacement. | Condition based replacement. | Proposed. | 2017 | 10 | Not referred. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement

## AEMO 2013 APR Projects
2013 APR Reference | Transmission Development | Limitation Addressed | 2013 APR Project Status | 2013 APR Anticipated Timing | 2013 APR Indicative Cost ($ million) | 2012 APR Reference | 2013 NTNDP | Map Reference (if applicable) | Augmentation Type
Section 3.2.1 | South Australia–Victoria (Heywood) Interconnector Upgrade RIT-T. | Thermal capabilities and voltage stability of the transmission network in South Australia's south-east, and thermal capacity limitations of the Heywood transformers, including limitations caused by uneven loading on the transformers. | Committed. | Expected. Commissioning date of July 2016. | $107.7 million ($45.0 million in Victoria and $62.7 million in South Australia). | Section 3.2.1 AEMO and ElectraNet have now completed the PSCR, PADR and PACR stages of the RIT-T related to the South Australia-Victoria (Heywood) interconnector upgrade project. . | Included in the 2013 NTNDP studies. |  | Main Grid
Section 3.2 Table 3-2 | Eastern Metropolitan Melbourne Reactive Support RIT-T. Installing new switched shunt capacitors in the Melbourne metropolitan region. | Inadequate reactive power support in Metropolitan Melbourne. | Priority assessment | Studies making use of 2012 forecasts show this limitation has been deferred until 2018–19 or later. | Not stated. | Section 3.2.2 | Deferral of additional reactive support is consistent with 2013 NSCAS reporting. | T-V1 | Main Grid
Section 3.1.1 | Install three 220/66 kV 225 MVA transformers at Brunswick Terminal Station. | Thermal capacity of 220/66 kV transformers sat Richmond and West Melbourne terminal stations. | Committed. | mid–2015 | Not stated. | Section 3.1.1 | Connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.1.1 | Construct a new 220 kV terminal station at Elaine and connect to the existing Moorabool–Ballarat 220 kV No.2 line. | Connection for Mount Mercer wind farm (130 MW). | Committed. | late–2014 | Not stated. | Section 3.1.1 | Connection asset - Not within the 2013 NTNDP scope. |  | Main Grid
Section 3.1.2 | Install a 500 kV emergency bus-tie at Alcoa Portland Substation. | Continued supply to the Alcoa Portland Aluminium Smelter during outage of Alcoa-Heywood 500 kV line and circuit breakers. | Proposed. | mid–2014 | Not stated. | Section 3.1.2 | Connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.1.2 | Construct a new terminal station at Deer Park and connect to the existing Keilor-Geelong No.2 220 kV line; and install two 220/66 kV 225 MVA transformers at Deer Park. | Thermal capacity of Altona and Keilor 220/66 kV transformers. | Proposed. | late–2017 | Not stated. | Section 3.1.2 | Connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.2.2 | Installation of an additional new (third) 1000 MVA 500/220 kV transformer at Rowville Terminal Station | Thermal capability of the Rowville A1 500/220 kV transformer and Metropolitan Melbourne 220 kV lines. | Current RIT-T | 2018–19 | 51 | Section 3.2.3 | Potential overloading of 500/220 kV transformers at Rowville and Cranbourne was identified as a limitation in the 2013 NTNDP. The limitation was observed in the 2013–14 to 2017–18 period. An economic planning study could defer the timing of the project beyond 2017–18 and identify the best location of an additional 500/220 kV transformer. | T-V2 | Main Grid
Section 3.2 Table 3-2 & Section 3.4.5 Table 3-21 | Regional Victoria Reactive Support RIT-T: - Installing new switched shunt capacitors at Bendigo Terminal Station or other locations in regional Victoria. | Inadequate reactive power support around Bendigo in Regional Victoria. | Priority assessment | Studies making use of 2012 forecasts showed this limitation has been deferred until 2019 or later. | Not stated. | Section 3.2.5 | Deferral of additional reactive support is consistent with 2013 NSCAS reporting. | T-V9 | Main Grid
Section 3.2.3 | Regional Victorian thermal capacity upgrade RIT-T: 1) Installation of a wind monitoring scheme on the Ballarat–Bendigo 220 kV line. 2) Uprating Ballarat–Bendigo 220 kV line. 3) Installation of the third Moorabool–Ballarat 220 kV line. | Thermal capability of the Ballarat–Bendigo and Ballarat–Moorabool No.1 220 kV lines. | Current RIT-T | Wind monitoring scheme - 2014-15. Uprating of Ballarat-Bendigo 220 kV in and third Moorabool-Ballarat 220 kV line - 2016-17. | 126.2 | Sections 3.2.6 and 3.2.7 | The loading of the Ballarat–Bendigo and Ballarat–Moorabool 220 kV lines was identified as a limitation in the 2013 NTNDP. The limitation was observed in the 2013–14 to 2017–18 period. | T-V8 | Main Grid
Section 3.2 Table 3-2 | Victorian Reliability Support RIT-T. Acquire a non-network service. | Thermal capability of the Murray–Dederang 330 kV lines. | Deferred. | Studies with making use of 2012 forecasts show the need to acquire a non-network service is deferred until at least 2015-16. | Not stated. | Section 3.2.8 | Deferral of Victorian reliability support is consistent with 2013 NSCAS reporting. |  | Main Grid
Section 3.4.1 Table 3-9 | A new additional 500 kV line from Hazelwood to Cranbourne. | Thermal capability of the Hazelwood–Cranbourne, Hazelwood–Rowville and Hazelwood–South Morang No.1&2 lines. | Monitoring | When over 2,500 MW new generation is connected to Latrobe Valley 500 kV network. | 224 | Section 3.3.1 Table 3-17 | Not identified as a limitation. 2013 NTNDP did not identify significant new generation in Latrobe Valley area. |  | Main Grid
Section 3.4.1 Table 3-9 | A new 500/220 kV transformer at Hazelwood. | Thermal capability of Hazelwood 500/220 kV transformers. | Monitoring | When significant new generation is connected to Latrobe Valley 220 kV network. | 40 | Section 3.3.1 Table 3-17 | Not identified as a limitation. 2013 NTNDP did not identify significant new generation in Latrobe Valley 220 kV area. |  | Main Grid
Section 3.4.1 Table 3-9 | Upgrade Hazelwood–Rowville and Yallourn–Rowville 220 kV lines. | Thermal capability of Hazelwood–Rowville and Yallourn–Rowville 220 kV lines. | Monitoring | When significant new generation is connected to Latrobe Valley 220 kV network. | Not stated. | Section 3.3.1 Table 3-17 | Not identified as a limitation. Short-term rating allows to reschedule generation following a contingency. |  | Main Grid
Section 3.4.1 Table 3-9 | A new additional 500 kV line from Loy Yang to Hazelwood. | Thermal capability of Loy Yang–Hazelwood 500 kV lines. | Monitoring | When over 1,500 MW new generation is connected to 500 kV network between Loy Yang and Hazelwood. | 68 | Section 3.3.1 Table 3-17 | Not identified as a limitation. 2013 NTNDP did not identify significant new generation in Loy Yang area. |  | Main Grid
Section 3.4.2 Table 3-10 | Voltage control at Alcoa Portland 500 kV bus bar and Heywood terminal station. Options include: • Install a switched capacitor with individual phase switching at Heywood terminal station or near Alcoa Portland • Install a static VAr compensator or a synchronous static compensator • Build additional transposition towers along the Moorabool–Heywood/Alcoa Portland 500 kV line | Moorabool–Heywood–Portland 500 kV line voltage imbalance. | Priority assessment | Within 5 to 10 years. | approximately 12.3 - 46 based on considered options. | Section 3.3.2 Table 3-18 | Quality of supply issue - not within the 2013 NTNDP scope. | T-V11 | Main Grid
Section 3.4.2 Table 3-11 | New dynamic reactive compensation at Heywood/Alcoa Portland. | Voltage instability or collapse (1) during a prior outage of the Heywood–Alcoa Portland 500 kVA No.1 line and, (2) Victoria–South Australia interconnector capacity upgrade to more than 650 MW. | Monitoring | Beyond 10 years. | 46 | Section 3.3.2 Table 3-19 | Voltage control issue - Not within the 2013 NTNDP scope. |  | Main Grid
Section 3.4.2 Table 3-11 | A new additional Moorabool–Mortlake/Tarrone–Heywood 500 kV line. | Thermal capability of Moorabool–Mortlake/Tarrone–Heywood 500 kV circuits. | Monitoring | When over 2,500 MW new generation is connected in the Moorabool-Mortlake/Tarrone-Heywood 500 kV circuits. | 420 | Section 3.3.2 Table 3-19 | This limitation arises during periods of high wind generation and moderate demand periods. |  | Main Grid
Section 3.4.3 Table 3-12 | An additional new (third) 330 kV line between Murray and Dederang or a new 330 kV line between Jindera and Dederang. | Thermal capability of Murray–Dederang 330 kV No.1 and 2 line. | Monitoring | At the time of increased import from New South Wales to Victoria and Murray generation. | 121-183 | Section 3.3.3 Table 3-21 | This limitation does not arise as a constraint in system normal operation in the 2013 NTNDP plan. At least 15 minute available for generation re-dispatch to remove post-contingent overload. |  | Main Grid
Section 3.4.3 Table 3-12 | Uprating of Dederang–Mount Beauty 220 kV No.1 and 2 lines. | Thermal capability of Dederang–Mount Beauty 220 kV No.1 and 2 lines. | Monitoring | At the time of increased import from New South Wales to Victoria. | 23 | Section 3.3.3 Table 3-21 | This limitation does not arise as a constraint in system normal operation in the 2013 NTNDP plan. At least 15 minute available for generation re-dispatch to remove post-contingent overload. |  | Main Grid
Section 3.4.3 Table 3-12 | Uprating of Eildon–Thomastown 220 kV line. | Thermal capability of Eildon–Thomastown 220 kV line. | Monitoring | At the time of increased import from New South Wales to Victoria. | 74 | Section 3.3.3 Table 3-21 | This limitation does not arise as a constraint in system normal operation in the 2013 NTNDP plan. At least 15 minute available for generation re-dispatch to remove post-contingent overload. |  | Main Grid
Section 3.4.3 Table 3-12 | An additional new (fourth) 330/220 kV transformer at Dederang. | Dederang 330/220 kV transformers capability. | Monitoring | At the time of increased import from New South Wales to Victoria. | 26 | Section 3.3.3 Table 3-21 | This limitation does not arise as a constraint in system normal operation in the 2013 NTNDP plan. At least 15 minute available for generation re-dispatch to remove post-contingent overload. |  | Main Grid
Section 3.4.3 Table 3-12 | Uprating of Dederang–South Morang 330 kV No.1 and 2 lines and series compensation; or an additional new (third) 330 kV line with 50% series compensation between Dederang and South Morang. | Thermal capability of Dederang–South Morang 330 kV No.1 and 2 line. | Monitoring | At the time of increased import from New South Wales to Victoria. | 16-341 | Section 3.3.3 Table 3-20 | This limitation does not arise as a constraint in system normal operation in the 2013 NTNDP plan. At least 15 minute available for generation re-dispatch to remove post-contingent overload. |  | Main Grid
Section 3.4.3 Table 3-12 | Additional new shunt capacitors or series compensation at Dederang and Wodonga terminal stations. | Voltage collapse at South Morang, Dederang, Wodonga and Jindera. | Monitoring | At the time of increased import from New South Wales to Victoria. | Not stated. | Section 3.3.3 Table 3-21 | Voltage control - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.4.4 Table 3-13 | Options include: • Install wind monitoring facilities • Replace sections of the Rowville–Malvern circuits with high capacity (high temperature) conductor • Cut-in the No. 1 and No. 4 Rowville–Richmond 220 kV lines at the Malvern terminal station to form the No. 3 and No. 4 Rowville–Richmond–Malvern lines • Loop-in and switch the No. 1 and No. 4 Rowville–Richmond 220 kV lines at Malvern terminal station to form the No. 2 and No. 4 Rowville–Malvern 220 kV lines, and the No. 1 and No. 4 Richmond–Malvern 220 kV lines | Thermal capability of Rowville–Malvern 220 kV circuits. | Priority assessment | Within 10 years. | approximately 0.3 - 25 based on considered options. | Section 3.3.4 Table 3-22 | Limitation does not arise in the 2013 NTNDP expansion plan. This was a radial line and timing depends on the point of connection load forecasts and any load transfers to nearby terminal stations. | T-V3 | Main Grid
Section 3.4.4 Table 3-14 | Options include: Upgrade stations assets at Rowville, Springvale and Heatherton terminal stations A new Cranbourne–Heatherton 220 kV double circuit line or underground cable A new underground cable between Heatherton and Malvern. | Thermal capability of Rowville–Springvale and Springvale–Heatherton 220 kV circuits. | Priority assessment | Within 10 years. | Not stated for upgrade of station assets. approximately 76 - 671 based on considered options. | Section 3.3.4 Table 3-23 | Limitation arises in the 2013 NTNDP expansion plan. This was a radial line and timing depends on the point of connection load forecasts and any load transfers to nearby terminal stations. | T-V4 | Main Grid
Section 3.4.4 Table 3-15 | An additional new (fourth) 500/220 kV transformer at Keilor; or Install high rated 500/220 kV transformers at Keilor as part of SP AusNet's asset renewal program. | Thermal capability of Keilor A2 and A4 500/220 kV transformers. | Priority assessment | Within 10 years. | Approximately 44 based on considered options. | Section 3.3.4 Table 3-27 | An additional 500/220 kV transformer was identified in the Western Metropolitan Melbourne area to remove limitation on Moorabool 500/220 kV A1 transformer. This reduces the loading on Keilor 500/220 kV transformers. | T-V5 | Main Grid
Section 3.4.4 Table 3-16 & Table 3-19 | Ringwood terminal station Supply. Options include: • Connect the Rowville–Templestowe 220 kV line at Ringwood terminal station • Upgrade the existing Ringwood–Thomastown 220 kV line and replace the isolators at Ringwood terminal station | Ringwood–Thomastown 220 kV line loading. Ringwood–Rowville 220 kV line loading. | Priority assessment | Within 10 years. | approximately 8.85 - 9.6 based on considered options. | Section 3.2.4 | The limitation of the Ringwood–Thomastown 220 kV line arises in the 2013 NTNDP expansion plan during 2023–24 to 2027–28. | T-V6 | Main Grid
Section 3.4.4 Table 3-17 | Melbourne Metropolitan voltage stability priority assessment. | A risk of voltage instability in the Melbourne metropolitan area. | Priority assessment | The economic evaluation optimal timing to install additional reactive power support is around 2019–20. | Not stated. | Section 3.3.4 Table 3-26 | Voltage control issue - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.4.4 Table 3-18 Table 3-19 | An additional new (third) 330/220 kV transformer at South Morang and connection (cut-in) of the Thomastown–Rowville 220 kV line at South Morang; A new 1,000 MVA 500/220 kV transformer at South Morang and connection (cut-in) of the Thomastown–Rowville 220 kV line at South Morang; Replacement of existing 330/220 kV transformers at South Morang with high rated new transformers as part of SP AusNet's asset replacement program. | Thermal capability of South Morang H1 and H2 330/220 kV transformers. | Priority assessment | The first transformer replacement is expected to be completed in 2016. | approximately 52 - 77.8 based on considered options. | Section 3.3.4 Table 3-24 & Table 3-27; Section 3.6 Table 3-24 | This limitation arises in the 2013 NTNDP expansion plan. However, a new additional 500/220 kV transformer in the Melbourne Eastern Metropolitan area would reduce the loading on South Morang 330/220 kV transformers. | T-V7 | Main Grid
Section 3.4.4 Table 3-19 | An additional new 1,000 MVA 500/330 kV transformer at South Morang; or A new 1,000 MVA 500/220 kV transformer at South Morang and connection (cut-in) of the Thomastown–Rowville 220 kV line at South Morang | Thermal capability of SMTS 500/330 kV F2 transformer. | Monitoring | At the time of additional export capability from Victoria to New South Wales. | 55-72 | Section 3.3.4 Table 3-27 | This limitation does not arise as a constraint in the 2013 expansion plan. |  | Main Grid
Section 3.4.4 Table 3-19 | Connection (cut-in) of the Thomastown–Rowville 220 kV line at South Morang; or Connection (cut-in) of Eildon-Thomastown 220 kV line at South Morang. | Thermal capability of South Morang–Thomastown No.1 and No.2 220 kV line. | Monitoring | Subject to amount of additional load growth around the Melbourne Metropolitan area. | 8-10 | Section 3.3.4 Table 3-25 | This limitation does not arise as a constraint in the 2013 expansion plan. A new additional 500/220 kV transformer in the Melbourne Eastern Metropolitan area would reduce the loading on this line. |  | Main Grid
Section 3.4.4 Table 3-19 | Up-rate the Keilor–Thomastown 220 kV No.2 line; or an additional 500/220 kV transformer at Rowville. | Thermal capability of Keilor–Thomastown No.2 220 kV line. | Monitoring | Subject to amount of additional load growth around the Melbourne Metropolitan area. | 10-51 | Section 3.3.4 Table 3-27 | This limitation does not arise as a constraint in the 2013 expansion plan. |  | Main Grid
Section 3.4.4 Table 3-19 | Connection (cut-in) Thomastown–Ringwood 220 kV line at Templestowe. | Thermal capability of Templestowe–Thomastown 220 kV line. | Monitoring | Subject to amount of additional load growth around the Melbourne Metropolitan area. | Not stated. | Section 3.3.4 Table 3-27 | This limitation does not arise as a constraint in the 2013 expansion plan. |  | Main Grid
Section 3.4.4 Table 3-19 | An additional 500/220 kV transformer at Cranbourne or Uprating of East Rowville–Rowville 220 kV line or a new 220 kV underground cable between East Rowville and Rowville. | Rowville–East Rowville 220 kV line loading. Thermal capability of Cranbourne A1 500/220 kV transformer. | Monitoring | Subject to amount of additional load growth at East Rowville and Tyabb Terminal Stations. | 33-83 | Section 3.2.3 | Potential overloading of 500/220 kV transformers at Rowville and Cranbourne and Rowville–East Rowville 220 kV line arises as a limitation in the 2013 NTNDP expansion plan. |  | Main Grid
Section 3.4.4 Table 3-19 | Options include: Reconfigure the meshed network to reduce fault levels; Replace assets with high fault level withstand and interruption capability; and Install series reactors to limit fault level contribution. | Increase in fault levels beyond network plant capability. | Monitoring | At the time of significant network augmentation and connection of new generators, particularly within Greater Melbourne and Geelong areas and their vicinity. | Not stated. | Section 3.3.4 Table 3-27 | Fault level requirement - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.4.5 Table 3-20 | Options include: Replace limiting elements at Geelong Terminal Station; Additional new 220 kV line/s between Geelong and Moorabool. | Thermal capability of Geelong–Moorabool 220 kV line. | Priority assessment | Not stated. (NCIPAP project timing 2015/16) | 0.87-45 | Section 3.3.5 Table 3-28 | Replacement of limiting termination equipment modelled in the 2013 NTNDP. | T-V10 | Main Grid
Section 3.4.5 Table 3-22 | A phase angle regulating transformer on the Bendigo-Fosterville–Shepparton 220 kV line; or Uprating of Bendigo–Fosterville–Shepparton 220 kV line. | Thermal capability of Bendigo–Fosterville–Shepparton 220 kV line loading. | Monitoring | At the time of significant load growth in Regional Victoria and/or increased import from New South Wales. | 43-56 | Section 3.3.5 Table 3-30 | Possible future project with significant load growth and/or increase import from New South Wales to Victoria. However, this limitation does not arise in the 2013 NTNDP expansion plan. |  | Main Grid
Section 3.4.5 Table 3-22 | Options include: A phase angle regulating transformer on the Bendigo–Fosterville–Shepparton 220 kV line; Replace the existing Dederang–Glenrowan 220 kV lines with a new double circuit line; or Replace the existing Dederang–Shepparton 220 kV line with a new double circuit 220 kV line. | Thermal capability of Dederang–Glenrowan 220 kV line. | Monitoring | At the time of significant load growth in Regional Victoria and/or increased import from New South Wales. | 43-253 | Section 3.3.5 Table 3-30 | Possible future project with significant load growth and/or increase import from New South Wales to Victoria. However, this limitation does not arise in the 2013 NTNDP expansion plan. |  | Main Grid
Section 3.4.5 Table 3-22 | Options include: A phase angle regulating transformer on the Bendigo–Fosterville-Shepparton 220 kV line; Uprate the Dederang–Shepparton 220 kV line. Replace the existing Dederang–Glenrowan 220 kV lines with a new double circuit line; or Replace the existing Dederang–Shepparton 220 kV line with a new double circuit 220 kV line. | Thermal capability of Dederang–Shepparton 220 kV line. | Monitoring | At the time of significant load growth in Regional Victoria and/or increased import from New South Wales. | 43-253 | Section 3.3.5 Table 3-30 | Possible future project with significant load growth and/or increase import from New South Wales to Victoria. However, this limitation does not arise in the 2013 NTNDP expansion plan. |  | Main Grid
Section 3.4.5 Table 3-22 | Options include: A phase angle regulating transformer on the Bendigo–Fosterville-Shepparton 220 kV line; Replace the existing Dederang–Shepparton 220 kV line with a new double circuit line. | Thermal capability of Glenrowan–Shepparton 220 kV line. | Monitoring | At the time of significant load growth at Shepparton Terminal Station. | 43-253 | Section 3.3.5 Table 3-30 | Possible future project with significant load growth. However, this limitation does not arise in the 2013 NTNDP expansion plan. |  | Main Grid
Section 3.4.5 Table 3-22 | Uprate the line termination elements of Ballarat–Waubra–Horsham 220 kV line at Horsham; or Replace the existing Ballarat–Waubra–Horsham 220 kV line with a new double circuit line. | Thermal capability of Ballarat–Waubra–Horsham 220 kV line. | Monitoring | At the time of significant load growth at Horsham Terminal Station. | 855 | Section 3.3.5 Table 3-30 | Limitation arises in the 2013 NTNDP during periods of high wind generation and moderate demand periods. |  | Main Grid
Section 3.4.5 Table 3-22 | Replace the existing Kerang–Wemen–Red Cliffs 220 kV line with a new double circuit line. | Thermal capability of Kerang–Wemen–Red Cliffs 220 kV line. | Monitoring | At the time of significant load growth at Wemen/Red Cliffs Terminal Stations. | 683 | Section 3.3.5 Table 3-30 | Limitation arises in the 2013 NTNDP during periods of high wind generation and moderate demand periods. |  | Main Grid
Section 3.4.5 Table 3-22 | Uprate the Moorabool–Terang 220 kV line; or Replace the existing Moorabool–Terang 220 kV line with a new double circuit line. | Thermal capability of Moorabool–Terang 220 kV line. | Monitoring | At the time significant net load growth at Terang Terminal Station. | 58-247 | Section 3.3.5 Table 3-30 | Limitation arises in the 2013 NTNDP during periods of high wind generation and moderate demand periods. |  | Main Grid
Section 3.4.5 Table 3-22 | A new additional (third) 500/220 kV transformer at Moorabool. | Thermal capability of Moorabool 500/220 kV transformer. | Monitoring | At the time of increased load growth in Geelong, Regional Victoria or high import from South Australia or increased generation in the VIC South-West 500 kV corridor. | 49 | Section 3.3.5 Table 3-29 | Overloading of the Moorabool 500/220 kV A1 transformer arises as a limitation in the 2013 NTNDP expansion plan during 2018–29 to 2032–33. Also this limitation arises during periods of high wind generation and moderate demand periods. |  | Main Grid
Section 3.4.5 Table 3-22 | Network operational arrangements, series reactor to control fault levels and/or switchgear replacement. | Increase in fault levels beyond network plant capability. | Monitoring | At the time of increased generation particularly in Regional Victoria. | Not stated. | Section 3.3.5 Table 3-30 | Fault levels - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a new additional (third) 220/66 kV 150 MVA transformer at Ballarat Terminal Station | Thermal capacity of the existing 220/66 kV transformers at Ballarat Terminal Station. | Proposed. | 2022 | Not stated. | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install two new 220/22 kV 75 MVA transformers at Bendigo Terminal Station. | Thermal capacity of the existing 220/66/22 kV transformers at Bendigo Terminal Station. | Committed. | Late-2013 | Not stated. | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install an additional new (fourth) 220/66 kV 150 MVA transformer at Cranbourne Terminal Station. | Thermal capacity of the existing 220/66 kV transformers at Cranbourne Terminal Station. | Proposed. | Summer 2021-22 | Not stated. | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Establish a new terminal station at Dandenong with 220/66 kV transformation. | Thermal capacity of existing 220/66 kV transformers at East Rowville, Heatherton and Springvale terminal stations. | Proposed. | Summer 2022-23 | Not stated. | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a new additional (third) 220/66 kV transformer at Glenrowan Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Glenrowan Terminal Station. | Proposed. | After 2021 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a 100 MVAr capacitor bank at the Keilor Terminal Station. | Supply of additional reactive power. | Proposed. | Prior to summer 2014-15 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a new additional (third) 220/66 kV transformer at Malvern Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Malvern Terminal Station. | Proposed. | After 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a new additional (fourth) 220/66 kV transformer at Morwell Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Morwell Terminal Station. | Proposed. | After 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a new additional (third) 220/22 kV transformer at Ringwood Terminal Station. | Thermal capacity of existing 220/22 kV transformers at Ringwood Terminal Station. | Proposed. | Approximately 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope. |  | Local Network
Section 3.5 | Install a new additional (fifth) 220/66 kV transformer at Ringwood Terminal Station, | Thermal capacity of existing 220/66 kV transformers at Ringwood Terminal Station. | Proposed. | 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.5 | Install a new additional (third) 220/66 kV 225 MVA transformer at South Morang Terminal Station. | Thermal capacity of existing 220/66 kV transformers at South Morang Terminal Station. | Proposed. | 2021 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.5 | Install a new additional (fourth) 220/66 kV transformer at Templestowe Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Templestowe Terminal Station. | Proposed. | After 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.5 | Install a new additional (third) 220/66 kV transformer at Terang Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Terang Terminal Station. | Proposed. | After 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.5 | Install a new additional (third) 220/66 kV transformer at Tyabb Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Tyabb Terminal Station. | Proposed. | 2013-14 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.5 | Install a new additional (second) 220/66 kV transformer at Wemen Terminal Station. | Thermal capacity of existing 220/66 kV transformers at Wemen Terminal Station. | Proposed. | Approximately 2022 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.5 | Install a new additional (third) 330/66 kV transformer at Wodonga Terminal Station. | Thermal capacity of existing 330/66 kV transformers at Wodonga Terminal Station. | Proposed. | After 2021 | Not Stated | Section 3.4 | Distribution connection asset - Not within the 2013 NTNDP scope |  | Local Network
Section 3.6 | Replace 12 towers on the Bendigo-Kerang 220 kV line. | Condition based replacement. | Completed. | 2013 | 8 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace transformers and 220 kV circuit breakers at Brooklyn Terminal Station. | Condition based replacement. | Committed. | 2013 | 50 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV R2A/2B transformer group with one 220/66 kV 150 MVA transformer at Bendigo Terminal Station. | Condition based replacement. | Committed. | 2013 | 9 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace seven bulk oil 220 kV circuit breakers at Rowville Terminal Station. | Condition based replacement. | Committed. | 2013 | 17 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B1 and B3 transformers with two 220/66 kV 150 MVA transformers and four 66 kV circuit breakers at Geelong Terminal Station. | Condition based replacement. | Committed. | 2013 | 21 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace transmission line structure, conductor and insulator replacement | Condition based replacement. | Committed. | 2013 | 21 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope.
Section 3.6 | Replace five bulk oil 220 kV circuit breakers at 220 kV switchyard at Hazelwood Power Station (stage 2). | Condition based replacement. | Committed. | 2013 | 12 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 330/220 kV H1 transformer at Dederang. | Condition based replacement. | Committed. | 2014 | 17 | Section 3.5 | Condition based renewals - emerging limitations of this transformer do not arise in the 2013 NTNDP expansion plan. |  | Asset Replacement
Section 3.6 | Replace 220 kV CTs and three 6 kV circuit breakers at East Rowville Terminal Station. | Condition based replacement. | Proposed. | 2014 | 2 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B1 transformer and eight 220 kV air blast and three 66 kV circuit breakers at Glenrowan Terminal Station. | Condition based replacement. | Committed. | 2014 | 30 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV 150 MVA B2 transformer and four 66 kV single phase capacitive voltage transformers at Morwell Terminal Station. | Condition based replacement. | Proposed. | 2014 | 7.6 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace nine bulk oil 220 kV circuit breakers at Ringwood Terminal Station. | Condition based replacement. | Committed. | 2015 | 20 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace eleven bulk oil 220 kV circuit breakers at 220 kV switchyard at Hazelwood Power Station (stage 3). | Condition based replacement. | Proposed. | 2015 | 8 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B1 150 MVA transformer and 66 kiva bulk oil and minimum oil circuit breakers at Fishermens Bend Terminal Station. | Condition based replacement. | Proposed. | 2016 | 22.8 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace three 220/66 kV 150 MVA transformers and seven 220 kV, sixteen 66 kV and 22 kV switch bays at West Melbourne Terminal Station. | Condition based replacement. | Proposed. | 2016 | 176 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace three 220/66 kV 150 MVA transformers with 225 MVA transformers and 220 kV GIS and 22 kV switchboard at Richmond Terminal Station. | Condition based replacement. | Proposed. | 2016 | 198 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 330/220 kV 700 MVA transformer at South Morang Terminal Station; Keep H2 transformer as a cold spare. | Condition based replacement. | Proposed. | 2016 | 32.6 | Section 3.5 | Condition based renewals - emerging limitations of this transformer arise in the 2013 NTNDP expansion plan. |  | Asset Replacement
Section 3.6 | Replace minimum oil 220 kV circuit breakers at 220 kV switchyard at Yallourn Power Station. | Condition based replacement. | Proposed. | 2016 | 20.6 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace three 220/66 kV 150 MVA transformers, two minimum oil 220 kV circuit breakers and eleven 66 kV bulk oil circuit breakers at Heatherton Terminal Station. | Condition based replacement. | Proposed. | 2017 | 56.8 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace remaining bulk oil 220 kV circuit breakers and install remote operation isolators at 220 kV switchyard at Hazelwood Power Station (stage 4). | Condition based replacement. | Proposed. | 2017 | 20.4 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B4 transformers and six 66 kV bulk oil circuit breakers at Ringwood Terminal Station. | Condition based replacement. | Proposed. | 2017 | 15.8 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace selected towers of Dederang-South Morang No.1 and No.2 330 kV lines. | Condition based replacement. | Proposed. | 2017 | 19 | Section 3.5 | Condition based renewals. |  | Asset Replacement
Section 3.6 | Replace 500/220 kV A4 and 220/66 kV B4 transformers at Keilor Terminal Station. | Condition based replacement. | Proposed. | 2018 | 48 | Section 3.5 | Condition based renewals. Need for an additional 500/220 kV transformer in the Western Melbourne Metropolitan area arises in the 2013 expansion plan. |  | Asset Replacement
Section 3.6 | Replace four minimum oil 220 kV, 66 kV and 22 kV circuit breakers at Brooklyn Terminal Station. | Condition based replacement. | Proposed. | 2019 | 43.1 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B1, B2 and B3 transformers, minimum oil 220 kV and selected 66 kV circuit breakers at Springvale Terminal Station (Stage 1). | Condition based replacement. | Proposed. | 2019 | 81.1 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B2 transformer and fifteen 66 kV circuit breakers at Templestowe Terminal Station. | Condition based replacement. | Proposed. | 2020 | 36.8 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace selected 500 kV current transformers at Hazelwood and Loy Yang terminal stations. | Condition based replacement. | Proposed. | 2020 | 4 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/11 kV No.1 and 2 transformers at Morwell Power Station. | Condition based replacement. | Proposed. | 2020 | 21 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace No.1 and 2 66 kV reactors at Red Cliffs Terminal Station. | Condition based replacement. | Proposed. | 2020 | 12 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace two 220 kV minimum oil CBs and 66 kV CBs at East Rowville Terminal Station. | Condition based replacement. | Proposed. | 2020 | 20 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Transmission fall arrest installation program | Condition based replacement. | Proposed. | 2022 | 32 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Transmission conductor and insulator replacement | Condition based replacement. | Proposed. | 2022 | 23 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace selected towers on Murray–Dederang No.1 and 2 330 kV lines. | Condition based replacement. | Proposed. | 2022 | 20 | Section 3.5 | Condition based renewals. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV 150 MVA B4 transformer and bulk oil and minimum oil 66 kV circuit breakers at Thomastown Terminal Station. | Condition based replacement. | Proposed. | 2022 | 20 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/66 kV B4 transformer and bulk oil 66 kV circuit breakers at Geelong Terminal Station. | Condition based replacement. | Proposed. | 2022 | 16 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Section 3.6 | Replace 220/22 kV L1 and L3 transformers at West Melbourne Terminal Station. | Condition based replacement. | Proposed. | 2022 | 33 | Section 3.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement
Note on B9: Chandana Samarasinghe: Which one is the proposed option ?

## ElectraNet 2013 APR Projects
2013 APR Reference | Transmission Development | Limitation Addressed | 2013 APR Project Status | 2013 APR Anticipated Timing | 2013 APR Indicative Cost ($ million) | 2012 APR Reference | 2013 NTNDP | Map Reference (if applicable) | Augmentation type
Section 5.10 | Remove the protection limit of the TIPS-Northfield and TIPS-Kilburn lines and bring the lines to their design ratings. | Outage of TIPS to Kilburn 275 kV overloads the TIPS to Northfield 275 kV line; Outage of TIPS to Northfield 275 kV overloads the TIPS to Kilburn 275 kV line. | Committed. | 2013 | 2 | Table 7.4 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.10 | Install 2 x 25 MVA 132/33 kV transformers and replace selected assets at Hummocks. | Thermal overload of the remaining transformer at Hummocks under N-1 conditions. | Committed. | 2013 | 11 | Table 9.6 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.10 | Rebuild Waterloo and install 2 x 25 MVA 132/33 kV transformers. | Thermal overload of the remaining transformer at Waterloo under N-1 conditions; Waterloo substation at end of technical life. | Committed. | 2013 | 43 | Table 9.6 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.10 | Install 1 x 15 Mvar 132 kV switched capacitor bank at Kadina East Substation. | Inadequate voltage levels on the Yorke Peninsula under peak load contingent conditions. | Committed. | 2013 | 4.3 | Table 9.6 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.10 | Break out 2nd Davenport to Cultana 275 kV circuit; install 2x200 MVA 275/132 kV transformers at Cultana and reconfigure 132 kV Davenport to Whyalla lines. | The outage of Cultana 275/132 kV transformer, Davenport to Cultana 275 kV line or Cultana to Whyalla 132 kV circuit leads to inadequate 132 kV voltages and thermal overloads the 132 kV lines. | Committed. | 2014 | 72 | Table 12.2 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.10 | Establish Munno Para substation and install a single 225 MVA 275/66 kV transformer supplying into the Northern Suburbs. | Load growth in the Metro North overloads the 66 kV network and the 275/66 kV transformer capacity exceeds the ETC requirement. | Committed. | 2015 | 42.6 | Table 7.4 | Included in the 2013 NTNDP studies. |  | Local Network
Section 5.10 | Heywood Interconnector Upgrade: Decommission Snuggery–Keith and Keith–Tailem Bend #1 132 kV lines. Install reactive support if required on the South East–Tailem Bend 132 kV network. Establish Black Range series compensation site and install series compensation for the Tailem Bend–South East 275 kV lines. | Dynamic stability limitations and thermal overloading of the Snuggery–Keith and Keith–Tailem Bend #1 132 kV lines and South East 275/132 kV transformer during increased power transfer between South Australia and Victoria. | Committed. | 2016 | 63 (excluding VIC network augmentation costs) | Table 6.3 | Included in the 2013 NTNDP studies. |  | Main Grid
Section 5.12 | Rebuild Davenport-Brinkworth-Para 275 kV as a high capacity 275 kV AC double circuit line with twin conductors. | Transmission limitations on the network between NSA and ADE. | Conceptual | Not stated. | 350 | Table 6.3 | This potential limitation has been identified in the 2013 NTNDP. | T-S2 | Main Grid
Section 2.1.3 | Augmentation of the network supplying the Riverland region (being investigated jointly by ElectraNet and AEMO) | Potential supply limitations to Riverland region | Under investigation | Not stated. | TBA | Table 10.5 | Limitation arises during times of peak load conditions in the Riverland area when Murraylink is not importing to South Australia. Limitation was also observed under high levels of wind generation in the NSA zone. AEMO and ElectraNet are currently undertaking a joint planning study to identify solutions to this potential reliability limitation. | T-S3 | Main Grid
Section 5.12 | String vacant 275 kV circuit between Tailem Bend and Tungkillo and establish a 3rd 275 kV circuit. between Para and Tungkillo. | Transmission limitations on the Tailem Bend -Tungkillo transmission corridor. | Conceptual | Not stated. | 150 | Table 6.3 | This potential limitation has been identified in the 2013 NTNDP. | T-S4 | Main Grid
Section 5.10 | Install additional circuit breakers and minor plant replacement at Tailem Bend substation. | Substandard circuit breaker arrangement at Tailem Bend substation makes it difficult to obtain outages for maintenance and places network security at risk. | Proposed. | 2019 | 16 | Table 11.6 | For security and compliance - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Work has been initiated to explore either an increase in the amount of contracted generation or a demand side solution to cover the balance of load. | Contracted generation to support the Port Lincoln load during an outage of the radial 132 kV transmission line is exceeded. | Proposed. | 2019 | TBD | Table 12.2 | Local supply/network need - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Install 1 x 15 Mvar 132 kV PoW switched capacitor bank at Hummocks. | Inadequate voltage levels on the Yorke Peninsula under peak load contingent conditions. | Proposed. | 2021 | 4.2 | Table 9.6 | Reactive power support - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Install 2x3 Mvar 11 kV capacitor bank at Naracoorte substation to delay the Kincraig substation rebuild project. | Inadequate 132/33 kV transformer capacity in 2021/22 during the loss of one 132/33 kV transformers at Kincraig substation. | Proposed. | 2021 | 0.8 (SA Power Networks Cost) | N/A | Local supply/network need - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Install 2nd 225 MVA 275/66 kV transformer at Mount Barker South; retire aged 132 kV assets at Mount Barker from service. | Mount Barker 132/66 kV transformers unable to meet ETC service standards under the peak load outage of the Mount Barker South 275/66 kV transformer. | Proposed. | 2023 | 10.4 | Table 8.3 | Local supply/network need - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Rebuild Kincraig substation on an adjacent site with 2 x 60 MVA 132/33 kV transformers. | Inadequate 132/33 kV transformer capacity in 2023/24 during the loss of one 132/33 kV transformers at Kincraig substation. | Proposed. | 2023 | 37 | Table 11.6 | Local supply/network need - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Install 1 x 12 Mvar 132 kV PoW switched capacitor bank at Kadina East. | Inadequate voltage levels on the Yorke Peninsula under peak load contingent conditions. | Proposed. | 2023 | 3.3 | N/A | Reactive power support - not within the 2013 NTNDP scope. |  | Local Network
Section 5.10 | Reinforce the lower Eyre Peninsula by constructing a double circuit 275 kV line from Cultana-Yadnarie- Port Lincoln in a staged approach. Establishing 275/132 kV substations at Yadnarie and Port Lincoln. Install 100 Mvar cap bank at Yadnarie and SVC at Port Lincoln. In future convert the Port Lincoln to Yadnarie 132 kV line for sub-transmission purposes. This significant augmentation is currently being deferred by the use of the Port Lincoln generators to manage this line overload. | Thermal overload of the Middleback–Yadnarie 132 kV transmission line under system normal conditions; line condition prevents further line uprating from being a viable option. No new load can be connected in the South of Middleback without having to add more generation to the South of Middleback. Condition on the 132 kV radial line between Whyalla and Port Lincoln indicates line replacement. | Proposed. | Subject to connection application. | 548 | Table 12.2 | Limitation does not arise in the 2013 NTNDP expansion plan. The Eyre Peninsula 132 kV network limitation is driven by local peak load in lower Eyre Peninsula. This limitation does not arise at the time of 10% POE SA summer maximum demand modelled in 2013 NTNDP studies. | T-S1 | Main Grid
Section 5.11 | Replace all non-compliant plant. | Non-compliant NGM current transformers and voltage transformers at various connection points. | Proposed. | 2013-2018 | 14 | Table 6.1 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Replace the existing SVC control system at Para substation with modern-day equipment. | Condition of the existing Para SVC control system and the lack of spare parts make maintenance impossible and manufacturer support is largely withdrawn. Significant business risk that failure will have severe impact on the interconnectors’ transfer capacity. | Proposed. | 2013-2018 | 15 | Table 6.4 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Mannum to Adelaide pumping station #1 substation to modern-day standards and replace the 132/3.3 kV transformers. | Mannum to Adelaide pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013-2018 | 16 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Mannum to Adelaide pumping station #2 substation to modern-day standards and replace the 132/3.3 kV transformers. | Mannum to Adelaide pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013-2018 | 15 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Mannum to Adelaide pumping station #3 substation to modern-day standards and replace the 132/3.3 kV transformers. | Mannum to Adelaide pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013-2018 | 11 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Millbrook substation to modern-day standards and replace the 132/3.3 kV transformers. | Millbrook pumping station primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013–2018 | 12 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Morgan to Whyalla pumping station #4 substation to current day standards and replace the 132/3.3 kV transformers. | Morgan to Whyalla pumping station #4 primary plant at end of technical life; site not aligned with current environmental practices and company practices. | Proposed. | 2013–2018 | 12 | Table 9.8 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Morgan to Whyalla pumping station #1 substation to current day standards and replace the 132/3.3 kV transformers. | Morgan to Whyalla pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013–2018 | 22 | Table 10.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Morgan to Whyalla pumping station #2 substation to current day standards and replace the 132/3.3 kV transformers. | Morgan to Whyalla pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013–2018 | 15 | Table 10.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Morgan to Whyalla pumping station #3 substation to current day standards and replace the 132/3.3 kV transformers. | Morgan to Whyalla pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2013–2018 | 12 | Table 10.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild Neuroodla substation; install 1 x 10 MVA transformer. | Neuroodla substation at end of technical life; 132/33 kV transformer condition assessment indicates replacement is required. | Proposed. | 2013–2018 | 7 | Table 13.2 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild Mount Gunson substation; install 1 x 10 MVA transformer. | Mount Gunson substation at end of technical life; 132/33 kV transformer condition assessment indicates replacement is required. | Proposed. | 2013–2018 | 7 | Table 13.2 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Replace the existing secondary systems at Happy Valley with modern day equipment and minor poor condition plant. | Condition of the existing secondary systems at Happy Valley placing limitations on transfer capacity and protection effectiveness. | Proposed. | 2018–2023 | 17 | Table 7.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Replace the existing primary & secondary plant at Dry Creek with modern day equipment. | Condition of the primary and secondary plant at Dry Creek connection point at the end of its technical life. | Proposed. | 2018–2023 | 20 | Table 7.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild Kanmantoo substation; utilise 10 MVA transformer recently replaced. | Kanmantoo substation at end of technical life; condition assessment indicates replacement is required (132/33 kV transformer replaced already). | Proposed. | 2018–2023 | 13 | Table 8.3 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Murray Bridge to Hahndorf pumping station #1 substation to modern-day standards and replace the 132/11 kV transformers. | Murray Bridge to Hahndorf pumping station #1 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2018–2023 | 18 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Murray Bridge to Hahndorf pumping station #2 substation to modern-day standards and replace the 132/11 kV transformers. | Murray Bridge to Hahndorf pumping station #2 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2018–2023 | 12 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Murray Bridge to Hahndorf pumping station #3 substation to modern-day standards and replace the 132/11 kV transformers. | Murray Bridge to Hahndorf pumping station #3 primary plant at end of technical life; site not aligned with current environmental practices and company policies. | Proposed. | 2018–2023 | 16 | Table 8.5 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Keith substation when it is economic to do so. | Keith substation condition assessment indicates replacement is required in the medium term. | Proposed. | 2018–2023 | 32 | Table 11.6 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.11 | Rebuild the Mt Gambier substation when it is economic to do so. | Mt Gambier substation condition assessment indicates replacement is required in the medium term. | Proposed. | 2018–2023 | 31 | Table 11.8 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.

## Transend 2013 APR Projects
2013 APR Reference | Transmission Development | Limitation Addressed | 2013 APR Project Status | 2013 APR Anticipated Timing | 2013 APR Indicative Cost ($ million) | 2012 APR Reference | 2013 NTNDP | Map Reference (if applicable) | Augmentation type
Section 4.3.2 | Creek Road Substation 110 kV redevelopment. | Condition based replacement. | Committed. | 2014-03-01 | Not stated | Section 4.3.18 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 4.3.3 | Burnie Substation 110 kV redevelopment. | Condition based replacement. | Committed. | 2014-04-01 | Not stated. | Section 4.3.7 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 4.3.4 | Tungatinah Substation 110 kV redevelopment and the extension of the 110 kV transmission circuits that connect Meadowbank and Tarraleah power stations and New Norfolk to Tungatinah substations; and replacement of the 110/22 kV supply transformer at Tungatinah Substation. | Condition based replacement. | Committed. | 2014-04-01 | Not stated. | Section 4.3.9 | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 4.3.5 | Avoca Substation asset replacements. | Condition based replacement. | Committed. | 2014-04-01 | Not stated. | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 4.3.6 | George Town Substation 110 kV redevelopment. | Condition based replacement. | Committed. | 2014-07-01 | Not stated. | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 4.4.1 | Meadowbank Substation 110 kV redevelopment. | Condition based replacement. | Advanced. | 2015-06-01 | Not stated. | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.2.1.6.1 | An additional 110/44-22 kV 20/30 MVA transformer at Rosebery Substation . Preferred option: Relocate the 110/44-22 kV 20/30 MVA transformer T3 from Davenport to Rosebery Substation. | Thermal capacity of existing 110/44-22 kV transformers at Rosebery Substation. | Proposed. | 2016-06-01 | 3.8 | Section 5.2.1.6.1 | Local supply issue - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.2.1.6.2 | Install a new 220/110 kV 30/50 MVA transformer at Queenstown and connect to Farrell-John Butters 220 kV line; and rearrangement of Farrell-Rosebery-Queenstown 110 kV circuit at Newton Substation. | Loss of the Farrell–Rosebery–Queenstown 110 kV line (single contingency) results in loss of supply to Rosebery, Queenstown and Newton Substations. | Proposed. | 2017-06-01 | 12.5 | Section 5.2.1.6.2 | Radial supply - not within the 2013 NTNDP scope. | T-T2 | Main Grid
Section 5.2.1.6.4 | Install an additional new 220 kV circuit breaker in the bus coupler bay to create a double circuit breaker arrangement. | Possible total loss of supply to the area and a significant loss of generation due to failure of existing bus-coupler circuit breaker. | Proposed. | 2015-06-01 | 1.3 | Section 5.2.1.6.5 | Substation security enhancement - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.2.2.6.1 | Convert one of the 110/22-11 kV transformers at Emu Bay Substation to 110/22 kV operation and transfer portion of load from Burnie Substation to Emu Bay Substation. | Thermal capacity of existing 110/22 kV transformers at Burnie Substation. | Proposed. | 2021 | 3.7 | Section 5.2.2.6.1 | Substation security enhancement - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.2.2.6.2 | Convert one of the 110/22-11 kV transformers at Wesley Vale Substation to 110/22 kV operation and transfer portion of load from Devonport Substation to Wesley Vale Substation. | Thermal capacity of existing 110/22 kV transformers at Devonport Substation. | Proposed. | 2018-12-01 | 1.6 | Section 5.2.2.6.2 | Local supply issue - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.2.3.6.1 | Install additional new 220 kV circuit breakers at George Town Substation to convert Comalco No.4/Tamar Valley Power Station diameter to circuit-breaker-and-a-half, and Comalco No.5 connection to double circuit breaker. | A failure of a circuit breaker at George Town substation of Basslink converter station connection could lead to a significant loss of supply to the to the area and a significant loss of generation. Under certain conditions, this could cause instability. | Proposed. | 2017-06-01 | 6.99 | Section 5.2.3.6.1 | Substation security enhancement - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.2.4.6.1 | Install additional radiators to the existing 110/22 kV transformer. | Thermal capacity of the existing 110/22 kV transformer at Avoca. | Proposed. | 2019-07-05 | 0.1 | Section 5.2.4.6.1 | Local supply issue - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.2.4.6.2 | Upgrading Aurora's 22 kV distribution network instead of construction of a new 110 kV transmission line. | Loss of the Palmerston-Avoca-St Marys 110 kV line (single contingency) or 110/22 kV transformer at Avoca Substation results in loss of supply to Avoca and St Marys. Thermal capacity of St Marys 110/22 kV transformer. | Proposed. | 2014-06-01 | 2.4 | Section 5.2.4.6.4 | Local supply issue - not within the 2013 NTNDP scope. | T-T4 | Local Network.
Section 5.2.5.6.1 | Demand management initiatives proposed by Aurora to defer transmission augmentation and then install a 110 kV underground cable/overhead line from Creek Road Substation to the Kingston Tee. | A single asset failure between the Chapel Street Substation and Kingston Tee results in loss of supply to Kingston, Electrona, Knights Road, Kermandie and Huon River substations. | Proposed. | 2019-06-01 | 13.2 | Section 5.2.5.6.1 | Constraint not identified as part of (n-1) assessment. | T-T3 | Main Grid
Section 5.2.5.6.4 | Upgrade the existing Waddamana–Palmerston 220 kV line from 110 kV operation to 220 kV operation and reconfigure the Waddamana 220 kV substation. | A single 220 kV asset failure between Palmerston and Waddamana Substations could result in a blackout of the southern network under some scenarios. | Proposed. | 2016-06-01 | 26.7 | Section 5.2.5.6.4 | Constraint not identified as part of (n-1) assessment. | T-T1 | Main Grid
Section 5.2.5.6.3 | Install two 40 MVAr 110 kV capacitor banks at Creek Road Substation. | Insufficient reactive support in greater Hobart area. | Proposed. | 2015-06-01 | 4.9 | Section 5.2.5.6.5 | 2013 NSCAS identified reactive power limitation in Sothern Tasmania with all three Gordon generators out of service. |  | Local Network.
Section 5.2.5.6.6 | Install two 110/33 kV 30/60 MVA kV transformers at Bridgewater Substation complete with 110 kV and 33 kV infrastructure to supply new 33 kV sub-transmission. | Thermal capacity of the existing 110/11 kV transformers at Bridgewater. | Proposed. | 2019-06-01 | 16.8 | Section 5.2.5.6.9 | Local supply issue - not within the 2013 NTNDP scope. |  | Local Network.
Section 5.5.1 | Lindisfarne supply transformer replacement. | Condition based replacement. | Proposed. | 2016-03-01 | 5.8 | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.5.2 | Transmission line insulator assembly renewal program. | Condition based replacement. | Proposed. | Over next five years. | 10.7 | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.5.3 | Transmission protection renewal program. | Condition based replacement. | Proposed. | Over next five years. | 5.2 | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.
Section 5.5.4 | Southern Tasmanian 110 kV transmission line redevelopment. | Condition based replacement. | Proposed. | Not stated. | Not stated. | Not stated. | Condition based renewals - not within the 2013 NTNDP scope. |  | Asset Replacement.