## Commutation Faults
Year | Event | Date | Time | AC Event Description (provided by TasNetworks) | Fault Ride Through | George Town Generation (MW) | Basslink Import (MW) | Trip during AC Netwok Event | Import Limit | Commutation Failures | AC Events Recorded | Trip during Netwok Event | Successful
2006 | 1 | 2006-07-06 | 13:35 | Unknown | Successful | 0 | 205.6954 | 0 | 478 | 4 | 3 | 0 | Unsuccessful
| 2 | 2006-08-17 | 14:29 | Sheffield - Paloona 110 kV Line | Successful | 118.52 | 330.1982 | 0 | 478
| 3 | 2006-11-30 | 13:29 | George Town - Bell Bay 220 kV Trans Line No 2 | Successful | 114.68 | 183.0984 | 0 | 478
| 4 | 2006-11-30 | 13:29 | Hadspen - George Town Trans Line No 2 | Successful | 114.68 | 183.0984 | 0 | 478
2007 | 5 | 2007-02-16 | 18:30 | Liapootah Repulse – Cluny – Chapel St 220kV Transmission Line | Successful | 112.9796 | 115.3158 | 0 | 478 | 13 | 12 | 0
| 6 | 2007-02-16 | 20:28 | Liapootah Repulse – Cluny – Chapel St 220kV Transmission Line | Successful | 114.53 | 111.7034 | 0 | 478
| 7 | 2007-02-16 | 20:42 | Liapootah Repulse – Cluny – Chapel St 220kV Transmission Line | Successful | 115.38 | 89.6976 | 0 | 478
| 8 | 2007-02-23 | 19:43 | Multiple Circuit Trips in Hobart Area | Successful | 0 | 159.3055 | 0 | 478
| 9 | 2007-03-08 | 17:18 | Unknown | Successful | 111.0001 | 408.9998 | 0 | 478
| 10 | 2007-04-14 | 4:55 | Mowbray 22 kV bus event | Successful | 99.1197 | 365.0019 | 0 | 478
| 11 | 2007-04-22 | 13:07 | Trevallyn 22 kV circuit breaker trips | Successful | 115.2404 | 346.0978 | 0 | 478
| 12 | 2007-08-06 | 7:05 | Chapel Street - Kingston - Electrona 110kV Transline auto reclose | Successful | 109.5698 | 307.6001 | 0 | 478
| 13 | 2007-08-10 | 13:34 | Hadspen 220/110kV transformer trip due to 110kV dropper event. | Successful | 111.5399 | 101.2948 | 0 | 478
| 14 | 2007-08-10 | 15:26 | Gordon - Chapel Street 220kV Transmission Line | Successful | 110.3199 | 177.5994 | 0 | 478
| 15 | 2007-08-10 | 16:50 | Gordon - Chapel Street 220kV Transmission Line | Successful | 111.3599 | 149.5107 | 0 | 478
| 16 | 2007-09-27 | 21:26 | Trevallyn 22 kV circuit breaker trips | Successful | 0 | 244.2025 | 0 | 478
| 17 | 2007-12-20 | 4:13 | Sheffield - Burnie No.1 220 kV & Sheffield - Burnie No.2 110 kV Trans Line | Successful | 116.7401 | 374.1982 | 0 | 478
2008 | 18 | 2008-02-04 | 23:07 | Unknown | Successful | 176.2302 | 428.499 | 0 | 478 | 9 | 8 | 0
| 19 | 2008-02-12 | 0:52 | Trevallyn 22 kV feeder fault | Successful | 192.19 | 425.5012 | 0 | 478
| 20 | 2008-06-26 | 7:24 | Sheffield - Farrell 220 kV Transmission Line | Successful | 188.9699 | 307.596 | 0 | 478
| 21 | 2008-07-08 | 2:42 | Sheffield - Burnie 220 kV Transmission Line | Successful | 119.03 | 180.6995 | 0 | 478
| 22 | 2008-07-09 | 4:13 | Risdon - Lindisfarne 110 kV Transmission Line | Successful | 75.68 | 214.8031 | 0 | 478
| 23 | 2008-08-14 | 17:32:52.663 | Palmerston Substation Event | Successful | 0 | 387.0155 | 0 | 478
| 24 | 2008-09-26 | 7:09 | Chapel Street - Kingston - Electrona 110kV Transline auto reclose | Successful | 0 | 65.9 | 0 | 478
| 25 | 2008-12-20 | 16:14 | Palmerston - Hadspen 220kV Transmission Line | Successful | 108.2498 | 441.9993 | 0 | 478
| 26 | 2008-12-20 | 16:28 | Palmerston - Hadspen 220kV Transmission Line | Successful | 109.6903 | 434.0011 | 0 | 478
2009 | 27 | 2009-01-22 | 19:13 | Feeder faults at Hadspen and Trevallyn | Successful | 118.2001 | 445.5976 | 0 | 478 | 19 | 15 | 0
| 28 | 2009-03-14 | 9:39 | Burnie - Studland Bay and Burnie - Paloona Trip and AR | Successful | 117.3599 | 150.0948 | 0 | 478
| 29 | 2009-03-14 | 10:29 | Sheffield - Burnie NO 2, 110 kV transmission line | Successful | 117.54 | 142.7976 | 0 | 478
| 30 | 2009-03-14 | 10:49 | Unknown | Successful | 117.5 | 158.102 | 0 | 478
| 31 | 2009-03-14 | 12:09 | Liapootah - Repulse - Cluny - Chapel St 1 220 kV transmission line | Successful | 116.9901 | 82.9981 | 0 | 478
| 32 | 2009-03-24 | 15:53 | Lindisfarne 110 kV bus Zone fault | Successful | 0 | 429.0968 | 0 | 478
| 33 | 2009-03-29 | 13:26 | George Town - Tamar Valley 3 220 kV transmission line | Successful | 118.88 | 402.2982 | 0 | 478
| 34 | 2009-04-15 | 7:07 | Unknown | Successful | 17.04 | 250.9061 | 0 | 478
| 35 | 2009-04-15 | 7:13 | Sheffield - Fisher 220 kV Transmission Line | Successful | 17.04 | 250.9061 | 0 | 478
| 36 | 2009-04-15 | 7:49 | Palmerston - Avoca 110 kV Transmission line | Successful | 17.04 | 133.6008 | 0 | 478
| 37 | 2009-04-18 | 16:12157.645 | Unknown | Successful | 48.5489 | 260.597 | 0 | 478
| 38 | 2009-06-23 | 20:29 | Mowbray 22 kV cable trip | Successful | 91.4847 | 392.498 | 0 | 478
| 39 | 2009-07-14 | 18:11 | Unknown | Successful | 4.5253 | 61.5947 | 0 | 478
| 40 | 2009-08-16 | 8:24 | Ulverstone - Emu Bay and Sheffield - Burnie 2 110 kV lines trip | Successful | 0 | 152.6047 | 0 | 478
| 41 | 2009-08-16 | 8:47 | HA T152 (Palmerston - Hadspen 1 220 kV transmission line) | Successful | 0 | 176.9864 | 0 | 478
| 42 | 2009-08-16 | 8:54 | HA P152 (Hadspen - George 2 220 kV Transmission line) | Successful | 0 | 176.9864 | 0 | 478
| 43 | 2009-08-16 | 9:02 | Hadspen - Trevallyn 110 kV transmission line | Successful | 0 | 82.3989 | 0 | 478
| 44 | 2009-10-25 | 7:58 | Chapel St - Risdon 110 kV Transmission Line | Successful | 203.9 | 441.9998 | 0 | 478
| 45 | 2009-10-30 | 23:26 | Farrell - John Butters 220 kV Transmission Line | Successful | 202.9 | 408.9988 | 0 | 478
2011 | 46 | 2011-02-04 | 4:29 | Unknown | Successful | 122.6999 | 291.1989 | 0 | 478 | 1 | 0 | 0
2012 | 47 | 2012-11-15 | 19:37 | Unknown | Successful | 202.7026 | 240.5125 | 0 | 478 | 5 | 4 | 0
| 48 | 2012-11-30 | 4:44 | George Town 110 kV Customer Fault | Successful | 197.9398 | 169.1 | 0 | 478
| 49 | 2012-12-04 | 14:12 | Farrell - Rosebery - Queenstown 110 kV Transmission Line | Successful | 202.4047 | 295.4064 | 0 | 478
| 50 | 2012-12-08 | 19:32 | Sheffield - Lemonthyme 220 kV Transmission Line | Successful | 200.321 | 123.3022 | 0 | 478
| 51 | 2012-12-08 | 19:42 | Sheffield - Farrell 1 and 2, Sheffield-Cethana, Sheffield-Wilmot 220 kV Transmission Lines (West Coast Islanded) | Successful | 200.321 | 123.3022 | 0 | 478
2013 | 52 | 2013-11-22 | 17:27 | Palmerston - Hadspen No 1, 220 kV Transmission line (Auto-Reclose) | Successful | 0 | 376.5915 | 0 | 478 | 16 | 14 | 2
2014 | 53 | 2014-01-24 | 5:22 | Norwood - Scottsdale - Derby 110 kV Transmission line | Successful | 203.2977 | 221.6012 | 0 | 478
| 54 | 2014-03-05 | 3:51 | Palmerston - Hadspen No 4, 110 kV Transmission Line (Auto-Reclose) | Successful | 0 | 150.7007 | 0 | 478
| 55 | 2014-09-08 | 11:40 | George Town 220 kV Customer internal Fault | Successful | 0 | 469.9973 | 0 | 478
| 56 | 2014-09-08 | 13:21 | Sheffield - Farrell NO 2, 220 kV Transmission Line | Successful | 0 | 454.1997 | 0 | 478
| 57 | 2014-11-04 | 13:16 | Unknown | Successful | 0 | 448.6949 | 0 | 478
| 58 | 2014-11-07 | 10:41 | Unknown | Successful | 0 | 155.0033 | 0 | 478
| 59 | 2014-11-08 | 13:00 | George Town 220 kV Customer internal Fault | Successful | 0 | 263.703 | 0 | 478
| 60 | 2014-11-08 | 13:44 | George Town 220 kV Customer internal Fault | Successful | 0 | 219.7031 | 0 | 478
| 61 | 2014-11-22 | 16:27 | George Town 110 kV Customer Internal Fault | Successful | 0 | 463.3011 | 0 | 478
| 62 | 2014-11-22 | 16:33 | George Town 110 kV Customer Internal Fault | Successful | 0 | 469.3983 | 0 | 478
| 63 | 2014-11-22 | 17:27 | George Town 110 kV Customer Internal Fault | Successful | 0 | 473.1028 | 0 | 478
| 64 | 2014-12-01 | 6:03 | Sheffield - George Town No 1, 220kV Transmission Line auto reclose | Successful | 0 | 457.2004 | 0 | 478
| 65 | 2014-12-02 | 4:05 | Lindisfarne - Risdon No 2, 110 kV Trip (Auto Reclose) | Successful | 0 | 466.9998 | 0 | 478
| 66 | 2014-12-10 | 14:44 | Waddamana - Lindisfarne No 2, 220kV Transmission Line auto reclose | Unsuccessful | 0 | 426.1025 | 1 | 478
| 67 | 2014-12-16 | 7:46 | Gordon - Chapel St No 1 & 2, 220kV Transmission Line auto reclose | Unsuccessful | 0 | 459.7 | 2 | 478
| 68 | 2014-12-16 | 12:08 | Gordon - Chapel St No 1, 220kV Transmission Line auto reclose | Successful | 0 | 452.9009 | 0 | 478
2015 | 69 | 2015-01-03 | 19:33 | Lindisfarne - Risdon No 2, 110 kV Trip (Auto Reclose) | Successful | 0 | 418.7987 | 0 | 478 | 2 | 2 | 1
| 70 | 2015-02-23 | 0:53 | Gordon - Chapel St No 2, 220kV Transmission Line auto reclose | Unsuccessful | 0 | 461.91 | 3 | 478

## Historical Performance Summary
Historical Performance Summary Chart Data
| ENERGY TRANSMITTED (GWh) |  |  | Commutation Failures
Year: | Tasmania to Victoria (GWH) | Victoria to Tasmania (GWH) | Total (GWH) | Commutation Failures | Trip during Netwok Event | AC Events Recorded
2006 |  |  |  | 4 | 0 | 3
2007 | 628.49 | 1958.1 | 2586.59 | 13 | 0 | 12
2008 | 71.54 | 2841.41 | 2912.94 | 9 | 0 | 8
2009 | 559.98 | 2202.63 | 2762.6 | 19 | 0 | 15
2010 | 1084.1 | 1471.92 | 2556.02 | 0 | 0 | 0
2011 | 949.12 | 1389.69 | 2338.81 | 1 | 0 | 0
2012 | 1910.58 | 930.65 | 2841.23 | 5 | 0 | 4
2013 | 2776.14 | 76.62 | 2852.76 | 1 | 0 | 1
2014 | 2041.76 | 1097.23 | 3138.99 | 16 | 2 | 14
2015 |  |  |  | 2 | 1 | 2