## Disclaimer
Disclaimer
This modelling assumptions workbook contains data provided by or collected from third parties,
and conclusions, opinions, assumptions or forecasts that are based on that data.
AEMO has made every effort to ensure the quality of the information in this workbook but cannot guarantee
that the information, forecasts and assumptions in it are accurate, complete or appropriate for your
circumstances. This modelling assumptions workbook does not include all of the information that an investor,
participant or potential participant in the electricity or gas market might require, and does not amount to a
recommendation of any investment.
Anyone proposing to use the information in this workbook should independently verify and check its
accuracy, completeness and suitability for purpose, and obtain independent and specific advice from
appropriate experts.
This dataset or the information in it may be subsequently updated or amended. This work does
not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed
legal advice about the National Electricity Law, the National Electricity Rules, or any other applicable
laws, procedures or policies.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and
consultants involved in the preparation of this document:
• make no representation or warranty, express or implied, as to the currency, accuracy, reliability or
completeness of the information in this workbook; and
• are not liable (whether by reason of negligence or otherwise) for any statements, opinions,
information or other matters contained in or derived from this publication, or any omissions from it,
or in respect of a person’s use of the information in this workbook.

## Change log
Version History
Version Number | Date | Description
1 | 2018-03-02 | First release market modelling assumptions for 2018 ISP
2 | 2018-04-06 | Gas prices for new entrants corrected, reflecting a regional mapping error to the original consultancy forecast
QRET changed from capacity (MW) target to a consumption target, as per policy description
Augmentation options updated (with Snowy 2 and BoTN information and new Horsham link build cost)
Connection costs revised
REZ build limits updated to reflect: a) new interconnectors may provide increased access to REZs, relieving transmission limitations b) REZ transmission limits may be exceeded, with the cost of intra-regional augmentations added (on a $/MW basis).
Updated development lead time of OCGTs, reducing the development time
Added Snowy2.0 and Battery of the Nation Pumped Hydro MLF assumption
Minimum reserve level constraint applied from 2020
Added operational generation limits worksheet
Added change log worksheet
2.1 | 2018-04-20 | Updated the Pumped Hydro economic life in LCOE sheet from 30 to 50 years
Updated the wind peak contribution factors in Firm Capacity sheet
Updated VNI Option 8 transfer levels from (-900,1200) to (-1200,1500) MW in "Augmentation options" sheet
Updated the Terranora capability from (-210, 107) to (-150, 50) MW in "Interconnector Capability" sheet
Included modelled technical details of Snowy2.0 and Battery of the Nation storage / pumping parameters
2.2 | 2018-06-01 | Updated TAS Maximum demand in "Maximum Demand" sheet
Updated data source for Refurbishment in the "Assumptions Summary" sheet.
Removed LCOE sheet and description for LCOE from the "Assumptions Summary" sheet to avoid confusion on the interpretation of assumptions
Updated collation of scenarios on "Scenarios" sheet.
Updated description in "Augmentation options" sheet.
2.3 | 2018-07-17 | Removed Peakier Demand sensitivities from the "Scenarios" sheet.
Removed "Renewable Energy Zones" sheet - technology availability columns. Potential confusion with Build Limits defining what technology is available in REZs, and the Renewable Energy Zones sheet also declaring what technologies are available.
Refinement to emissions trajectory to reflect consistent starting point in 2020 for all scenarios
Reformatted for release
Updated coal forecast for new entrant coal to reflect June 2018 Resources and Energy Quarterly report (Department of Industry)
Added Liquid fuel price to the "Gas and Liquid fuel price" sheet.
Updated emissions target trajectories on "Emission Trajectory" sheet.
Updated Generic new entrant units table in "MLF" sheet.
2.4 | 2018-08-21 | Corrected emissions target trajectories on "Emission Trajectory" sheet, and described on "Scenarios" sheet, to match the baselines indicated in the ISP report and Consultation documents.
Corrections to the data reported on "DSP" sheet.
Revised the table title "DSP Relative to Operational Max Demand" in "Demand Summary" sheet to "Total NEM Summer DSP relative to NEM Operational Max Demand with coincident regional peaks".
Corrections to Rooftop PV uptakes (energy) in "Rooftop PV" sheet.
Corrections to Energy and Maximum Demand trajectories to reflect modelled assumptions.
Reformatted "Electric Vehicles" sheet.
Removed 2040 - 2050 demand forecast components to ensure consistency of data quality.
Corrected classification of Bayswater and Loy Yang A generator retirement dates as "announced" rather than "end of technical life".
Corrected formatting of High DER series on some of the figures within the "Demand Summary" sheet, to ease identification.

## Assumptions Summary
2018 Integrated System Plan modelling assumptions
This file presents tables of input data for the 2018 Integrated System Plan market modelling studies. It is a compilation of data from a number of sources, listed below.
Version History
Version Number | Date | Description
1 | 2018-03-02 | First release market modelling assumptions for 2018 ISP
2.0 | 2018-04-06 | Assumptions updated, as per Change Log worksheet
2.1 | 2018-04-20 | Assumptions updated, as per Change Log worksheet
2.2 | 2018-06-01 | Assumptions updated, as per Change Log worksheet
2.31 | 2018-07-17 | Assumptions updated, as per Change Log worksheet
2.4 | 2018-08-03 | Assumptions updated, as per Change Log worksheet
Worksheet Descriptions
Worksheet | Assumptions Grouping | Description | Source
Scenarios | Assumptions Book summary | Integrated System Plan scenario definition
Renewable Energy Zones |  | Renewable Energy Zones defined for the Integrated System Plan | AEMO internal study
Demand, Maximum Demand, Rooftop PV, Gross State Product and Electric Vehicles, DSP, Battery Aggregation | Demand Summary | Demand forecasting elements for Integrated System Plan | AEMO internal study Strong PV and battery storage informed by Bloomberg New Energy Outlook 2017
Base LRET | Renewable Policy Summary | Conversion from Clean Energy Regulator Australian LRET targets to NEM-only financial year targets that include 1997 hydroelectric baseline | Clean Energy Regulator, Office of Chief Economist
ACT Auction |  | Renewable generators assigned to supply of ACT demand above and beyond LRET targets | ACT Government
Desalination |  | Projected load for desalination with renewable proportions | Regional water authorities, desalination plant operators
GreenPower |  | Renewable energy above and beyond LRET requirement required to meet GreenPower obligations | GreenPower auditing, AEMO projection
Effective LRET |  | Combined Base LRET, ACT Auction, Desalination and GreenPower parameters
QRET and VRET |  | Target renewable settings for the Queensland and Victorian Renewable Energy Targets respectively | QLD and VIC public policy documents
Emission Trajectory |  | Whole of NEM emissions targets | Commonwealth Government, CSIRO, AEMO modelling outcomes
Interconnector Capability | Interconnector settings | Maximum forward and reverse interconnector flow capability for capacity expansion modelling | 2017 Interconnector capabilities report; adjustments for capacity expansion modelling
Proportioning factors |  | Proportion of interconnector losses applied to regional reference nodes | 2017 Regional Boundaries and Marginal Loss Factors
Augmentation options |  | Capability, cost and timing for interconnector augmentation options | AEMO internal study
Hydro Inflows | Hydro settings | Expected long-term inflow of water to hydroelectric storage reservoirs | 2016 NTNDP
Storage Initial Level |  | Expected water volumes and total storage capacity in hydroelectric storage reservoirs | BoM, regional water authorities, hydroelectric operators
Maximum capacity | Generator reliability settings | Installed capacity of existing, committed and advanced generators. Existing generators refer to maximal seasonal ratings. | Generator information (2017 December release)
Firm capacity |  | Firm capacity of existing, committed and advanced generators and new entrant generator classes | Generator information (2017 December release)
Reserves |  | Minimum reserve levels for reliable regional supply | AEMO internal study
Seasonal ratings |  | Winter and summer ratings for existing, committed, advanced and new entrant generators | Generator information (2017 December release)
Maintenance ratings |  | De-rating applied to generators under maintenance, staged construction or to track age-related degradation | Generator information (2017 December release)
Generator Reliability Settings |  | Defines a generators' forced outage rate, mean time to repair after an outage, and the derating experienced during a partial outage | AEMO internal study
Maintenance |  | The percentage of time per year that a generator is expected to be out of service for maintenance. | AEMO internal study
Build cost | Generator technical and financial settings | Build costs for new entrant generator classes | CSIRO, AEMO internal study
Connection cost |  | Cost to connect different generation classes according to NEM zone | AEMO internal study
Build limits |  | Modelled limitations impacting build constraints within the expansion modelling | AEMO internal study
Lead times |  | Modelled limitations impacting build timings within the expansion modelling | AEMO internal study
WACC |  | Weighted average cost of capital for new generation projects | AEMO internal study
Storage properties |  | Battery storage to power ratio, lifetime and round-trip efficiency | Bloomberg New Energy Finance
Coal and Biomass price |  | Coal fuel price for each coal generator | Existing generators: 2016 Wood Mackenzie Coal Cost Report New entrants: Resources and Energy Quarterly (June 2018) report, Department of Industry, Innovation and Science (AEMO conversions).
Gas and Liquid fuel price |  | Fuel price for each gas and liquid fuel generator | Core Energy Gas Pricing Consultancy Databook (March 2017 Update) Fuel and technology cost review (ACIL Allen)
Refurbishment |  | Cost and timing for refurbishment of ageing generators | Public announcements, AEMO internal study
Retirement |  | Announced and end-of-technical-life generator retirement | Public announcements, AEMO internal study
Heat rates |  | Efficiency of conversion of fuel to output for thermal generators | Fuel and technology cost review (ACIL Allen)
Auxiliary |  | Auxiliary (self) load for each generator or generator class | Fuel and technology cost review (ACIL Allen)
Fixed OPEX |  | Fixed operating cost regardless of output for each generator or generator class | Fuel and technology cost review (ACIL Allen)
Variable OPEX |  | Variable operating cost per MWh of output for each generator or generator class | Fuel and technology cost review (ACIL Allen)
Emissions |  | Emissions production per MWh of output for each generator or generator class | ACIL Allen - AEMO Emissions Factors Update 2016
MLF |  | Marginal loss factors for each generator | 2017 Regional Boundaries and Marginal Loss Factors

## Scenarios
Scenario settings
| Central Cases |  | Scenarios |  |  | Sensitivities |  | Counterfactual
Scenario/sensitivity | Neutral | Neutral with Storage Initiative | Slow Change | Fast Change | High DER | Increased role for gas | Early coal retirement | No Interconnector development
Demand Settings
Economic growth and population outlook | Neutral | Neutral | Weak | Strong | Neutral | Neutral | Neutral | Neutral
Rooftop PV - up to 100 kW | Neutral | Neutral | Neutral | Neutral | Strong | Neutral | Neutral | Neutral
Non-scheduled PV - from 100 kW to 30 MW | Neutral | Neutral | Neutral | Neutral | Strong | Neutral | Neutral | Neutral
Demand Side Participation | Neutral | Neutral | Strong | Weak | Strong | Neutral | Neutral | Neutral
Electric Vehicle Uptake | Neutral | Neutral | Weak | Strong | Neutral | Neutral | Neutral | Neutral
Battery storage installed capacity | Neutral | Neutral | Neutral | Neutral | Strong | Neutral | Neutral | Neutral
Battery storage aggregation by 2050 | 45% | 45% | 90% | 10% | 90% | 45% | 45% | 45%
Policy Settings
Emissions trajectory | 28% 2005 - 2030 | 28% 2005 - 2030 | 28% 2005 - 2030 | 52% 2005 - 2030 | 28% 2005 - 2030 | 28% 2005 - 2030 | 28% 2005 - 2030 | 28% 2005 - 2030
| 70% 2016 - 2050 | 70% 2016 - 2050 | 70% 2016 - 2050 | 90% 2005 - 2050 | 70% 2016 - 2050 | 70% 2016 - 2050 | 70% 2016 - 2050 | 70% 2016 - 2050
LRET | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
VRET 25% by 2020 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
VRET 40% by 2025 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Queensland Renewables 400 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
QRET 50% by 2030 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Energy Efficiency Improvement | Neutral | Neutral | Weak | Strong | Neutral | Neutral | Neutral | Neutral
Supply Side Settings
Coal plant retirements | Model outcome Life extension possible | Model outcome Life extension possible | Model outcome Life extension possible | Model outcome Life extension possible | Model outcome Life extension possible | Model outcome Life extension possible | Model outcome Life extension possible | Model outcome Life extension possible
Variable renewable energy (wind and utility PV) cost reductions | Neutral | Neutral | Slow | Neutral | Neutral | Slow | Neutral | Neutral
Storage (Pumped Hydro, battery and solar thermal) cost reductions | Neutral | Neutral | Neutral | Rapid | Slow | Slow | Neutral | Neutral
Gas Market Settings
Gas demand - LNG export | Neutral | Neutral | Weak | Strong | Neutral | Neutral | Neutral | Neutral
Gas demand - Residential/Commercial/Industrial | Neutral | Neutral | Weak | Strong* | Neutral | Neutral | Neutral | Neutral
Gas prices | IM outcome (Neutral base) | IM outcome (Neutral base) | IM outcome (Weak base) | IM outcome (Strong base) | IM outcome (Neutral base) | Lower bound reflecting production costs. $6/GJ floor | IM outcome (Neutral base) | IM outcome (Neutral base)
Gas demand - gas powered generation | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas | Model outcome Assume ADGSM process remains to secure domestic gas
New gas supplies | Model outcome | Model outcome | Model outcome | Model outcome | Model outcome | Increased supplies assumed to drive low domestic prices | Model outcome | Model outcome
Hydrogen blending in gas | None | None | None | None | None | None | None | None
Interconnector development settings
Interconnector development settings | Model outcome | Includes development of Snowy 2.0 and BoTN, including relevant interconnector developments. Model to choose other development options | Model outcome | Model outcome | Model outcome | Model outcome | Model outcome | No Interconnector development options available

## Renewable Energy Zones
Renewable Energy Zones
# | Name | NEM Region | NEM Zone
0 | Far North QLD | Qld | NQ
1 | North Qld Clean Energy Hub | Qld | NQ
2 | Northern Qld | Qld | NQ
3 | Barcaldine | Qld | CQ
4 | Isaac | Qld | NQ
5 | Fitzroy | Qld | CQ
6 | Darling Downs | Qld | SWQ
7 | North West NSW | NSW | NNS
8 | Northern NSW Tablelands | NSW | NNS
9 | Central NSW Tablelands | NSW | NCEN
10 | Central West NSW | NSW | NCEN
11 | Southern NSW Tablelands | NSW | CAN
12 | Broken Hill | NSW | SWNSW
13 | Murray River (NSW) | NSW | SWNSW
| Murray River (Vic) | Vic | NVIC
14 | Western Victoria | Vic | CVIC
15 | Moyne | Vic | MEL
16 | Gippsland | Vic | LV
17 | South East SA | SA | SESA
18 | Riverland (SA) | SA | NSA
| Riverland (NSW) | NSW | SWNSW
19 | Mid-North SA | SA | NSA
20 | Yorke Peninsula | SA | NSA
21 | Northern SA | SA | NSA
22 | Leigh Creek | SA | NSA
23 | Roxby Downs | SA | NSA
24 | Eastern Eyre Peninsula | SA | NSA
25 | Western Eyre Peninsula | SA | NSA
26 | King island | Tas | TAS
27 | North East Tasmania | Tas | TAS
28 | North West Tasmania | Tas | TAS
29 | Tasmania Midlands | Tas | TAS
30 | New England | NSW | NNS
31 | Tumut | NSW | CAN
32 | Cooma-Monaro | NSW | CAN
33 | Ovens Murray | Vic | NVIC

## Demand Summary
Demand Summary
NEM Gross State Product growth
| Economic Growth | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Neutral BAU | Neutral | 100% | 103.1% | 106.2% | 109.2% | 112.6% | 115.8% | 119.2% | 122.6% | 126.1% | 129.6% | 133.2% | 136.8% | 140.3% | 143.7% | 147% | 150.4% | 153.8% | 157.2% | 160.7% | 164.2% | 167.8%
Fast Change | Strong | 100% | 103.8% | 107.6% | 111.5% | 115.8% | 120% | 124.4% | 129% | 133.7% | 138.5% | 143.4% | 148.5% | 153.5% | 158.5% | 163.6% | 168.7% | 173.9% | 179.3% | 184.7% | 190.4% | 196.1%
Slow Change | Weak | 100% | 102.4% | 104.8% | 107% | 109.5% | 111.8% | 114.2% | 116.6% | 119% | 121.4% | 123.8% | 126.2% | 128.4% | 130.5% | 132.6% | 134.6% | 136.6% | 138.6% | 140.6% | 142.6% | 144.6%
High DER | Neutral | 100% | 103.1% | 106.2% | 109.2% | 112.6% | 115.8% | 119.2% | 122.6% | 126.1% | 129.6% | 133.2% | 136.8% | 140.3% | 143.7% | 147% | 150.4% | 153.8% | 157.2% | 160.7% | 164.2% | 167.8%
PV Generation Relative to Underlying Demand
| PV versus Demand | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Neutral BAU | Neutral PV versus Neutral Demand | 4.278% | 5.006% | 5.609% | 6.285% | 6.962% | 7.643% | 8.219% | 8.858% | 9.372% | 9.885% | 10.44% | 11.06% | 11.53% | 12.03% | 12.43% | 12.88% | 13.21% | 13.36% | 13.65% | 13.73% | 13.86% | 13.99% | 14.07%
Fast Change | Neutral PV versus Strong Demand | 4.203% | 4.91% | 5.481% | 6.108% | 6.77% | 7.389% | 7.923% | 8.578% | 9.03% | 9.411% | 9.915% | 10.35% | 10.74% | 11.07% | 11.34% | 11.6% | 11.83% | 11.81% | 11.93% | 12.23% | 12.43% | 12.77% | 13.11%
Weak | Neutral PV versus Weak Demand | 4.55% | 5.261% | 6% | 6.755% | 7.569% | 8.354% | 9.075% | 9.768% | 10.37% | 11.02% | 11.7% | 12.51% | 13.33% | 14.05% | 14.98% | 15.96% | 16.73% | 17.61% | 18.3% | 18.97% | 19.33% | 19.81% | 20.16%
High DER | Strong PV versus Neutral Demand | 4.104% | 4.71% | 5.218% | 5.748% | 6.314% | 6.942% | 7.541% | 8.215% | 8.918% | 9.726% | 10.71% | 11.98% | 13.38% | 15.05% | 16.68% | 18.25% | 19.63% | 20.5% | 21.39% | 21.71% | 22.1% | 22.37% | 22.65%
Total NEM Summer DSP relative to NEM Operational Max Demand with coincident regional peaks
| DSP versus Demand | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Neutral BAU | Neutral DSP versus Neutral Demand | 1.114% | 1.125% | 1.272% | 1.393% | 1.555% | 1.681% | 1.793% | 1.929% | 2.054% | 2.179% | 2.355% | 2.506% | 2.617% | 2.777% | 2.902% | 3.018% | 3.19% | 3.272% | 3.397% | 3.596% | 3.686% | 3.838% | 3.992%
Fast Change | Strong DSP versus Strong Demand | 1.089% | 1.103% | 1.318% | 1.504% | 1.731% | 1.959% | 2.154% | 2.365% | 2.582% | 2.741% | 3.005% | 3.222% | 3.362% | 3.62% | 3.777% | 3.962% | 4.213% | 4.295% | 4.478% | 4.792% | 4.951% | 5.213% | 5.457%
Weak | Weak DSP versus Weak Demand | 1.18% | 1.201% | 1.218% | 1.206% | 1.238% | 1.242% | 1.235% | 1.247% | 1.235% | 1.239% | 1.264% | 1.283% | 1.287% | 1.309% | 1.328% | 1.353% | 1.397% | 1.404% | 1.414% | 1.442% | 1.418% | 1.425% | 1.433%
High DER | Strong DSP versus Neutral Demand | 1.114% | 1.125% | 1.359% | 1.562% | 1.803% | 2.026% | 2.233% | 2.461% | 2.684% | 2.876% | 3.161% | 3.397% | 3.58% | 3.856% | 4.059% | 4.257% | 4.547% | 4.682% | 4.927% | 5.238% | 5.447% | 5.712% | 5.979%
EV % of Vehicle Fleet
| EV uptake versus Fleet Size | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Neutral BAU | Neutral EV uptake | 0.09105% | 0.1964% | 0.318% | 0.5047% | 0.77% | 1.124% | 1.582% | 2.115% | 3.075% | 4.031% | 5.036% | 6.16% | 7.373% | 8.669% | 10.07% | 11.58% | 13.14% | 14.81% | 16.81% | 18.88% | 20.92%
Fast Change | Strong EV uptake | 0.2621% | 0.5466% | 0.8684% | 1.372% | 2.433% | 3.7% | 5.177% | 6.754% | 8.375% | 9.994% | 12.81% | 16.2% | 19.95% | 23.43% | 26.79% | 30.36% | 34.87% | 39.87% | 44.53% | 49.14% | 53.2%
Weak | Weak EV uptake | 0.03167% | 0.07222% | 0.1152% | 0.1737% | 0.2649% | 0.3934% | 0.5683% | 0.7803% | 1.022% | 1.285% | 1.63% | 2.029% | 2.469% | 2.878% | 3.332% | 3.83% | 4.401% | 5.018% | 5.708% | 6.453% | 7.199%
High DER | Neutral EV uptake | 0.09105% | 0.1964% | 0.318% | 0.5047% | 0.77% | 1.124% | 1.582% | 2.115% | 3.075% | 4.031% | 5.036% | 6.16% | 7.373% | 8.669% | 10.07% | 11.58% | 13.14% | 14.81% | 16.81% | 18.88% | 20.92%
Battery Storage Capacity Relative to Operational Max Demand
| Battery uptake versus MD | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Neutral BAU | Neutral uptake versus Neutral MD | 0.3106% | 0.8207% | 1.596% | 2.595% | 3.525% | 4.425% | 5.239% | 6.039% | 6.806% | 7.456% | 8.214% | 8.98% | 9.625% | 10.34% | 10.94% | 11.43% | 12.05% | 12.39% | 12.77% | 13.33% | 13.8% | 14.15% | 14.6%
Fast Change | Neutral uptake versus Strong MD | 0.3035% | 0.8043% | 1.548% | 2.499% | 3.384% | 4.281% | 5.054% | 5.803% | 6.545% | 7.108% | 7.81% | 8.518% | 9.039% | 9.711% | 10.18% | 10.64% | 11.16% | 11.37% | 11.61% | 12.19% | 12.54% | 12.91% | 13.32%
Weak | Neutral uptake versus Weak MD | 0.3289% | 0.8756% | 1.705% | 2.771% | 3.782% | 4.78% | 5.685% | 6.593% | 7.406% | 8.157% | 8.96% | 9.843% | 10.68% | 11.58% | 12.5% | 13.4% | 14.36% | 15.05% | 15.65% | 16.42% | 17.01% | 17.44% | 18%
High DER | Strong uptake versus Neutral MD | 0.4092% | 0.6823% | 1.057% | 1.501% | 2.081% | 2.777% | 3.573% | 4.496% | 5.551% | 6.65% | 7.985% | 9.486% | 11.03% | 12.91% | 15% | 17.35% | 20.33% | 23.31% | 26.56% | 30.27% | 33.64% | 36.6% | 39.12%

## Demand
Energy Consumption (GWh)
Amount of energy consumed by customers in each region in each financial year
Operational demand
Energy consumption which is net of rooftop PV generation
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 67717.1622 | 65295.5657 | 66089.2716 | 65850.9496 | 65666.0335 | 64660.6017 | 64881.2876 | 64215.0193 | 63698.1127 | 64842.5016 | 64976.2386 | 64523.0615 | 64441.1835 | 63010.5511 | 63860.0039 | 64925.091 | 64484.8948 | 65323.2988 | 65451.3216 | 66739.2878 | 67235.0197 | 67820.479 | 68411.5074
QLD | 51016.4265 | 50496.1096 | 50395.1823 | 50471.2494 | 50628.9137 | 50667.1326 | 50723.2894 | 51029.6355 | 52392.7383 | 51992.69 | 51912.7804 | 51364.851 | 51485.927 | 52182.3354 | 52111.466 | 50889.0867 | 51727.991 | 51809.1926 | 52353.8154 | 53083.7517 | 53592.4937 | 54149.1887 | 54809.9279
SA | 12154.5089 | 10843.1563 | 12266.9702 | 12203.4267 | 12066.4034 | 11353.7181 | 11889.4744 | 11234.7486 | 10932.6766 | 10713.263 | 10989.1651 | 10301.3912 | 10111.2666 | 10133.1656 | 10145.8075 | 9852.4426 | 9594.6932 | 9566.6943 | 9646.6569 | 9689.9254 | 9744.6038 | 9783.6696 | 9873.5995
TAS | 10373.5052 | 10423.0415 | 10379.8017 | 10346.857 | 9930.599 | 9906.4527 | 9883.3405 | 9896.4074 | 9979.1069 | 10062.6824 | 10142.087 | 10224.1508 | 10232.4689 | 10220.3344 | 10217.8888 | 10206.3073 | 10283.5367 | 10360.1435 | 10430.719 | 10474.2534 | 10528.2704 | 10585.031 | 10646.5282
VIC | 43577.3158 | 42751.4959 | 42548.1357 | 42533.8664 | 42630.2236 | 42769.8543 | 43116.7882 | 43191.1153 | 43343.694 | 43338.5163 | 43525.5457 | 42810.9993 | 43075.4681 | 42624.9345 | 42763.9122 | 42438.5006 | 42260.1359 | 43918.7885 | 43546.1743 | 44050.7356 | 44535.0901 | 45021.1414 | 45571.608
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 68812.5348 | 66360.2468 | 67460.2804 | 67743.333 | 67007.8361 | 66906.1125 | 67002.2968 | 65797.3937 | 66941.4113 | 68452.7148 | 69812.1073 | 69858.0751 | 70163.2189 | 70553.2613 | 71428.2877 | 73633.8933 | 74342.8293 | 76629.1328 | 77804.4427 | 78140.8988 | 78572.3193 | 76932.0654 | 75532.242
QLD | 52095.5113 | 51758.9934 | 51901.1403 | 52212.7422 | 53199.6802 | 53496.6191 | 53960.5309 | 53921.8379 | 54281.6008 | 55769.8524 | 56166.9621 | 56261.1146 | 56554.6343 | 57549.0686 | 58293.6406 | 57951.2003 | 58390.7463 | 59803.3171 | 60893.0023 | 59547.8663 | 58415.2578 | 57229.8999 | 56353.364
SA | 12445.0496 | 11014.2063 | 12650.8623 | 12682.2964 | 12083.8472 | 11767.8187 | 11956.933 | 11425.4641 | 11345.4479 | 11173.2229 | 11159.6265 | 10882.5643 | 10985.4551 | 11128.4904 | 11278.7436 | 11331.8621 | 11368.7225 | 11610.0979 | 11803.8111 | 12171.0799 | 12092.0855 | 11848.3856 | 11828.092
TAS | 10617.1551 | 10668.0483 | 10665.3912 | 10699.7499 | 10676.1451 | 10674.6221 | 10683.1363 | 10719.9589 | 10814.4691 | 10909.387 | 11010.4435 | 11112.7127 | 11206.3144 | 11316.5094 | 11422.4236 | 11542.6628 | 11681.5443 | 11816.3155 | 11926.5654 | 12037.9158 | 12133.4569 | 12229.294 | 12328.4965
VIC | 44281.7632 | 43689.8741 | 43486.6503 | 43674.5791 | 43462.1114 | 43175.3073 | 44238.286 | 44128.7434 | 44490.6255 | 44742.6824 | 44133.0788 | 44911.1235 | 45253.7287 | 45236.5961 | 46331.8752 | 46441.1545 | 46428.3251 | 48503.6776 | 49242.6208 | 48297.2432 | 49169.1968 | 49891.3379 | 49426.4743
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 63291.6876 | 62278.461 | 61767.8418 | 61408.189 | 61184.3681 | 60765.7547 | 60393.7637 | 60191.9568 | 60134.8487 | 59907.9841 | 59923.1514 | 56735.9958 | 53660.5836 | 50566.2188 | 49269.2681 | 47931.9331 | 47404.6696 | 47293.3776 | 46941.0864 | 46178.3548 | 45969.1458 | 45827.2463 | 45661.0496
QLD | 47891.5891 | 47059.6184 | 46316.6178 | 45803.2373 | 45476.5745 | 45627.181 | 45206.2373 | 44631.5604 | 44698.6504 | 44206.7532 | 43593.416 | 43149.0036 | 42811.6435 | 42655.3441 | 39920.6104 | 37106.9103 | 35289.9131 | 33173.3952 | 32849.27 | 31970.7012 | 31391.8292 | 30757.4542 | 30300.7732
SA | 11401.74 | 11168.129 | 11561.3605 | 11443.3436 | 11343.3245 | 11239.6395 | 11155.7208 | 11004.8806 | 10834.1118 | 10548.0754 | 10708.0389 | 10392.3432 | 10108.0349 | 10331.9146 | 10145.3236 | 9474.5659 | 9340.715 | 8335.3617 | 7850.9148 | 7725.3472 | 7687.5332 | 7591.5664 | 7585.731
TAS | 9866.9688 | 9904.9391 | 9611.9255 | 9506.126 | 9416.7116 | 9391.1841 | 9367.5005 | 9371.3117 | 9431.8199 | 9493.3843 | 9540.0546 | 9574.3332 | 9588.3464 | 9595.3366 | 9546.9134 | 9419.5995 | 9039.1453 | 8850.5893 | 7793.6159 | 7544.3962 | 7880.0515 | 7644.9865 | 7789.5832
VIC | 40845.1383 | 40219.5853 | 39869.2157 | 39780.7826 | 37906.568 | 35811.6028 | 35823.2562 | 36002.7404 | 36050.5344 | 36051.4173 | 35973.6283 | 35917.8484 | 35768.6124 | 35927.6231 | 35467.9118 | 34812.6413 | 34074.0501 | 32888.0356 | 32582.8308 | 31757.5055 | 31694.7731 | 31524.8667 | 31457.3689
Underlying demand
Energy consumption that is equivalent to the 'powerpoint' - gross of rooftop PV generation and other small non-scheduled systems
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 69982.7648 | 68018.7668 | 69315.4517 | 69615.4617 | 69977.9012 | 69505.5252 | 70277.94 | 70164.6346 | 70167.7769 | 71827.8669 | 72532.6583 | 72571.8607 | 72993.8603 | 72001.5632 | 73334.7945 | 74814.0488 | 74716.0233 | 75894.6811 | 76381.4701 | 77988.0267 | 78748.8789 | 79611.9259 | 80458.1094
QLD | 54001.4828 | 53814.7966 | 54086.6754 | 54538.9457 | 55071.8651 | 55449.8072 | 55853.9098 | 56476.0251 | 58147.1775 | 58055.3007 | 58313.7046 | 58046.7829 | 58445.0464 | 59409.3223 | 59609.375 | 58616.6607 | 59638.6889 | 59905.1121 | 60627.1388 | 61476.265 | 62096.586 | 62773.6665 | 63538.0364
SA | 13341.2226 | 12128.4684 | 13656.8944 | 13707.6562 | 13688.5215 | 13091.9738 | 13746.6179 | 13211.0077 | 13017.6576 | 12914.7614 | 13321.9526 | 12751.2721 | 12677.6736 | 12805.157 | 12936.0737 | 12752.4532 | 12596.8661 | 12662.227 | 12841.2888 | 12965.3998 | 13104.3315 | 13230.644 | 13399.0153
TAS | 10527.1511 | 10600.9969 | 10581.8366 | 10573.2684 | 10179.2434 | 10171.0753 | 10157.8289 | 10177.3631 | 10262.6658 | 10349.297 | 10433.8249 | 10519.5995 | 10530.4256 | 10520.2735 | 10521.1541 | 10513.2447 | 10593.6573 | 10672.8779 | 10747.6575 | 10793.8722 | 10850.2224 | 10910.7311 | 10975.7039
VIC | 45246.2891 | 44721.4468 | 44834.6159 | 45137.5547 | 45543.4837 | 45981.7841 | 46621.3057 | 46989.6629 | 47400.0541 | 47650.3222 | 48107.3903 | 47613.9871 | 48072.2453 | 47806.1586 | 48129.613 | 47973.8932 | 47949.4613 | 49743.1095 | 49505.4962 | 50115.2572 | 50699.94 | 51301.4972 | 51952.541
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 71078.1374 | 69083.4478 | 70686.4605 | 71507.8451 | 71319.7039 | 71751.036 | 72398.9492 | 71747.009 | 73411.0755 | 75438.0801 | 77368.527 | 77906.8744 | 78715.8957 | 79544.2734 | 80903.0783 | 83522.8511 | 84573.9578 | 87200.5151 | 88734.5912 | 89389.6377 | 90086.1785 | 88723.5123 | 87578.844
QLD | 55080.5676 | 55077.6805 | 55592.6334 | 56280.4386 | 57642.6315 | 58279.2937 | 59091.1513 | 59368.2275 | 60036.04 | 61832.4631 | 62567.8862 | 62943.0466 | 63513.7537 | 64776.0555 | 65791.5495 | 65678.7742 | 66301.4443 | 67899.2366 | 69166.3257 | 67940.3796 | 66919.3501 | 65854.3777 | 65081.4725
SA | 13631.7633 | 12299.5184 | 14040.7864 | 14186.5259 | 13705.9653 | 13506.0744 | 13814.0765 | 13401.7232 | 13430.4289 | 13374.7213 | 13492.4141 | 13332.4452 | 13551.862 | 13800.4818 | 14069.0098 | 14231.8726 | 14370.8955 | 14705.6306 | 14998.443 | 15446.5543 | 15451.8132 | 15295.3599 | 15353.5078
TAS | 10770.801 | 10846.0036 | 10867.426 | 10926.1613 | 10924.7894 | 10939.2447 | 10957.6248 | 11000.9146 | 11098.0279 | 11196.0016 | 11302.1813 | 11408.1614 | 11504.2712 | 11616.4486 | 11725.6889 | 11849.6003 | 11991.6649 | 12129.0498 | 12243.5039 | 12357.5346 | 12455.4089 | 12554.9941 | 12657.6722
VIC | 45950.7365 | 45659.825 | 45773.1305 | 46278.2674 | 46375.3716 | 46387.2372 | 47742.8036 | 47927.291 | 48546.9856 | 49054.4883 | 48714.9234 | 49714.1113 | 50250.5059 | 50417.8202 | 51697.576 | 51976.5472 | 52117.6505 | 54327.9987 | 55201.9426 | 54361.7648 | 55334.0467 | 56171.6937 | 55807.4073
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 65557.2902 | 65001.6621 | 64994.022 | 65172.7011 | 65496.2359 | 65610.6782 | 65790.4162 | 66141.5721 | 66604.513 | 66893.3494 | 67479.5711 | 64784.7951 | 62213.2604 | 59557.2309 | 58744.0587 | 57820.8909 | 57635.7981 | 57864.7599 | 57871.2348 | 57427.0936 | 57483.005 | 57618.6932 | 57707.6516
QLD | 50876.6454 | 50378.3054 | 50008.1109 | 49870.9336 | 49919.5259 | 50409.8556 | 50336.8577 | 50077.9499 | 50453.0896 | 50269.3639 | 49994.3402 | 49830.9356 | 49770.7629 | 49882.331 | 47418.5193 | 44834.4842 | 43200.611 | 41269.3147 | 41122.5935 | 40363.2145 | 39895.9215 | 39381.932 | 39028.8817
SA | 12588.4537 | 12453.4411 | 12951.2847 | 12947.573 | 12965.4426 | 12977.8951 | 13012.8643 | 12981.1397 | 12919.0928 | 12749.5738 | 13040.8265 | 12842.2241 | 12674.4419 | 13003.906 | 12935.5898 | 12374.5765 | 12342.8879 | 11430.8944 | 11045.5467 | 11000.8216 | 11047.2609 | 11038.5408 | 11111.1468
TAS | 10020.6147 | 10082.8944 | 9813.9604 | 9732.5374 | 9665.3559 | 9655.8067 | 9641.989 | 9652.2674 | 9715.3788 | 9779.9989 | 9831.7925 | 9869.7819 | 9886.3032 | 9895.2758 | 9850.1788 | 9726.5369 | 9349.266 | 9163.3237 | 8110.5544 | 7864.015 | 8202.0035 | 7970.6866 | 8118.7589
VIC | 42514.1116 | 42189.5362 | 42155.6958 | 42384.4709 | 40819.8281 | 39023.5326 | 39327.7738 | 39801.2881 | 40106.8945 | 40363.2232 | 40555.4729 | 40720.8361 | 40765.3897 | 41108.8471 | 40833.6127 | 40348.034 | 39763.3755 | 38712.3566 | 38542.1527 | 37822.0271 | 37859.623 | 37805.2225 | 37838.3019

## Maximum Demand
Maximum Demand (Power, MW)
Amount of power that must be generated at times of peak operational demand. Peak operational demand occurs in Summer months in all NEM regions except Tasmania.
10% Probability of exceedance
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 14174.5074 | 14115.2155 | 13944.9701 | 13925.3388 | 13892.111 | 13777.8832 | 13829.4859 | 13992.0256 | 13934.696 | 14176.5628 | 14104.0308 | 14052.3749 | 14190.605 | 14150.0535 | 14166.0818 | 14303.3451 | 14187.395 | 14309.3076 | 14556.6881 | 14597.808 | 14600.4834 | 14605.903 | 14615.0272
QLD | 9427.3802 | 9452.4247 | 9327.9071 | 9543.9967 | 9514.2752 | 9647.5914 | 9648.8835 | 9548.6114 | 9668.4424 | 9954.7503 | 9997.3533 | 9944.5864 | 10004.928 | 9886.0401 | 9857.4725 | 10110.3858 | 10180.8309 | 10217.9401 | 10313.154 | 10051.0297 | 10059.1147 | 10067.5866 | 10076.6658
SA | 3241.9067 | 3029.6853 | 3047.6314 | 2961.5144 | 2931.1783 | 2904.928 | 2901.0951 | 2946.7213 | 2951.0788 | 2918.6142 | 2907.9915 | 2872.149 | 2885.3631 | 2883.7271 | 2889.2793 | 2860.6437 | 2837.0377 | 2855.2411 | 2896.2365 | 2898.7194 | 2900.7218 | 2902.8042 | 2905.0162
TAS | 1801.9246 | 1804.2916 | 1791.5492 | 1788.5129 | 1722.0182 | 1715.7191 | 1724.8434 | 1711.896 | 1729.6232 | 1733.7061 | 1745.4913 | 1754.7761 | 1753.2591 | 1750.2671 | 1748.4594 | 1740.1909 | 1744.9195 | 1758.1071 | 1765.7444 | 1765.574 | 1766.1936 | 1766.8583 | 1767.6695
VIC | 9777.9234 | 9648.1395 | 9557.3693 | 9443.418 | 9486.7527 | 9377.2712 | 9603.2487 | 9691.9458 | 9743.3388 | 9856.1107 | 9795.7354 | 9750.802 | 9851.488 | 9812.23 | 9849.1858 | 9786.5962 | 9661.2311 | 10073.2717 | 10139.4178 | 10173.5225 | 10179.8 | 10186.2834 | 10193.1803
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 14488.9699 | 14237.1458 | 14435.9848 | 14474.6883 | 14238.3433 | 14109.3217 | 14256.2092 | 14410.349 | 14544.2025 | 14793.3254 | 14865.5337 | 14788.581 | 15075.2003 | 15104.2564 | 15357.6589 | 15443.3139 | 15450.4035 | 15607.1948 | 15924.4349 | 16100.5241 | 16120.4564 | 16139.9741 | 16159.7421
QLD | 9778.7892 | 9833.2907 | 9567.8404 | 9812.4448 | 10019.3847 | 10182.0255 | 10159.7496 | 10000.1095 | 10034.1398 | 10566.5036 | 10554.2757 | 10606.8103 | 10817.8201 | 10563.6992 | 10597.7771 | 10803.8547 | 10957.8086 | 11036.7316 | 11513.0024 | 10856.5238 | 10984.9876 | 11024.7627 | 11136.2915
SA | 3306.2363 | 3098.0188 | 3274.6632 | 3223.4481 | 3241.789 | 3003.6176 | 2990.252 | 3051.8464 | 3067.2251 | 3035.9511 | 3030.6615 | 3019.3031 | 3076.1989 | 3078.7215 | 3084.5986 | 3079.8271 | 3068.5118 | 3080.229 | 3366.273 | 3287.8063 | 3458.6887 | 3255.9707 | 3174.954
TAS | 1845.7082 | 1840.7708 | 1833.736 | 1840.1643 | 1827.1557 | 1826.5486 | 1831.245 | 1839.9253 | 1842.4928 | 1863.4279 | 1865.5938 | 1882.2994 | 1888.08 | 1900.7677 | 1911.1838 | 1924.2844 | 1930.2709 | 1942.3591 | 1950.2484 | 1961.0271 | 1962.6184 | 1964.1809 | 1965.8653
VIC | 9897.602 | 9814.0756 | 9723.8448 | 9761.2015 | 9789.6571 | 9568.455 | 9847.0222 | 10133.7076 | 10049.7498 | 10274.5795 | 10232.8802 | 10162.2136 | 10333.6234 | 10338.0784 | 10436.0726 | 10442.2607 | 10261.1481 | 11073.1915 | 10892.3691 | 10949.3298 | 10936.6134 | 10925.036 | 10903.7103
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 13334.4879 | 13209.1114 | 13059.5958 | 13106.8327 | 13073.8571 | 12996.8662 | 12911.0922 | 13029.117 | 13190.2085 | 13298.1131 | 13315.8544 | 12870.8413 | 12662.1065 | 12320.4535 | 12082.505 | 11753.6111 | 11765.6359 | 11884.0262 | 11886.1007 | 11968.787 | 11976.1693 | 11983.7153 | 11991.5335
QLD | 9101.8442 | 8925.8658 | 8707.8361 | 8840.8506 | 8878.9916 | 8999.5594 | 8999.4075 | 8726.0109 | 8754.2352 | 8983.1605 | 9017.7186 | 9061.5495 | 9031.4207 | 8796.4307 | 8464.7567 | 8328.7629 | 8064.2703 | 7947.1861 | 7863.9064 | 7564.4814 | 7567.4486 | 7570.5587 | 7573.8778
SA | 3039.1052 | 2834.9611 | 2865.8187 | 2794.4964 | 2776.4859 | 2751.6043 | 2709.1543 | 2797.594 | 2772.7478 | 2733.134 | 2748.0398 | 2708.2848 | 2756.609 | 2768.143 | 2748.9724 | 2661.6651 | 2601.8378 | 2596.0469 | 2639.7953 | 2644.2339 | 2645.3648 | 2646.6095 | 2647.8993
TAS | 1723.8293 | 1732.5957 | 1678.5034 | 1663.3454 | 1640.3043 | 1641.3898 | 1638.1147 | 1636.4305 | 1646.0552 | 1658.5548 | 1656.6263 | 1662.6806 | 1660.3136 | 1660.5593 | 1654.0398 | 1635.6738 | 1577.0255 | 1544.8179 | 1523.7835 | 1501.5739 | 1501.5414 | 1501.5257 | 1501.558
VIC | 9083.0169 | 8960.4003 | 8939.1911 | 8862.9842 | 8632.0876 | 8259.2455 | 8486.2585 | 8521.4026 | 8580.2522 | 8646.3327 | 8603.9695 | 8706.6445 | 8742.6611 | 8814.7276 | 8752.7498 | 8713.2769 | 8389.0929 | 8317.2194 | 8444.9189 | 8364.0018 | 8366.7769 | 8369.6355 | 8372.6411
50% Probability of exceedance
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 13289.745 | 13138.5986 | 12916.9596 | 12817.5278 | 12880.966 | 12718.1354 | 12803.9588 | 12804.7576 | 12702.6841 | 12828.2795 | 12941.7742 | 12992.2988 | 12993.4085 | 12905.6316 | 12725.9187 | 13035.3041 | 12945.7446 | 13119.7617 | 13239.3441 | 13034.3595 | 13046.018 | 13058.0961 | 13070.9239
QLD | 8927.1342 | 8887.419 | 8807.3621 | 8980.3169 | 8916.7791 | 8982.3513 | 9113.6557 | 8996.0867 | 9255.2021 | 9383.7119 | 9320.4944 | 9435.4667 | 9389.5542 | 9349.3307 | 9429.5743 | 9442.6513 | 9439.7344 | 9638.6852 | 9695.3619 | 9608.6304 | 9617.0193 | 9625.7951 | 9635.1783
SA | 2877.9377 | 2828.5093 | 2862.77 | 2794.691 | 2770.6921 | 2738.9885 | 2718.9279 | 2759.0582 | 2771.7532 | 2740.1113 | 2745.6352 | 2681.7288 | 2675.2845 | 2700.4396 | 2704.4055 | 2694.1637 | 2675.8196 | 2670.4281 | 2689.2054 | 2712.5187 | 2714.503 | 2716.5674 | 2718.7614
TAS | 1760.7671 | 1767.7368 | 1759.6949 | 1751.5714 | 1695.1787 | 1692.5172 | 1688.4564 | 1691.5807 | 1701.2725 | 1712.3249 | 1719.8884 | 1728.8376 | 1728.6123 | 1724.2373 | 1721.1408 | 1714.5294 | 1723.7132 | 1729.6258 | 1736.772 | 1738.921 | 1739.4075 | 1739.9143 | 1740.4572
VIC | 8989.5588 | 8986.7446 | 8877.9771 | 8757.0331 | 8868.7131 | 8769.7305 | 8875.5859 | 8992.745 | 9004.876 | 9048.1678 | 9111.9605 | 8938.02 | 9076.4022 | 9134.141 | 9107.5949 | 9139.0833 | 9067.8984 | 9158.4876 | 9350.823 | 9373.7003 | 9380.0403 | 9386.586 | 9393.5454
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 13417.5084 | 13335.2933 | 13134.7145 | 13047.7755 | 13218.2179 | 13079.4266 | 13307.3148 | 13338.6707 | 13208.2671 | 13465.7366 | 13660.9662 | 13674.9383 | 13908.226 | 13862.3688 | 13933.3159 | 14148.5347 | 13969.9022 | 14234.4558 | 14497.2016 | 14407.5703 | 14427.4533 | 14446.9217 | 14466.6403
QLD | 9175.3145 | 9055.5021 | 8966.431 | 9238.3769 | 9320.1544 | 9411.0562 | 9611.5641 | 9483.1065 | 9606.3482 | 9961.7814 | 9910.9893 | 10031.1763 | 10109.0379 | 10041.1182 | 10152.7359 | 10163.9285 | 10247.7872 | 10455.0767 | 10504.6132 | 10383.9415 | 10399.2305 | 10414.3525 | 10429.757
SA | 2950.1382 | 2890.0876 | 2921.7768 | 2860.8585 | 2847.5195 | 2819.6338 | 2799.9926 | 2858.5635 | 2862.7351 | 2863.7557 | 2872.8037 | 2811.7033 | 2846.0712 | 2891.2514 | 2885.4536 | 2911.1421 | 2890.4176 | 2878.9519 | 2928.4234 | 2942.4154 | 2945.751 | 2949.0285 | 2952.3554
TAS | 1804.4914 | 1802.3661 | 1805.0911 | 1804.8923 | 1800.2399 | 1798.6801 | 1798.1625 | 1802.1967 | 1818.1323 | 1827.1651 | 1839.8925 | 1849.0364 | 1855.344 | 1866.4001 | 1876.0332 | 1886.2628 | 1897.0652 | 1903.7975 | 1912.8345 | 1919.1625 | 1920.1166 | 1921.0532 | 1922.0061
VIC | 9072.1012 | 9158.0624 | 9049.386 | 8904.8391 | 9087.8941 | 8958.3446 | 9012.1163 | 9271.9631 | 9234.9697 | 9363.8476 | 9424.4043 | 9353.8674 | 9556.3322 | 9618.1179 | 9572.0952 | 9684.5279 | 9597.2092 | 9729.8507 | 9969.5488 | 10060.9465 | 10071.0896 | 10080.9817 | 10091.042
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 12371.5361 | 12311.798 | 12094.2045 | 12034.0297 | 12145.2663 | 11930.7992 | 12023.6688 | 12010.3054 | 11948.8085 | 12138.6863 | 12209.5715 | 11802.4044 | 11684.1591 | 11074.5931 | 10842.47 | 10842.8049 | 10695.2014 | 10842.0411 | 10835.9513 | 10616.7676 | 10630.0732 | 10643.7982 | 10658.2731
QLD | 8482.6485 | 8371.8235 | 8325.2691 | 8536.6377 | 8442.3844 | 8514.5699 | 8602.4962 | 8562.1556 | 8699.7115 | 8832.8662 | 8737.0663 | 8693.3862 | 8515.6739 | 8446.9206 | 8103.8133 | 7684.9524 | 7427.2763 | 7395.5121 | 7377.1077 | 7206.9327 | 7215.8854 | 7225.225 | 7235.172
SA | 2684.7159 | 2654.2431 | 2683.7168 | 2624.0057 | 2601.8001 | 2580.8972 | 2542.8788 | 2591.8751 | 2596.0636 | 2583.4916 | 2593.7292 | 2556.4017 | 2568.9985 | 2586.5662 | 2572.0359 | 2493.8919 | 2452.0176 | 2436.2832 | 2448.4783 | 2460.0372 | 2462.3388 | 2464.7204 | 2467.2316
TAS | 1686.4715 | 1690.4353 | 1651.0955 | 1630.9666 | 1621.5377 | 1614.9303 | 1612.9825 | 1613.1116 | 1624.502 | 1631.3518 | 1633.3995 | 1639.1012 | 1639.1044 | 1642.321 | 1633.4316 | 1613.1921 | 1557.7593 | 1529.4114 | 1503.1021 | 1488.1623 | 1488.3461 | 1488.5373 | 1488.7404
VIC | 8427.3288 | 8402.2998 | 8379.9667 | 8202.3231 | 8021.372 | 7697.2842 | 7747.9932 | 7921.5573 | 7842.1488 | 7933.0648 | 8024.3864 | 7874.49 | 8016.7869 | 8096.1317 | 7955.2407 | 7962.5725 | 7690.526 | 7624.0149 | 7768.281 | 7682.9371 | 7689.6983 | 7696.6653 | 7704.0459

## Gross State Product
Gross State Product ($ millions)
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 578687.4552 | 592892.2036 | 608310.9084 | 622819.0331 | 637547.0296 | 652139.7703 | 666766.1955 | 681821.255 | 697191.6598 | 712893.017 | 728988.7056 | 745250.6109 | 761214.4645 | 776818.4629 | 792377.803 | 808120.0099 | 824161.396 | 840545.2804 | 857348.3579 | 874512.7904 | 891971.9839
Qld | 325052.9602 | 339938.8762 | 354983.5568 | 369757.1534 | 386666.6915 | 403278.3374 | 420467.059 | 438061.2011 | 456024.5762 | 474167.4924 | 492335.3781 | 510392.3746 | 527924.8144 | 544713.2315 | 561089.767 | 577309.7153 | 593286.0162 | 609057.9718 | 624754.952 | 640448.5877 | 656213.2454
SA | 101523.5265 | 103829.2564 | 106336.8235 | 108675.8162 | 111214.917 | 113656.7274 | 116118.9545 | 118640.6146 | 121203.4169 | 123814.0119 | 126485.0331 | 129139.0553 | 131678.3919 | 134083.1732 | 136421.341 | 138744.3416 | 141099.3692 | 143503.4434 | 145967.3049 | 148480.496 | 151032.0945
Tas | 26190.8271 | 26643.9809 | 27246.4212 | 27909.118 | 28565.5939 | 29164.0099 | 29736.3139 | 30304.4887 | 30876.167 | 31465.957 | 32085.2395 | 32710.7668 | 33317.6967 | 33903.9631 | 34471.9383 | 35025.0339 | 35579.0275 | 36137.5789 | 36703.202 | 37276.8201 | 37856.1033
Vic | 381065.904 | 392568.6052 | 403093.4812 | 413928.1817 | 426289.0627 | 438165.6588 | 450295.3391 | 462681.7632 | 475265.6917 | 488026.0757 | 501034.6791 | 514153.1342 | 527058.8969 | 539721.4367 | 552400.0821 | 565276.4248 | 578370.2553 | 591658.0463 | 605147.1461 | 618842.0592 | 632696.4043
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 581910.7558 | 599688.6363 | 619032.7256 | 637807.1498 | 657171.5224 | 676691.2431 | 696578.8693 | 717242.427 | 738577.5831 | 760606.0211 | 783398.8585 | 806716.3129 | 830056.0334 | 853348.977 | 876946.3324 | 901111.2885 | 925988.1437 | 951643.651 | 978176.5255 | 1005534.4663 | 1033654.5677
Qld | 327475.8955 | 345068.4776 | 363145.6277 | 381267.9561 | 401945.0307 | 422645.6786 | 444310.2942 | 466769.5708 | 490000.7537 | 513808.75 | 538028.9092 | 562510.3182 | 586788.6433 | 610605.567 | 634321.2931 | 658221.0254 | 682207.0994 | 706325.7477 | 730725.2251 | 755491.3412 | 780716.4891
SA | 101918.9938 | 104658.1438 | 107645.9703 | 110507.5261 | 113621.6468 | 116675.0603 | 119793.2028 | 123015.4629 | 126324.5209 | 129727.6463 | 133238.3801 | 136775.5076 | 140234.6235 | 143593.4511 | 146924.4597 | 150283.8582 | 153724.1877 | 157266.2468 | 160922.9094 | 164683.9694 | 168538.4889
Tas | 26346.2503 | 26963.3738 | 27742.6112 | 28596.1855 | 29457.5835 | 30272.9458 | 31074.975 | 31886.4 | 32715.4384 | 33577.7252 | 34485.8053 | 35415.2159 | 36339.14 | 37255.2406 | 38166.2603 | 39076.1935 | 40002.9198 | 40951.1911 | 41924.114 | 42923.1369 | 43946.0357
Vic | 384002.8488 | 398694.3149 | 412702.6122 | 427321.9653 | 443849.8211 | 460154.2575 | 477033.5213 | 494491.0818 | 512474.7824 | 530967.5115 | 550052.1938 | 569581.5493 | 589197.3892 | 608860.8507 | 628864.7294 | 649424.3144 | 670575.9267 | 692306.6413 | 714634.1397 | 737573.8976 | 761080.7198
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 575475.9553 | 586172.8529 | 597815.9142 | 608240.1184 | 618613.7365 | 628663.0078 | 638522.9463 | 648582.3651 | 658730.0381 | 668986.3691 | 679419.3522 | 689822.2207 | 699774.9055 | 709232.3011 | 718487.4684 | 727746.6246 | 737112.4199 | 746619.2858 | 756330.0961 | 766187.4659 | 776127.1223
Qld | 322639.2518 | 334871.4839 | 347000.2834 | 358571.4235 | 371939.4221 | 384773.2748 | 397894.3786 | 411137.9722 | 424466.5473 | 437706.2641 | 450722.0697 | 463401.5189 | 475385.0234 | 486495.2448 | 497046.9443 | 507277.1731 | 517116.1931 | 526605.3098 | 535861.7747 | 544949.6005 | 553932.7374
SA | 101131.8495 | 103014.3572 | 105062.3527 | 106900.4142 | 108897.9775 | 110773.971 | 112639.6007 | 114534.3626 | 116440.5764 | 118365.8585 | 120323.4421 | 122240.7589 | 124027.4627 | 125667.286 | 127225.3586 | 128750.2387 | 130285.7152 | 131846.9477 | 133443.0162 | 135063.4828 | 136697.5455
Tas | 26036.0909 | 26328.3347 | 26760.0148 | 27240.2879 | 27703.8253 | 28101.7729 | 28465.458 | 28816.5125 | 29162.4663 | 29517.4946 | 29892.3086 | 30265.2059 | 30613.63 | 30936.1983 | 31235.4047 | 31514.6058 | 31788.1604 | 32059.2202 | 32329.8862 | 32600.6912 | 32869.3786
Vic | 378143.8885 | 386528.869 | 393720.2804 | 400959.2895 | 409442.8785 | 417275.3982 | 425148.1381 | 433070.8616 | 440988.0311 | 448884.7128 | 456831.4181 | 464706.6823 | 472228.2276 | 479380.8153 | 486402.5678 | 493454.5272 | 500551.7921 | 507671.1159 | 514816.2157 | 521987.7742 | 529144.0308

## Rooftop PV
Rooftop PV (Energy, GWh)
Amount of energy generated by behind-the-meter rooftop PV and small-scale non-scheduled generating systems
Neutral Rooftop PV uptake as in Neutral, Strong and Weak scenarios
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 2265.6026 | 2723.201 | 3226.1802 | 3764.5121 | 4311.8677 | 4844.9235 | 5396.6524 | 5949.6153 | 6469.6643 | 6985.3653 | 7556.4198 | 8048.7992 | 8552.6768 | 8991.0121 | 9474.7906 | 9888.9578 | 10231.1285 | 10571.3823 | 10930.1485 | 11248.7389 | 11513.8592 | 11791.4469 | 12046.602
QLD | 2985.0563 | 3318.687 | 3691.4931 | 4067.6963 | 4442.9513 | 4782.6746 | 5130.6204 | 5446.3895 | 5754.4393 | 6062.6108 | 6400.9242 | 6681.9319 | 6959.1194 | 7226.9869 | 7497.909 | 7727.5739 | 7910.6979 | 8095.9195 | 8273.3234 | 8392.5133 | 8504.0923 | 8624.4778 | 8728.1085
SA | 1186.7137 | 1285.3121 | 1389.9242 | 1504.2294 | 1622.1181 | 1738.2557 | 1857.1435 | 1976.2591 | 2084.981 | 2201.4984 | 2332.7875 | 2449.8808 | 2566.4069 | 2671.9914 | 2790.2662 | 2900.0106 | 3002.1729 | 3095.5327 | 3194.6319 | 3275.4744 | 3359.7277 | 3446.9744 | 3525.4158
TAS | 153.6459 | 177.9553 | 202.0349 | 226.4113 | 248.6443 | 264.6226 | 274.4885 | 280.9557 | 283.5589 | 286.6146 | 291.7379 | 295.4487 | 297.9567 | 299.9392 | 303.2653 | 306.9375 | 310.1207 | 312.7344 | 316.9385 | 319.6187 | 321.952 | 325.7001 | 329.1757
VIC | 1668.9733 | 1969.9509 | 2286.4802 | 2603.6883 | 2913.2601 | 3211.9298 | 3504.5176 | 3798.5476 | 4056.3601 | 4311.8059 | 4581.8446 | 4802.9877 | 4996.7772 | 5181.2241 | 5365.7008 | 5535.3927 | 5689.3255 | 5824.3211 | 5959.3219 | 6064.5216 | 6164.8499 | 6280.3558 | 6380.933
Strong Rooftop PV uptake as in High DER uptake scenario
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 2265.6026 | 2483.458 | 2867.7836 | 3233.0081 | 3609.5756 | 3993.5381 | 4414.3791 | 4831.9915 | 5304.0646 | 5839.9025 | 6492.899 | 7218.7981 | 8102.3962 | 9098.2409 | 10182.4899 | 11144.668 | 12008.5108 | 12699.5404 | 13275.3057 | 13658.0467 | 14030.8823 | 14343.8088 | 14671.5924
QLD | 2975.4319 | 2975.4319 | 3222.4665 | 3460.5679 | 3719.6398 | 3992.6224 | 4303.1288 | 4621.7227 | 5020.5331 | 5522.7667 | 6188.4806 | 6971.8627 | 7922.0241 | 8926.7771 | 9888.43 | 10610.2344 | 11174.7343 | 11620.0702 | 12031.8179 | 12285.6893 | 12537.5243 | 12763.8925 | 13020.8903
SA | 861.7137 | 1341.0071 | 1468.2303 | 1582.8273 | 1705.2641 | 1836.5549 | 1988.9314 | 2138.7836 | 2294.4541 | 2429.39 | 2545.0817 | 2619.0374 | 2688.4837 | 2748.7199 | 2814.0656 | 2856.5319 | 2908.3221 | 2957.7157 | 3016.1835 | 3050.1178 | 3093.3544 | 3134.7329 | 3186.2091
TAS | 153.6459 | 181.6886 | 211.2507 | 240.168 | 271.3424 | 303.0057 | 336.7238 | 368.5184 | 403.196 | 438.7227 | 477.8089 | 514.522 | 556.8064 | 603.9711 | 660.8094 | 719.2707 | 788.5829 | 863.4629 | 944.6385 | 1013.2334 | 1077.1866 | 1129.777 | 1176.6397
VIC | 1668.9733 | 1932.9441 | 2273.1277 | 2609.1686 | 2972.1789 | 3354.9143 | 3786.0085 | 4223.4713 | 4724.6657 | 5299.4489 | 6009.5841 | 6820.6804 | 7855.8662 | 9106.5991 | 10578.2109 | 12030.7535 | 13456.2595 | 14670.1896 | 15682.8978 | 16312.4407 | 16876.6105 | 17366.8386 | 17856.7826
Rooftop PV generation relative to demand
Percentage of generation that is sourced from rooftop PV and small-scale non-scheduled generating systems relative to underlying demand
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 3.237% | 4.004% | 4.654% | 5.408% | 6.162% | 6.971% | 7.679% | 8.48% | 9.22% | 9.725% | 10.42% | 11.09% | 11.72% | 12.49% | 12.92% | 13.22% | 13.69% | 13.93% | 14.31% | 14.42% | 14.62% | 14.81% | 14.97%
QLD | 5.528% | 6.167% | 6.825% | 7.458% | 8.068% | 8.625% | 9.186% | 9.644% | 9.896% | 10.44% | 10.98% | 11.51% | 11.91% | 12.16% | 12.58% | 13.18% | 13.26% | 13.51% | 13.65% | 13.65% | 13.69% | 13.74% | 13.74%
SA | 8.895% | 10.6% | 10.18% | 10.97% | 11.85% | 13.28% | 13.51% | 14.96% | 16.02% | 17.05% | 17.51% | 19.21% | 20.24% | 20.87% | 21.57% | 22.74% | 23.83% | 24.45% | 24.88% | 25.26% | 25.64% | 26.05% | 26.31%
TAS | 1.46% | 1.679% | 1.909% | 2.141% | 2.443% | 2.602% | 2.702% | 2.761% | 2.763% | 2.769% | 2.796% | 2.809% | 2.829% | 2.851% | 2.882% | 2.92% | 2.927% | 2.93% | 2.949% | 2.961% | 2.967% | 2.985% | 2.999%
VIC | 3.689% | 4.405% | 5.1% | 5.768% | 6.397% | 6.985% | 7.517% | 8.084% | 8.558% | 9.049% | 9.524% | 10.09% | 10.39% | 10.84% | 11.15% | 11.54% | 11.87% | 11.71% | 12.04% | 12.1% | 12.16% | 12.24% | 12.28%
Strong Rooftop PV uptake as in High DER uptake scenario (relative to Neutral Underlying Demand)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 3.237% | 3.651% | 4.137% | 4.644% | 5.158% | 5.746% | 6.281% | 6.887% | 7.559% | 8.13% | 8.952% | 9.947% | 11.1% | 12.64% | 13.88% | 14.9% | 16.07% | 16.73% | 17.38% | 17.51% | 17.82% | 18.02% | 18.24%
QLD | 5.51% | 5.529% | 5.958% | 6.345% | 6.754% | 7.2% | 7.704% | 8.184% | 8.634% | 9.513% | 10.61% | 12.01% | 13.55% | 15.03% | 16.59% | 18.1% | 18.74% | 19.4% | 19.85% | 19.98% | 20.19% | 20.33% | 20.49%
SA | 6.459% | 11.06% | 10.75% | 11.55% | 12.46% | 14.03% | 14.47% | 16.19% | 17.63% | 18.81% | 19.1% | 20.54% | 21.21% | 21.47% | 21.75% | 22.4% | 23.09% | 23.36% | 23.49% | 23.53% | 23.61% | 23.69% | 23.78%
TAS | 1.46% | 1.714% | 1.996% | 2.271% | 2.666% | 2.979% | 3.315% | 3.621% | 3.929% | 4.239% | 4.579% | 4.891% | 5.288% | 5.741% | 6.281% | 6.842% | 7.444% | 8.09% | 8.789% | 9.387% | 9.928% | 10.35% | 10.72%
VIC | 3.689% | 4.322% | 5.07% | 5.78% | 6.526% | 7.296% | 8.121% | 8.988% | 9.968% | 11.12% | 12.49% | 14.32% | 16.34% | 19.05% | 21.98% | 25.08% | 28.06% | 29.49% | 31.68% | 32.55% | 33.29% | 33.85% | 34.37%

## Electric Vehicles
Electric Vehicles (Energy, MWh)
Amount of energy consumed by electric vehicles
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 6520.5248 | 18571.3459 | 40769.262 | 67268.5995 | 107687.6458 | 165208.8459 | 243947.2941 | 346347.5896 | 467412.5081 | 675519.9133 | 886301.9171 | 1118692.673 | 1382410.318 | 1671784.824 | 2037091.169 | 2440312.213 | 2873702.592 | 3330542.548 | 3819653.509 | 4424277.794 | 5052763.075
Qld | 2471.5638 | 7170.3786 | 16163.1676 | 26680.4048 | 44326.367 | 71139.8766 | 108801.7823 | 158783.4653 | 218478.9752 | 328217.9678 | 439413.8481 | 565685.8161 | 711946.6724 | 875438.8439 | 1098456.629 | 1349041.734 | 1622188.166 | 1914735.944 | 2232153.684 | 2659622.544 | 3108877.594
SA | 620.1596 | 1875.7647 | 4270.574 | 6929.782 | 11017.6177 | 16967.7162 | 25144.879 | 35949.3338 | 48786.5196 | 79942.5145 | 112477.5682 | 146989.277 | 186768.2072 | 231058.8633 | 279055.5759 | 333483.5739 | 393102.4903 | 457514.6603 | 527403.5374 | 613312.9671 | 703932.5667
Tas | 195.5772 | 561.9539 | 1248.2363 | 2036.0405 | 3299.8529 | 5152.119 | 7675.8744 | 10954.2296 | 14808.8193 | 28352.6158 | 41923.0106 | 53070.3339 | 65772.485 | 79753.4584 | 94724.8769 | 111557.9735 | 133453.4477 | 156575.2453 | 181363.5879 | 207890.3917 | 241983.0824
Vic | 4800.562 | 13687.5451 | 30115.0088 | 49824.9567 | 79980.5208 | 123041.1783 | 182179.3655 | 259372.8524 | 351016.7676 | 508729.6316 | 669404.6619 | 831373.8314 | 1012208.498 | 1207806.597 | 1414602.562 | 1697437.229 | 1995954.487 | 2305925.307 | 2633157.054 | 2978017.703 | 3335894.834
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 16132.0993 | 44079.9379 | 95422.8425 | 155957.3276 | 250164.6842 | 441254.1913 | 676587.3265 | 955384.4596 | 1258445.087 | 1575100.936 | 1896475.009 | 2461027.449 | 3162603.707 | 3907704.701 | 4697531.542 | 5549459.977 | 6460146.098 | 7684226.241 | 8959862.658 | 10209701.32 | 11496807.93
Qld | 7336.8145 | 19661.4084 | 42148.1677 | 68904.3932 | 113657.5014 | 213372.5689 | 338201.7029 | 488005.075 | 651908.6446 | 823310.8511 | 997659.7988 | 1406784.743 | 1858005.99 | 2349767.051 | 2882726.169 | 3467043.224 | 4101244.628 | 4934942.795 | 5820377.051 | 6702009.573 | 7605150.949
SA | 3048.6727 | 7416.9546 | 14315.6051 | 20977.4957 | 31486.713 | 59816.3628 | 95076.9541 | 137602.8494 | 184577.9188 | 234952.0322 | 287624.9521 | 366531.8795 | 454072.8392 | 570354.2152 | 708515.4306 | 857200.3735 | 1016109.31 | 1186779.694 | 1414429.445 | 1637694.993 | 1856120.754
Tas | 1284.3942 | 3014.2887 | 5450.9178 | 7362.3301 | 10444.7243 | 21594.2204 | 34945.857 | 49581.6333 | 64884.842 | 80482.2076 | 96112.6983 | 121173.4566 | 155599.7863 | 197592.4942 | 241890.2599 | 289457.4559 | 340196.6011 | 406781.2196 | 476215.5054 | 544294.9785 | 613288.6426
Vic | 11886.988 | 32569.4386 | 70780.7215 | 116199.1716 | 187218.0856 | 331693.886 | 510820.4557 | 724476.5323 | 958452.3176 | 1204821.398 | 1456994.853 | 1789895.296 | 2232307.274 | 2778774.852 | 3339809.953 | 3927287.697 | 4540089.583 | 5181971.235 | 6002885.37 | 6792410.363 | 7552099.396
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 2760.9122 | 6516.1113 | 14890.2581 | 23999.4073 | 36772.7387 | 56473.1649 | 84656.6579 | 123147.3023 | 170133.8679 | 224145.9255 | 283437.2722 | 361334.9621 | 452303.726 | 553698.9027 | 661763.8061 | 790474.2392 | 933784.8908 | 1115045.38 | 1313628.288 | 1525197.666 | 1754747.854
Qld | 693.4455 | 2483.805 | 6093.3286 | 10047.3742 | 15279.7566 | 24236.5416 | 37710.0835 | 56586.3779 | 80016.6591 | 107240.5784 | 137437.5362 | 177641.1938 | 225288.7556 | 279096.3692 | 336973.5761 | 407221.0177 | 486548.9375 | 595037.0018 | 715549.7238 | 846096.7861 | 989397.8777
SA | 106.9993 | 528.4888 | 1453.4943 | 2463.6825 | 3699.8939 | 5577.9566 | 8341.0221 | 12217.3093 | 17075.1483 | 22763.7992 | 29095.2543 | 39510.6141 | 52075.5998 | 66508.7014 | 82314.8372 | 101575.4611 | 117320.8514 | 134693.5889 | 154029.2934 | 174644.3048 | 195695.2868
Tas | 57.2495 | 198.8922 | 478.3754 | 781.1261 | 1172.5678 | 1807.2579 | 2729.9879 | 3996.5694 | 5545.3232 | 7318.9338 | 9268.0604 | 12176.8102 | 15677.7488 | 19688.5547 | 24065.5489 | 29432.8137 | 35565.3227 | 42198.8863 | 49627.2892 | 59526.5634 | 70513.8671
Vic | 1513.6651 | 4791.1621 | 10954.6486 | 17673.0863 | 27105.4206 | 41669.1306 | 62527.8764 | 91057.2472 | 125944.3921 | 166125.9708 | 210345.4088 | 266150.9169 | 330469.3076 | 401465.917 | 476700.0349 | 565299.5712 | 663075.7547 | 739874.4333 | 818030.4035 | 928874.5755 | 1047654.165
Number of electric vehicles
Number of electric vehicles in operation, NEM-wide
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Total vehicles | 18957799.4391 | 19215611.2223 | 19472818.8982 | 19728499.7177 | 19983806.5769 | 20238459.1181 | 20492195.23 | 20744754.5684 | 20995911.1979 | 21245504.4822 | 21493802.6046 | 21740634.1485 | 21985922.9449 | 22229638.9835 | 22471519.2549 | 22711606.2325 | 22949972.1305 | 23186728.4846 | 23422037.8879 | 23656059.1936 | 23888960.8477
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Total vehicles | 16793626.8843 | 17017104.3467 | 17243252.3014 | 17471866.9056 | 17702459.9756 | 17934804.2947 | 18168701.7411 | 18403954.9978 | 18640354.872 | 18877618.1392 | 19115300.1936 | 19353241.9075 | 19591321.8452 | 19829455.0442 | 20068006.2163 | 20306931.3784 | 20546236.3789 | 20785959.777 | 21026191.7011 | 21267050.438 | 21508645.7073
Slow
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Total vehicles | 18900132.5261 | 19123057.798 | 19340237.2908 | 19551883.4481 | 19760942.8766 | 19967120.7985 | 20170151.2111 | 20369781.7401 | 20565810.5396 | 20758820.7843 | 20949834.7136 | 21138707.6834 | 21325377.0365 | 21509817.3063 | 21691764.5486 | 21871259.6569 | 22048373.0715 | 22223184.0667 | 22395828.9892 | 22566445.1996 | 22735137.8574
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Electric vehicles | 17261.581 | 37742.809 | 61915.6922 | 99566.9193 | 153880.7231 | 227569.2553 | 324094.8737 | 438706.7012 | 645717.9075 | 856484.0413 | 1082375.9291 | 1339150.4032 | 1621109.3188 | 1927179.0588 | 2263693.5709 | 2628935.7724 | 3016297.6813 | 3433820.1679 | 3936577.8517 | 4465144.8222 | 4998557.5066
% of fleet | 0.09105% | 0.1964% | 0.318% | 0.5047% | 0.77% | 1.124% | 1.582% | 2.115% | 3.075% | 4.031% | 5.036% | 6.16% | 7.373% | 8.669% | 10.07% | 11.58% | 13.14% | 14.81% | 16.81% | 18.88% | 20.92%
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Electric vehicles | 44009.2837 | 93012.5594 | 149742.9198 | 239697.4781 | 430665.952 | 663622.2682 | 940661.5515 | 1243072.2043 | 1561211.7794 | 1886624.1729 | 2449229.5798 | 3134521.3466 | 3909071.4422 | 4645988.8521 | 5377167.5108 | 6164717.8316 | 7164493.3203 | 8288255.8289 | 9363369.9748 | 10450517.2477 | 11443499.8347
% of fleet | 0.2621% | 0.5466% | 0.8684% | 1.372% | 2.433% | 3.7% | 5.177% | 6.754% | 8.375% | 9.994% | 12.81% | 16.2% | 19.95% | 23.43% | 26.79% | 30.36% | 34.87% | 39.87% | 44.53% | 49.14% | 53.2%
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Electric vehicles | 5985.899 | 13810.1405 | 22280.8747 | 33967.6738 | 52339.9122 | 78548.3315 | 114636.3446 | 158944.6099 | 210195.9068 | 266797.8623 | 341479.9739 | 428887.3879 | 526485.5794 | 619108.2411 | 722785.4945 | 837666.2661 | 970370.4127 | 1115224.7539 | 1278420.3764 | 1456155.361 | 1636805.3302
% of fleet | 0.03167% | 0.07222% | 0.1152% | 0.1737% | 0.2649% | 0.3934% | 0.5683% | 0.7803% | 1.022% | 1.285% | 1.63% | 2.029% | 2.469% | 2.878% | 3.332% | 3.83% | 4.401% | 5.018% | 5.708% | 6.453% | 7.199%
Electric vehicle consumption share of operational demand
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0.009629% | 0.02844% | 0.06169% | 0.1022% | 0.164% | 0.2555% | 0.376% | 0.5394% | 0.7338% | 1.042% | 1.364% | 1.734% | 2.145% | 2.653% | 3.19% | 3.759% | 4.456% | 5.099% | 5.836% | 6.629% | 7.515%
Qld | 0.004845% | 0.0142% | 0.03207% | 0.05286% | 0.08755% | 0.1404% | 0.2145% | 0.3112% | 0.417% | 0.6313% | 0.8464% | 1.101% | 1.383% | 1.678% | 2.108% | 2.651% | 3.136% | 3.696% | 4.264% | 5.01% | 5.801%
SA | 0.005102% | 0.0173% | 0.03481% | 0.05679% | 0.09131% | 0.1494% | 0.2115% | 0.32% | 0.4462% | 0.7462% | 1.024% | 1.427% | 1.847% | 2.28% | 2.75% | 3.385% | 4.097% | 4.782% | 5.467% | 6.329% | 7.224%
Tas | 0.001885% | 0.005391% | 0.01203% | 0.01968% | 0.03323% | 0.05201% | 0.07766% | 0.1107% | 0.1484% | 0.2818% | 0.4134% | 0.5191% | 0.6428% | 0.7803% | 0.927% | 1.093% | 1.298% | 1.511% | 1.739% | 1.985% | 2.298%
Vic | 0.01102% | 0.03202% | 0.07078% | 0.1171% | 0.1876% | 0.2877% | 0.4225% | 0.6005% | 0.8098% | 1.174% | 1.538% | 1.942% | 2.35% | 2.834% | 3.308% | 4% | 4.723% | 5.25% | 6.047% | 6.76% | 7.49%
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0.02344% | 0.06643% | 0.1415% | 0.2302% | 0.3733% | 0.6595% | 1.01% | 1.452% | 1.88% | 2.301% | 2.717% | 3.523% | 4.507% | 5.539% | 6.577% | 7.537% | 8.69% | 10.03% | 11.52% | 13.07% | 14.63%
Qld | 0.01408% | 0.03799% | 0.08121% | 0.132% | 0.2136% | 0.3989% | 0.6268% | 0.905% | 1.201% | 1.476% | 1.776% | 2.5% | 3.285% | 4.083% | 4.945% | 5.983% | 7.024% | 8.252% | 9.558% | 11.25% | 13.02%
SA | 0.0245% | 0.06734% | 0.1132% | 0.1654% | 0.2606% | 0.5083% | 0.7952% | 1.204% | 1.627% | 2.103% | 2.577% | 3.368% | 4.133% | 5.125% | 6.282% | 7.565% | 8.938% | 10.22% | 11.98% | 13.46% | 15.35%
Tas | 0.0121% | 0.02826% | 0.05111% | 0.06881% | 0.09783% | 0.2023% | 0.3271% | 0.4625% | 0.6% | 0.7377% | 0.8729% | 1.09% | 1.389% | 1.746% | 2.118% | 2.508% | 2.912% | 3.443% | 3.993% | 4.522% | 5.055%
Vic | 0.02684% | 0.07455% | 0.1628% | 0.2661% | 0.4308% | 0.7682% | 1.155% | 1.642% | 2.154% | 2.693% | 3.301% | 3.985% | 4.933% | 6.143% | 7.208% | 8.456% | 9.779% | 10.68% | 12.19% | 14.06% | 15.36%
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0.004362% | 0.01046% | 0.02411% | 0.03908% | 0.0601% | 0.09294% | 0.1402% | 0.2046% | 0.2829% | 0.3742% | 0.473% | 0.6369% | 0.8429% | 1.095% | 1.343% | 1.649% | 1.97% | 2.358% | 2.798% | 3.303% | 3.817%
Qld | 0.001448% | 0.005278% | 0.01316% | 0.02194% | 0.0336% | 0.05312% | 0.08342% | 0.1268% | 0.179% | 0.2426% | 0.3153% | 0.4117% | 0.5262% | 0.6543% | 0.8441% | 1.097% | 1.379% | 1.794% | 2.178% | 2.646% | 3.152%
SA | 0.0009384% | 0.004732% | 0.01257% | 0.02153% | 0.03262% | 0.04963% | 0.07477% | 0.111% | 0.1576% | 0.2158% | 0.2717% | 0.3802% | 0.5152% | 0.6437% | 0.8114% | 1.072% | 1.256% | 1.616% | 1.962% | 2.261% | 2.546%
Tas | 0.0005802% | 0.002008% | 0.004977% | 0.008217% | 0.01245% | 0.01924% | 0.02914% | 0.04265% | 0.05879% | 0.0771% | 0.09715% | 0.1272% | 0.1635% | 0.2052% | 0.2521% | 0.3125% | 0.3935% | 0.4768% | 0.6368% | 0.789% | 0.8948%
Vic | 0.003706% | 0.01191% | 0.02748% | 0.04443% | 0.07151% | 0.1164% | 0.1745% | 0.2529% | 0.3494% | 0.4608% | 0.5847% | 0.741% | 0.9239% | 1.117% | 1.344% | 1.624% | 1.946% | 2.25% | 2.511% | 2.925% | 3.305%

## DSP
Demand-side Participation (MW)
Electricity demand that will be removed from the market when modelled prices reach specified limits
Neutral
Queensland
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 32.46 | 32.46 | 34.0523 | 35.0223 | 37.4238 | 38.8108 | 40.3889 | 42.3314 | 43.1421 | 45.3484 | 48.2758 | 50.3232 | 51.5702 | 53.0035 | 53.8757 | 55.23 | 57.875 | 59.6883 | 61.6696 | 63.3588 | 63.0905 | 64.9843 | 66.8961
$500 - $1,000 | 0.36 | 0.36 | 0.37766 | 0.38842 | 0.41505 | 0.43043 | 0.44794 | 0.46948 | 0.47847 | 0.50294 | 0.53541 | 0.55811 | 0.57194 | 0.58784 | 0.59751 | 0.61253 | 0.64187 | 0.66198 | 0.68395 | 0.70269 | 0.69971 | 0.72071 | 0.74192
$1,000 - $7,500 | 1.09 | 1.09 | 1.1435 | 1.176 | 1.2567 | 1.3033 | 1.3563 | 1.4215 | 1.4487 | 1.5228 | 1.6211 | 1.6898 | 1.7317 | 1.7798 | 1.8091 | 1.8546 | 1.9434 | 2.0043 | 2.0709 | 2.1276 | 2.1186 | 2.1822 | 2.2464
$7,500 - MPC | 6.39 | 6.39 | 6.7034 | 6.8944 | 7.3672 | 7.6402 | 7.9509 | 8.3333 | 8.4929 | 8.9272 | 9.5035 | 9.9065 | 10.152 | 10.4342 | 10.6059 | 10.8724 | 11.3931 | 11.7501 | 12.1401 | 12.4727 | 12.4198 | 12.7927 | 13.169
MPC | 176.07 | 176.07 | 184.7068 | 189.9683 | 202.9947 | 210.5183 | 219.0782 | 229.6145 | 234.0121 | 245.9797 | 261.858 | 272.9639 | 279.728 | 287.5026 | 292.2335 | 299.5793 | 313.9262 | 323.7621 | 334.5094 | 343.6718 | 342.2164 | 352.4887 | 362.8588
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 32.46 | 32.46 | 34.1414 | 35.6642 | 37.5711 | 39.4311 | 41.0965 | 42.5687 | 44.3402 | 47.1498 | 49.1788 | 50.8992 | 52.2082 | 54.2172 | 56.2999 | 58.3806 | 60.1988 | 61.6958 | 63.0391 | 65.8321 | 67.0766 | 69.0425 | 71.0277
$500 - $1,000 | 0.36 | 0.36 | 0.37865 | 0.39554 | 0.41669 | 0.43731 | 0.45578 | 0.47211 | 0.49176 | 0.52292 | 0.54542 | 0.5645 | 0.57902 | 0.6013 | 0.6244 | 0.64747 | 0.66764 | 0.68424 | 0.69914 | 0.73012 | 0.74392 | 0.76572 | 0.78774
$1,000 - $7,500 | 1.09 | 1.09 | 1.1465 | 1.1976 | 1.2616 | 1.3241 | 1.38 | 1.4294 | 1.4889 | 1.5833 | 1.6514 | 1.7092 | 1.7531 | 1.8206 | 1.8905 | 1.9604 | 2.0215 | 2.0717 | 2.1168 | 2.2106 | 2.2524 | 2.3184 | 2.3851
$7,500 - MPC | 6.39 | 6.39 | 6.721 | 7.0208 | 7.3962 | 7.7623 | 8.0902 | 8.38 | 8.7287 | 9.2818 | 9.6812 | 10.0199 | 10.2776 | 10.6731 | 11.0831 | 11.4927 | 11.8506 | 12.1453 | 12.4097 | 12.9596 | 13.2045 | 13.5915 | 13.9823
MPC | 156.07 | 156.07 | 164.1542 | 171.4761 | 180.6447 | 189.5878 | 197.5948 | 204.6733 | 213.1909 | 226.6995 | 236.455 | 244.727 | 251.0206 | 260.6801 | 270.6941 | 280.6981 | 289.4399 | 296.638 | 303.0966 | 316.5254 | 322.5089 | 331.9612 | 341.5062
New South Wales
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 77.73 | 77.73 | 92.8563 | 108.0428 | 124.3374 | 139.6579 | 155.3028 | 170.6709 | 189.0836 | 208.1586 | 227.304 | 242.2635 | 257.6907 | 278.0438 | 292.7794 | 309.5983 | 328.5481 | 345.6494 | 363.7884 | 389.4479 | 404.0981 | 423.5158 | 443.1456
$500 - $1,000 | 0.27 | 0.27 | 0.32254 | 0.37529 | 0.43189 | 0.48511 | 0.53945 | 0.59284 | 0.65679 | 0.72305 | 0.78955 | 0.84152 | 0.8951 | 0.9658 | 1.017 | 1.0754 | 1.1412 | 1.2006 | 1.2636 | 1.3528 | 1.4037 | 1.4711 | 1.5393
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 27.01 | 32.2662 | 37.5432 | 43.2054 | 48.529 | 53.9654 | 59.3056 | 65.7037 | 72.332 | 78.9847 | 84.1829 | 89.5436 | 96.616 | 101.7364 | 107.5807 | 114.1655 | 120.1079 | 126.411 | 135.3273 | 140.418 | 147.1653 | 153.9864
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 77.73 | 77.73 | 91.1095 | 106.5544 | 121.6801 | 137.0607 | 153.3086 | 167.8506 | 185.994 | 204.6604 | 222.6753 | 240.9582 | 255.9211 | 273.4598 | 293.9347 | 312.0123 | 332.788 | 355.1466 | 371.3282 | 397.058 | 414.3212 | 435.5603 | 457.1417
$500 - $1,000 | 0.27 | 0.27 | 0.31647 | 0.37012 | 0.42266 | 0.47609 | 0.53253 | 0.58304 | 0.64606 | 0.7109 | 0.77348 | 0.83698 | 0.88896 | 0.94988 | 1.021 | 1.0838 | 1.156 | 1.2336 | 1.2898 | 1.3792 | 1.4392 | 1.5129 | 1.5879
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 27.01 | 31.6592 | 37.0261 | 42.282 | 47.6265 | 53.2724 | 58.3256 | 64.6301 | 71.1164 | 77.3763 | 83.7293 | 88.9287 | 95.0231 | 102.1379 | 108.4195 | 115.6388 | 123.4081 | 129.031 | 137.9716 | 143.9703 | 151.3506 | 158.8498
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 28.3775 | 28.3775 | 33.5 | 38.1748 | 43.9435 | 47.927 | 51.5418 | 57.3114 | 62.2751 | 67.5559 | 73.2614 | 78.4449 | 84.3275 | 89.0691 | 95.2638 | 101.2641 | 105.7532 | 109.7958 | 117.4408 | 124.6182 | 128.8018 | 134.6841 | 140.6145
$500 - $1,000 | 3.04 | 3.04 | 3.5888 | 4.0896 | 4.7075 | 5.1343 | 5.5215 | 6.1396 | 6.6714 | 7.2371 | 7.8483 | 8.4036 | 9.0338 | 9.5417 | 10.2053 | 10.8481 | 11.329 | 11.7621 | 12.5811 | 13.35 | 13.7982 | 14.4283 | 15.0636
$1,000 - $7,500 | 1.6 | 1.6 | 1.8888 | 2.1524 | 2.4777 | 2.7023 | 2.9061 | 3.2314 | 3.5112 | 3.809 | 4.1307 | 4.4229 | 4.7546 | 5.022 | 5.3712 | 5.7095 | 5.9627 | 6.1906 | 6.6216 | 7.0263 | 7.2622 | 7.5939 | 7.9282
$7,500 - MPC | 0.66 | 0.66 | 0.77914 | 0.88787 | 1.022 | 1.1147 | 1.1988 | 1.3329 | 1.4484 | 1.5712 | 1.7039 | 1.8245 | 1.9613 | 2.0716 | 2.2156 | 2.3552 | 2.4596 | 2.5536 | 2.7314 | 2.8984 | 2.9957 | 3.1325 | 3.2704
MPC | 43.5 | 43.5 | 51.3524 | 58.5184 | 67.3612 | 73.4676 | 79.0087 | 87.8531 | 95.4619 | 103.5568 | 112.3029 | 120.2486 | 129.2661 | 136.5345 | 146.0304 | 155.2283 | 162.1097 | 168.3067 | 180.0256 | 191.028 | 197.4411 | 206.4581 | 215.5488
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 28.3775 | 28.3775 | 37.231 | 46.2061 | 55.1565 | 63.3412 | 71.9342 | 80.2684 | 88.2698 | 99.0359 | 108.6035 | 119.0805 | 128.508 | 137.1636 | 149.2975 | 159.8409 | 169.5051 | 180.5924 | 191.5764 | 203.6471 | 216.1936 | 228.4049 | 240.8319
$500 - $1,000 | 3.04 | 3.04 | 3.9885 | 4.9499 | 5.9088 | 6.7856 | 7.7061 | 8.5989 | 9.4561 | 10.6094 | 11.6344 | 12.7568 | 13.7667 | 14.694 | 15.9938 | 17.1233 | 18.1586 | 19.3464 | 20.523 | 21.8161 | 23.1602 | 24.4684 | 25.7997
$1,000 - $7,500 | 1.6 | 1.6 | 2.0992 | 2.6052 | 3.1099 | 3.5714 | 4.0558 | 4.5258 | 4.9769 | 5.5839 | 6.1234 | 6.7141 | 7.2456 | 7.7337 | 8.4178 | 9.0123 | 9.5572 | 10.1823 | 10.8016 | 11.4822 | 12.1896 | 12.8781 | 13.5788
$7,500 - MPC | 0.66 | 0.66 | 0.86591 | 1.0747 | 1.2828 | 1.4732 | 1.673 | 1.8669 | 2.053 | 2.3034 | 2.5259 | 2.7696 | 2.9888 | 3.1901 | 3.4723 | 3.7176 | 3.9423 | 4.2002 | 4.4557 | 4.7364 | 5.0282 | 5.3122 | 5.6012
MPC | 6.5 | 6.5 | 8.5279 | 10.5837 | 12.6339 | 14.5086 | 16.4769 | 18.3859 | 20.2186 | 22.6846 | 24.8762 | 27.276 | 29.4354 | 31.418 | 34.1973 | 36.6123 | 38.826 | 41.3656 | 43.8815 | 46.6464 | 49.5202 | 52.3173 | 55.1637
South Australia
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 1.2201 | 1.2201 | 2.1927 | 3.1942 | 4.1003 | 5.0211 | 6.0119 | 6.8831 | 7.9672 | 8.9668 | 9.8215 | 10.7647 | 11.6576 | 12.7598 | 13.8323 | 14.7823 | 15.6548 | 16.5292 | 17.477 | 18.6323 | 19.7909 | 20.8426 | 21.9016
$500 - $1,000 | 0.86 | 0.86 | 1.5455 | 2.2515 | 2.8902 | 3.5392 | 4.2376 | 4.8516 | 5.6158 | 6.3204 | 6.9228 | 7.5876 | 8.217 | 8.9939 | 9.7499 | 10.4195 | 11.0345 | 11.6508 | 12.3189 | 13.1332 | 13.9498 | 14.6912 | 15.4376
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.35 | 7.8176 | 11.3882 | 14.6189 | 17.9017 | 21.4343 | 24.5402 | 28.4056 | 31.9693 | 35.0164 | 38.3791 | 41.5628 | 45.4923 | 49.3163 | 52.7033 | 55.8141 | 58.9315 | 62.3105 | 66.4296 | 70.5602 | 74.3101 | 78.0855
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 1.2201 | 1.2201 | 2.038 | 2.93 | 3.762 | 4.6431 | 5.5506 | 6.4077 | 7.312 | 8.2695 | 9.2163 | 10.1806 | 11.0565 | 11.9581 | 13.0218 | 14.0519 | 15.0213 | 16.0601 | 17.1054 | 18.0892 | 19.1628 | 20.2283 | 21.3057
$500 - $1,000 | 0.86 | 0.86 | 1.4365 | 2.0653 | 2.6517 | 3.2728 | 3.9124 | 4.5165 | 5.1539 | 5.8289 | 6.4962 | 7.1759 | 7.7933 | 8.4288 | 9.1786 | 9.9047 | 10.5879 | 11.3202 | 12.0569 | 12.7504 | 13.5072 | 14.2582 | 15.0176
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.35 | 7.2661 | 10.4464 | 13.4125 | 16.5541 | 19.7896 | 22.8452 | 26.0693 | 29.4832 | 32.8587 | 36.2967 | 39.4198 | 42.6342 | 46.4266 | 50.0991 | 53.5552 | 57.2589 | 60.9856 | 64.4932 | 68.3212 | 72.1197 | 75.9611
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 5.55 | 5.55 | 5.726 | 5.8484 | 6.0165 | 5.9282 | 6.0508 | 6.2067 | 6.3571 | 6.5266 | 6.6833 | 6.8983 | 7.0787 | 7.2692 | 7.3901 | 7.4919 | 7.6263 | 7.82 | 8.0395 | 8.1791 | 8.3766 | 8.5688 | 8.7628
$500 - $1,000 | 13.2 | 13.2 | 13.6185 | 13.9097 | 14.3095 | 14.0995 | 14.3912 | 14.7618 | 15.1196 | 15.5228 | 15.8953 | 16.4067 | 16.8358 | 17.2888 | 17.5765 | 17.8185 | 18.1383 | 18.599 | 19.121 | 19.4531 | 19.9228 | 20.3799 | 20.8413
$1,000 - $7,500 | 0.5 | 0.5 | 0.51585 | 0.52688 | 0.54203 | 0.53407 | 0.54512 | 0.55916 | 0.57271 | 0.58799 | 0.6021 | 0.62147 | 0.63772 | 0.65488 | 0.66578 | 0.67494 | 0.68706 | 0.70451 | 0.72428 | 0.73686 | 0.75465 | 0.77196 | 0.78944
$7,500 - MPC | 2.29 | 2.29 | 2.3626 | 2.4131 | 2.4825 | 2.446 | 2.4966 | 2.561 | 2.623 | 2.693 | 2.7576 | 2.8463 | 2.9208 | 2.9994 | 3.0493 | 3.0912 | 3.1467 | 3.2267 | 3.3172 | 3.3748 | 3.4563 | 3.5356 | 3.6157
MPC | 1.667 | 1.667 | 1.7198 | 1.7566 | 1.8071 | 1.7805 | 1.8174 | 1.8642 | 1.9094 | 1.9603 | 2.0073 | 2.0719 | 2.1261 | 2.1833 | 2.2196 | 2.2502 | 2.2906 | 2.3488 | 2.4147 | 2.4566 | 2.5159 | 2.5737 | 2.6319
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 5.55 | 5.55 | 5.8179 | 6.0326 | 6.2787 | 6.3105 | 6.5137 | 6.7633 | 6.9532 | 7.2233 | 7.5291 | 7.7943 | 8.086 | 8.3041 | 8.5499 | 8.7832 | 8.9899 | 9.2229 | 9.5133 | 9.7964 | 10.0695 | 10.3458 | 10.6246
$500 - $1,000 | 13.2 | 13.2 | 13.8372 | 14.3478 | 14.933 | 15.0088 | 15.492 | 16.0856 | 16.5373 | 17.1798 | 17.907 | 18.5378 | 19.2315 | 19.7504 | 20.3348 | 20.8897 | 21.3814 | 21.9355 | 22.6263 | 23.2995 | 23.9492 | 24.6062 | 25.2692
$1,000 - $7,500 | 0.5 | 0.5 | 0.52413 | 0.54348 | 0.56565 | 0.56851 | 0.58682 | 0.6093 | 0.62641 | 0.65075 | 0.67829 | 0.70219 | 0.72847 | 0.74812 | 0.77026 | 0.79128 | 0.8099 | 0.83089 | 0.85705 | 0.88256 | 0.90717 | 0.93205 | 0.95717
$7,500 - MPC | 2.29 | 2.29 | 2.4005 | 2.4891 | 2.5907 | 2.6038 | 2.6876 | 2.7906 | 2.869 | 2.9804 | 3.1066 | 3.216 | 3.3364 | 3.4264 | 3.5278 | 3.6241 | 3.7094 | 3.8055 | 3.9253 | 4.0421 | 4.1548 | 4.2688 | 4.3838
MPC | 1.667 | 1.667 | 1.7474 | 1.8119 | 1.8858 | 1.8954 | 1.9564 | 2.0314 | 2.0884 | 2.1695 | 2.2614 | 2.341 | 2.4286 | 2.4942 | 2.568 | 2.638 | 2.7001 | 2.7701 | 2.8573 | 2.9424 | 3.0244 | 3.1074 | 3.1911
Strong
Queensland
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 32.46 | 32.46 | 35.2097 | 37.1698 | 40.7993 | 43.4656 | 46.9013 | 49.7357 | 52.0509 | 55.5269 | 60.1367 | 63.3705 | 65.9977 | 69.376 | 71.4842 | 74.2128 | 79.2005 | 82.8291 | 86.2015 | 90.0765 | 90.8142 | 94.3351 | 97.8911
$500 - $1,000 | 0.36 | 0.36 | 0.3905 | 0.41223 | 0.45249 | 0.48206 | 0.52016 | 0.5516 | 0.57727 | 0.61582 | 0.66695 | 0.70281 | 0.73195 | 0.76942 | 0.7928 | 0.82306 | 0.87838 | 0.91862 | 0.95602 | 0.999 | 1.0072 | 1.0462 | 1.0857
$1,000 - $7,500 | 1.09 | 1.09 | 1.1823 | 1.2482 | 1.37 | 1.4596 | 1.5749 | 1.6701 | 1.7479 | 1.8646 | 2.0194 | 2.128 | 2.2162 | 2.3296 | 2.4004 | 2.4921 | 2.6595 | 2.7814 | 2.8946 | 3.0248 | 3.0495 | 3.1678 | 3.2872
$7,500 - MPC | 6.39 | 6.39 | 6.9313 | 7.3172 | 8.0316 | 8.5565 | 9.2329 | 9.7909 | 10.2466 | 10.9309 | 11.8384 | 12.475 | 12.9921 | 13.6572 | 14.0722 | 14.6094 | 15.5912 | 16.3056 | 16.9694 | 17.7323 | 17.8775 | 18.5706 | 19.2706
MPC | 176.07 | 176.07 | 190.985 | 201.617 | 221.3039 | 235.7667 | 254.4029 | 269.7773 | 282.3354 | 301.1896 | 326.1944 | 343.7351 | 357.9855 | 376.3101 | 387.7459 | 402.5462 | 429.6007 | 449.283 | 467.5756 | 488.5944 | 492.5957 | 511.6937 | 530.9821
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 32.46 | 32.46 | 35.0274 | 38.0183 | 41.1759 | 44.1916 | 47.0181 | 49.6679 | 52.621 | 56.9188 | 60.0547 | 62.9765 | 65.5708 | 68.4285 | 71.8373 | 75.2761 | 78.2355 | 81.1959 | 83.8149 | 87.3673 | 90.8072 | 94.3267 | 97.8842
$500 - $1,000 | 0.36 | 0.36 | 0.38847 | 0.42164 | 0.45666 | 0.49011 | 0.52146 | 0.55085 | 0.5836 | 0.63126 | 0.66604 | 0.69844 | 0.72722 | 0.75891 | 0.79672 | 0.83486 | 0.86768 | 0.90051 | 0.92956 | 0.96895 | 1.0071 | 1.0461 | 1.0856
$1,000 - $7,500 | 1.09 | 1.09 | 1.1762 | 1.2766 | 1.3827 | 1.4839 | 1.5789 | 1.6678 | 1.767 | 1.9113 | 2.0166 | 2.1147 | 2.2019 | 2.2978 | 2.4123 | 2.5278 | 2.6271 | 2.7265 | 2.8145 | 2.9338 | 3.0493 | 3.1675 | 3.2869
$7,500 - MPC | 6.39 | 6.39 | 6.8954 | 7.4842 | 8.1058 | 8.6995 | 9.2559 | 9.7775 | 10.3589 | 11.2049 | 11.8222 | 12.3974 | 12.9081 | 13.4707 | 14.1417 | 14.8187 | 15.4013 | 15.984 | 16.4996 | 17.1989 | 17.8761 | 18.5689 | 19.2693
MPC | 156.07 | 156.07 | 168.4143 | 182.7945 | 197.9768 | 212.4763 | 226.0664 | 238.807 | 253.0057 | 273.6697 | 288.7471 | 302.7953 | 315.269 | 329.0093 | 345.3991 | 361.9329 | 376.1618 | 390.3955 | 402.9881 | 420.0684 | 436.6076 | 453.5294 | 470.6343
New South Wales
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 77.73 | 77.73 | 103.0066 | 126.8519 | 151.8192 | 176.5757 | 199.9942 | 225.9737 | 253.9989 | 278.5219 | 309.1274 | 333.1624 | 358.1545 | 387.5127 | 412.5448 | 439.2906 | 469.7517 | 492.0782 | 523.2652 | 559.3418 | 590.8385 | 622.0772 | 653.7028
$500 - $1,000 | 0.27 | 0.27 | 0.3578 | 0.44063 | 0.52735 | 0.61335 | 0.69469 | 0.78493 | 0.88228 | 0.96746 | 1.0738 | 1.1573 | 1.2441 | 1.346 | 1.433 | 1.5259 | 1.6317 | 1.7093 | 1.8176 | 1.9429 | 2.0523 | 2.1608 | 2.2707
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 27.01 | 35.7932 | 44.0791 | 52.7549 | 61.3574 | 69.495 | 78.5225 | 88.2608 | 96.7821 | 107.4171 | 115.7689 | 124.4533 | 134.6548 | 143.3531 | 152.6468 | 163.2316 | 170.9897 | 181.8267 | 194.3628 | 205.3074 | 216.1624 | 227.1519
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 77.73 | 77.73 | 99.7444 | 123.2241 | 146.852 | 170.0697 | 194.4421 | 215.5349 | 240.6048 | 266.5367 | 290.9246 | 316.3731 | 336.7103 | 361.6822 | 384.5123 | 410.448 | 435.4217 | 461.4406 | 483.1775 | 511.1711 | 535.8229 | 561.2308 | 586.7618
$500 - $1,000 | 0.27 | 0.27 | 0.34647 | 0.42803 | 0.5101 | 0.59075 | 0.67541 | 0.74867 | 0.83576 | 0.92583 | 1.0105 | 1.0989 | 1.1696 | 1.2563 | 1.3356 | 1.4257 | 1.5125 | 1.6028 | 1.6783 | 1.7756 | 1.8612 | 1.9495 | 2.0382
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 27.01 | 34.6597 | 42.8185 | 51.0289 | 59.0967 | 67.5657 | 74.8951 | 83.6065 | 92.6175 | 101.0919 | 109.9349 | 117.0017 | 125.6791 | 133.6122 | 142.6245 | 151.3024 | 160.3436 | 167.8969 | 177.6242 | 186.1904 | 195.0192 | 203.8908
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 28.3775 | 28.3775 | 36.477 | 44.655 | 52.9262 | 61.1607 | 68.83 | 79.1677 | 88.382 | 97.5547 | 107.5022 | 115.6123 | 123.798 | 133.9254 | 142.2641 | 151.6663 | 159.6314 | 166.2229 | 182.4354 | 192.7905 | 202.7611 | 214.0022 | 225.4268
$500 - $1,000 | 3.04 | 3.04 | 3.9077 | 4.7838 | 5.6698 | 6.552 | 7.3736 | 8.481 | 9.4681 | 10.4508 | 11.5164 | 12.3852 | 13.2621 | 14.3471 | 15.2404 | 16.2476 | 17.1009 | 17.807 | 19.5438 | 20.6531 | 21.7212 | 22.9255 | 24.1493
$1,000 - $7,500 | 1.6 | 1.6 | 2.0567 | 2.5178 | 2.9841 | 3.4484 | 3.8808 | 4.4637 | 4.9832 | 5.5004 | 6.0613 | 6.5185 | 6.9801 | 7.5511 | 8.0212 | 8.5514 | 9.0005 | 9.3721 | 10.2862 | 10.8701 | 11.4322 | 12.066 | 12.7102
$7,500 - MPC | 0.66 | 0.66 | 0.84838 | 1.0386 | 1.231 | 1.4225 | 1.6008 | 1.8413 | 2.0556 | 2.2689 | 2.5003 | 2.6889 | 2.8793 | 3.1148 | 3.3088 | 3.5274 | 3.7127 | 3.866 | 4.2431 | 4.4839 | 4.7158 | 4.9772 | 5.243
MPC | 43.5 | 43.5 | 55.9159 | 68.4519 | 81.1309 | 93.7536 | 105.5099 | 121.3566 | 135.4813 | 149.5422 | 164.7907 | 177.2227 | 189.7706 | 205.2951 | 218.0775 | 232.4901 | 244.6999 | 254.804 | 279.6564 | 295.5296 | 310.8137 | 328.0453 | 345.5581
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 28.3775 | 28.3775 | 42.0027 | 55.8353 | 69.5673 | 84.0319 | 98.4561 | 113.2009 | 128.7267 | 143.2602 | 158.0867 | 174.0511 | 187.0908 | 201.6314 | 217.202 | 232.053 | 247.5899 | 262.2023 | 277.5009 | 294.4607 | 311.0968 | 327.2947 | 343.6211
$500 - $1,000 | 3.04 | 3.04 | 4.4996 | 5.9815 | 7.4526 | 9.0021 | 10.5473 | 12.1269 | 13.7901 | 15.3471 | 16.9354 | 18.6456 | 20.0425 | 21.6002 | 23.2682 | 24.8592 | 26.5236 | 28.089 | 29.7279 | 31.5448 | 33.3269 | 35.0622 | 36.8112
$1,000 - $7,500 | 1.6 | 1.6 | 2.3682 | 3.1481 | 3.9224 | 4.738 | 5.5512 | 6.3826 | 7.258 | 8.0774 | 8.9134 | 9.8135 | 10.5487 | 11.3685 | 12.2464 | 13.0838 | 13.9598 | 14.7837 | 15.6463 | 16.6025 | 17.5405 | 18.4538 | 19.3743
$7,500 - MPC | 0.66 | 0.66 | 0.97689 | 1.2986 | 1.618 | 1.9544 | 2.2899 | 2.6328 | 2.9939 | 3.3319 | 3.6768 | 4.0481 | 4.3513 | 4.6895 | 5.0517 | 5.3971 | 5.7584 | 6.0983 | 6.4541 | 6.8485 | 7.2355 | 7.6122 | 7.9919
MPC | 6.5 | 6.5 | 9.6209 | 12.7893 | 15.9347 | 19.2479 | 22.5519 | 25.9292 | 29.4855 | 32.8144 | 36.2105 | 39.8673 | 42.8541 | 46.1847 | 49.7512 | 53.1529 | 56.7117 | 60.0587 | 63.5629 | 67.4477 | 71.2582 | 74.9685 | 78.7081
South Australia
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 1.2201 | 1.2201 | 2.6899 | 4.206 | 5.5475 | 6.9365 | 8.3085 | 9.7354 | 11.351 | 12.8297 | 14.144 | 15.5487 | 16.7871 | 18.3041 | 19.7434 | 21.2268 | 22.4805 | 23.7152 | 25.3123 | 27.1335 | 28.6408 | 30.2105 | 31.7922
$500 - $1,000 | 0.86 | 0.86 | 1.896 | 2.9647 | 3.9103 | 4.8893 | 5.8564 | 6.8622 | 8.0009 | 9.0432 | 9.9696 | 10.9597 | 11.8326 | 12.9019 | 13.9164 | 14.962 | 15.8457 | 16.7159 | 17.8417 | 19.1254 | 20.1878 | 21.2943 | 22.4091
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.35 | 9.5904 | 14.9956 | 19.7786 | 24.7306 | 29.6223 | 34.7097 | 40.4697 | 45.7415 | 50.4276 | 55.4358 | 59.851 | 65.2595 | 70.391 | 75.6799 | 80.1495 | 84.5515 | 90.2459 | 96.739 | 102.1127 | 107.7094 | 113.3486
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 1.2201 | 1.2201 | 2.4973 | 3.883 | 5.1948 | 6.4998 | 7.8362 | 9.101 | 10.4031 | 11.7923 | 13.163 | 14.4541 | 15.6651 | 16.8378 | 18.1251 | 19.5999 | 20.8973 | 22.2441 | 23.6157 | 24.7861 | 26.1414 | 27.4524 | 28.7632
$500 - $1,000 | 0.86 | 0.86 | 1.7603 | 2.737 | 3.6616 | 4.5815 | 5.5235 | 6.4149 | 7.3327 | 8.3119 | 9.2781 | 10.1882 | 11.0417 | 11.8683 | 12.7757 | 13.8152 | 14.7297 | 15.6791 | 16.6458 | 17.4708 | 18.4261 | 19.3501 | 20.2741
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.35 | 8.9036 | 13.844 | 18.521 | 23.1737 | 27.9385 | 32.4477 | 37.0901 | 42.0429 | 46.9298 | 51.5332 | 55.8507 | 60.0317 | 64.6213 | 69.8795 | 74.505 | 79.3069 | 84.197 | 88.3698 | 93.2019 | 97.8757 | 102.5494
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 5.55 | 5.55 | 5.8719 | 6.1368 | 6.4151 | 6.4474 | 6.7338 | 6.9858 | 7.2793 | 7.6076 | 7.9156 | 8.2754 | 8.6004 | 8.8678 | 9.1692 | 9.4339 | 9.6614 | 10.0128 | 10.3676 | 10.7166 | 10.9872 | 11.3252 | 11.6656
$500 - $1,000 | 13.2 | 13.2 | 13.9656 | 14.5957 | 15.2575 | 15.3343 | 16.0155 | 16.6148 | 17.313 | 18.0936 | 18.8264 | 19.682 | 20.455 | 21.091 | 21.8078 | 22.4374 | 22.9784 | 23.8143 | 24.6581 | 25.488 | 26.1318 | 26.9355 | 27.7453
$1,000 - $7,500 | 0.5 | 0.5 | 0.529 | 0.55287 | 0.57793 | 0.58084 | 0.60665 | 0.62935 | 0.65579 | 0.68537 | 0.71312 | 0.74553 | 0.77481 | 0.7989 | 0.82605 | 0.8499 | 0.8704 | 0.90206 | 0.93402 | 0.96546 | 0.98984 | 1.0203 | 1.051
$7,500 - MPC | 2.29 | 2.29 | 2.4228 | 2.5321 | 2.6469 | 2.6603 | 2.7784 | 2.8824 | 3.0035 | 3.139 | 3.2661 | 3.4145 | 3.5486 | 3.659 | 3.7833 | 3.8925 | 3.9864 | 4.1314 | 4.2778 | 4.4218 | 4.5335 | 4.6729 | 4.8134
MPC | 1.667 | 1.667 | 1.7636 | 1.8432 | 1.9268 | 1.9365 | 2.0225 | 2.0982 | 2.1864 | 2.2849 | 2.3775 | 2.4855 | 2.5832 | 2.6635 | 2.754 | 2.8335 | 2.9018 | 3.0074 | 3.1139 | 3.2187 | 3.3 | 3.4015 | 3.5038
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 5.55 | 5.55 | 5.9812 | 6.3293 | 6.709 | 6.8833 | 7.2426 | 7.6369 | 8.0365 | 8.4674 | 8.9292 | 9.342 | 9.7796 | 10.197 | 10.5463 | 10.9239 | 11.289 | 11.7284 | 12.1782 | 12.6026 | 13.0134 | 13.4504 | 13.8897
$500 - $1,000 | 13.2 | 13.2 | 14.2257 | 15.0534 | 15.9566 | 16.371 | 17.2256 | 18.1634 | 19.1138 | 20.1387 | 21.2369 | 22.2189 | 23.2595 | 24.2522 | 25.0831 | 25.9812 | 26.8495 | 27.8945 | 28.9643 | 29.9737 | 30.9507 | 31.9901 | 33.0351
$1,000 - $7,500 | 0.5 | 0.5 | 0.53885 | 0.5702 | 0.60442 | 0.62011 | 0.65249 | 0.68801 | 0.72401 | 0.76283 | 0.80443 | 0.84162 | 0.88104 | 0.91864 | 0.95012 | 0.98414 | 1.017 | 1.0566 | 1.0971 | 1.1354 | 1.1724 | 1.2117 | 1.2513
$7,500 - MPC | 2.29 | 2.29 | 2.4679 | 2.6115 | 2.7682 | 2.8401 | 2.9884 | 3.1511 | 3.316 | 3.4938 | 3.6843 | 3.8546 | 4.0352 | 4.2074 | 4.3515 | 4.5073 | 4.658 | 4.8393 | 5.0249 | 5.2 | 5.3695 | 5.5498 | 5.7311
MPC | 1.667 | 1.667 | 1.7965 | 1.901 | 2.0151 | 2.0674 | 2.1753 | 2.2937 | 2.4138 | 2.5432 | 2.6819 | 2.8059 | 2.9373 | 3.0627 | 3.1676 | 3.281 | 3.3907 | 3.5226 | 3.6577 | 3.7852 | 3.9086 | 4.0398 | 4.1718
Weak
Queensland
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 32.46 | 32.46 | 32.6254 | 32.2053 | 33.0832 | 33.0322 | 33.1417 | 33.5322 | 33.0302 | 33.5945 | 34.6407 | 35.0112 | 34.8193 | 34.7606 | 34.3475 | 34.2557 | 34.9482 | 35.1158 | 35.3714 | 35.451 | 34.4576 | 34.664 | 34.8703
$500 - $1,000 | 0.36 | 0.36 | 0.36183 | 0.35718 | 0.36691 | 0.36635 | 0.36756 | 0.37189 | 0.36632 | 0.37258 | 0.38419 | 0.38829 | 0.38617 | 0.38552 | 0.38093 | 0.37992 | 0.3876 | 0.38945 | 0.39229 | 0.39317 | 0.38215 | 0.38444 | 0.38673
$1,000 - $7,500 | 1.09 | 1.09 | 1.0956 | 1.0814 | 1.1109 | 1.1092 | 1.1129 | 1.126 | 1.1091 | 1.1281 | 1.1632 | 1.1757 | 1.1692 | 1.1673 | 1.1534 | 1.1503 | 1.1736 | 1.1792 | 1.1878 | 1.1904 | 1.1571 | 1.164 | 1.1709
$7,500 - MPC | 6.39 | 6.39 | 6.4226 | 6.3399 | 6.5127 | 6.5026 | 6.5242 | 6.6011 | 6.5022 | 6.6133 | 6.8193 | 6.8922 | 6.8544 | 6.8429 | 6.7616 | 6.7435 | 6.8798 | 6.9128 | 6.9631 | 6.9788 | 6.7832 | 6.8239 | 6.8645
MPC | 176.07 | 176.07 | 176.9672 | 174.6884 | 179.4501 | 179.1739 | 179.7678 | 181.8861 | 179.1627 | 182.2237 | 187.8988 | 189.9082 | 188.8674 | 188.549 | 186.308 | 185.8103 | 189.5667 | 190.4758 | 191.862 | 192.2936 | 186.9056 | 188.0247 | 189.1438
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 32.46 | 32.46 | 32.8114 | 32.9898 | 33.4978 | 33.93 | 34.1711 | 34.2412 | 34.54 | 35.6044 | 36.0336 | 36.2186 | 36.1085 | 36.4755 | 36.8712 | 37.2451 | 37.437 | 37.4246 | 37.3218 | 38.062 | 37.8934 | 38.1309 | 38.3684
$500 - $1,000 | 0.36 | 0.36 | 0.3639 | 0.36588 | 0.37151 | 0.3763 | 0.37898 | 0.37975 | 0.38307 | 0.39487 | 0.39963 | 0.40168 | 0.40046 | 0.40453 | 0.40892 | 0.41307 | 0.4152 | 0.41506 | 0.41392 | 0.42213 | 0.42026 | 0.42289 | 0.42553
$1,000 - $7,500 | 1.09 | 1.09 | 1.1018 | 1.1078 | 1.1248 | 1.1394 | 1.1475 | 1.1498 | 1.1598 | 1.1956 | 1.21 | 1.2162 | 1.2125 | 1.2248 | 1.2381 | 1.2507 | 1.2571 | 1.2567 | 1.2533 | 1.2781 | 1.2725 | 1.2804 | 1.2884
$7,500 - MPC | 6.39 | 6.39 | 6.4592 | 6.4943 | 6.5943 | 6.6794 | 6.7268 | 6.7406 | 6.7995 | 7.009 | 7.0935 | 7.1299 | 7.1082 | 7.1805 | 7.2584 | 7.332 | 7.3698 | 7.3673 | 7.3471 | 7.4928 | 7.4596 | 7.5064 | 7.5531
MPC | 156.07 | 156.07 | 157.7596 | 158.6175 | 161.0598 | 163.1376 | 164.2971 | 164.6341 | 166.0709 | 171.1885 | 173.2523 | 174.1414 | 173.6124 | 175.3766 | 177.2794 | 179.0773 | 179.9997 | 179.9403 | 179.4459 | 183.0047 | 182.1944 | 183.3362 | 184.478
New South Wales
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 77.73 | 77.73 | 77.6823 | 77.6913 | 78.3968 | 78.4007 | 78.568 | 78.5777 | 79.8719 | 81.2272 | 82.4161 | 82.0305 | 81.8411 | 83.147 | 82.7215 | 82.8984 | 83.5999 | 83.7869 | 84.1972 | 86.2372 | 85.7714 | 86.3142 | 86.8571
$500 - $1,000 | 0.27 | 0.27 | 0.26983 | 0.26987 | 0.27232 | 0.27233 | 0.27291 | 0.27294 | 0.27744 | 0.28215 | 0.28628 | 0.28494 | 0.28428 | 0.28882 | 0.28734 | 0.28795 | 0.29039 | 0.29104 | 0.29246 | 0.29955 | 0.29793 | 0.29982 | 0.3017
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 27.01 | 26.9934 | 26.9966 | 27.2417 | 27.2431 | 27.3012 | 27.3046 | 27.7543 | 28.2252 | 28.6384 | 28.5043 | 28.4386 | 28.8923 | 28.7445 | 28.8059 | 29.0497 | 29.1147 | 29.2572 | 29.9661 | 29.8043 | 29.9929 | 30.1815
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 77.73 | 77.73 | 77.2433 | 78.405 | 79.0881 | 79.7768 | 80.7923 | 80.8109 | 82.4225 | 84.0113 | 85.1329 | 86.2064 | 86.0342 | 86.6982 | 88.1715 | 88.8118 | 90.1206 | 91.7168 | 91.647 | 93.8397 | 93.9344 | 94.8879 | 95.8413
$500 - $1,000 | 0.27 | 0.27 | 0.26831 | 0.27234 | 0.27472 | 0.27711 | 0.28064 | 0.2807 | 0.2863 | 0.29182 | 0.29571 | 0.29944 | 0.29885 | 0.30115 | 0.30627 | 0.30849 | 0.31304 | 0.31858 | 0.31834 | 0.32596 | 0.32629 | 0.3296 | 0.33291
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 27.01 | 26.8409 | 27.2445 | 27.4819 | 27.7212 | 28.0741 | 28.0806 | 28.6406 | 29.1927 | 29.5824 | 29.9554 | 29.8956 | 30.1263 | 30.6383 | 30.8608 | 31.3155 | 31.8702 | 31.8459 | 32.6079 | 32.6408 | 32.9721 | 33.3034
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 28.3775 | 28.3775 | 28.2944 | 27.9064 | 28.3152 | 27.609 | 26.8461 | 27.2408 | 27.2198 | 27.3301 | 27.5852 | 27.6233 | 27.8881 | 27.7667 | 28.0869 | 28.3199 | 28.128 | 27.8409 | 28.4521 | 28.9027 | 28.6505 | 28.7811 | 28.9117
$500 - $1,000 | 3.04 | 3.04 | 3.0311 | 2.9895 | 3.0333 | 2.9577 | 2.8759 | 2.9182 | 2.916 | 2.9278 | 2.9551 | 2.9592 | 2.9876 | 2.9746 | 3.0089 | 3.0338 | 3.0133 | 2.9825 | 3.048 | 3.0963 | 3.0692 | 3.0832 | 3.0972
$1,000 - $7,500 | 1.6 | 1.6 | 1.5953 | 1.5734 | 1.5965 | 1.5567 | 1.5137 | 1.5359 | 1.5347 | 1.5409 | 1.5553 | 1.5575 | 1.5724 | 1.5656 | 1.5836 | 1.5968 | 1.5859 | 1.5697 | 1.6042 | 1.6296 | 1.6154 | 1.6228 | 1.6301
$7,500 - MPC | 0.66 | 0.66 | 0.65807 | 0.64904 | 0.65855 | 0.64213 | 0.62438 | 0.63356 | 0.63307 | 0.63564 | 0.64157 | 0.64246 | 0.64862 | 0.64579 | 0.65324 | 0.65866 | 0.6542 | 0.64752 | 0.66174 | 0.67222 | 0.66635 | 0.66939 | 0.67242
MPC | 43.5 | 43.5 | 43.3727 | 42.7779 | 43.4045 | 42.322 | 41.1525 | 41.7576 | 41.7254 | 41.8945 | 42.2855 | 42.344 | 42.7498 | 42.5637 | 43.0546 | 43.4117 | 43.1176 | 42.6775 | 43.6144 | 44.3051 | 43.9185 | 44.1187 | 44.3189
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 28.3775 | 28.3775 | 28.5491 | 28.7314 | 28.8428 | 28.5782 | 28.5394 | 28.4173 | 28.2126 | 28.8496 | 29.0621 | 29.4677 | 29.575 | 29.5023 | 30.1406 | 30.4026 | 30.4779 | 30.788 | 31.0508 | 31.4567 | 31.8964 | 32.251 | 32.6057
$500 - $1,000 | 3.04 | 3.04 | 3.0584 | 3.0779 | 3.0898 | 3.0615 | 3.0573 | 3.0443 | 3.0223 | 3.0906 | 3.1133 | 3.1568 | 3.1683 | 3.1605 | 3.2289 | 3.257 | 3.265 | 3.2982 | 3.3264 | 3.3699 | 3.417 | 3.455 | 3.493
$1,000 - $7,500 | 1.6 | 1.6 | 1.6097 | 1.62 | 1.6262 | 1.6113 | 1.6091 | 1.6022 | 1.5907 | 1.6266 | 1.6386 | 1.6615 | 1.6675 | 1.6634 | 1.6994 | 1.7142 | 1.7184 | 1.7359 | 1.7507 | 1.7736 | 1.7984 | 1.8184 | 1.8384
$7,500 - MPC | 0.66 | 0.66 | 0.66399 | 0.66823 | 0.67082 | 0.66467 | 0.66377 | 0.66093 | 0.65617 | 0.67098 | 0.67592 | 0.68536 | 0.68785 | 0.68616 | 0.70101 | 0.7071 | 0.70885 | 0.71606 | 0.72217 | 0.73162 | 0.74184 | 0.75009 | 0.75834
MPC | 6.5 | 6.5 | 6.5393 | 6.5811 | 6.6066 | 6.546 | 6.5371 | 6.5091 | 6.4622 | 6.6081 | 6.6568 | 6.7497 | 6.7743 | 6.7576 | 6.9039 | 6.9639 | 6.9811 | 7.0521 | 7.1123 | 7.2053 | 7.306 | 7.3873 | 7.4685
South Australia
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 1.2201 | 1.2201 | 1.229 | 1.2437 | 1.2231 | 1.2138 | 1.2218 | 1.2065 | 1.2278 | 1.2329 | 1.219 | 1.2175 | 1.2111 | 1.2258 | 1.2357 | 1.2341 | 1.2267 | 1.2202 | 1.2196 | 1.2328 | 1.2448 | 1.2494 | 1.2539
$500 - $1,000 | 0.86 | 0.86 | 0.86628 | 0.87665 | 0.86212 | 0.85559 | 0.86118 | 0.85045 | 0.86545 | 0.86901 | 0.85921 | 0.8582 | 0.85368 | 0.864 | 0.87101 | 0.8699 | 0.86464 | 0.86009 | 0.85964 | 0.86892 | 0.87743 | 0.88063 | 0.88383
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.35 | 4.3817 | 4.4342 | 4.3607 | 4.3277 | 4.356 | 4.3017 | 4.3776 | 4.3956 | 4.346 | 4.3409 | 4.318 | 4.3702 | 4.4057 | 4.4001 | 4.3735 | 4.3504 | 4.3482 | 4.3951 | 4.4382 | 4.4543 | 4.4705
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 1.2201 | 1.2201 | 1.2103 | 1.2375 | 1.2328 | 1.243 | 1.256 | 1.2556 | 1.2635 | 1.278 | 1.2881 | 1.2988 | 1.2973 | 1.2989 | 1.3166 | 1.3289 | 1.3343 | 1.3449 | 1.3548 | 1.3591 | 1.3694 | 1.3782 | 1.387
$500 - $1,000 | 0.86 | 0.86 | 0.85311 | 0.87226 | 0.86895 | 0.87614 | 0.88531 | 0.88505 | 0.89061 | 0.90079 | 0.90796 | 0.91546 | 0.91445 | 0.91555 | 0.92806 | 0.9367 | 0.94049 | 0.94795 | 0.95496 | 0.958 | 0.96526 | 0.97145 | 0.97765
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.35 | 4.3151 | 4.412 | 4.3953 | 4.4317 | 4.478 | 4.4767 | 4.5048 | 4.5563 | 4.5926 | 4.6305 | 4.6254 | 4.631 | 4.6942 | 4.738 | 4.7571 | 4.7949 | 4.8303 | 4.8457 | 4.8824 | 4.9137 | 4.9451
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
Price band | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
$300 - $500 | 5.55 | 5.55 | 5.5982 | 5.5931 | 5.6309 | 5.4322 | 5.431 | 5.4591 | 5.4813 | 5.5189 | 5.5443 | 5.6163 | 5.6581 | 5.7062 | 5.699 | 5.6775 | 5.6812 | 5.7281 | 5.792 | 5.7973 | 5.8427 | 5.8831 | 5.9235
$500 - $1,000 | 13.2 | 13.2 | 13.3146 | 13.3024 | 13.3924 | 12.9199 | 12.917 | 12.9837 | 13.0367 | 13.126 | 13.1864 | 13.3577 | 13.457 | 13.5715 | 13.5544 | 13.5034 | 13.512 | 13.6236 | 13.7756 | 13.7881 | 13.8962 | 13.9923 | 14.0883
$1,000 - $7,500 | 0.5 | 0.5 | 0.50434 | 0.50388 | 0.50729 | 0.48939 | 0.48928 | 0.49181 | 0.49381 | 0.4972 | 0.49949 | 0.50597 | 0.50973 | 0.51407 | 0.51343 | 0.51149 | 0.51182 | 0.51604 | 0.5218 | 0.52228 | 0.52637 | 0.53001 | 0.53365
$7,500 - MPC | 2.29 | 2.29 | 2.3099 | 2.3078 | 2.3234 | 2.2414 | 2.2409 | 2.2525 | 2.2617 | 2.2772 | 2.2876 | 2.3174 | 2.3346 | 2.3545 | 2.3515 | 2.3426 | 2.3441 | 2.3635 | 2.3899 | 2.392 | 2.4108 | 2.4274 | 2.4441
MPC | 1.667 | 1.667 | 1.6814 | 1.6799 | 1.6913 | 1.6316 | 1.6312 | 1.6396 | 1.6463 | 1.6576 | 1.6652 | 1.6869 | 1.6994 | 1.7139 | 1.7117 | 1.7053 | 1.7064 | 1.7204 | 1.7396 | 1.7412 | 1.7549 | 1.767 | 1.7791
Winter
Price band | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
$300 - $500 | 5.55 | 5.55 | 5.6148 | 5.6257 | 5.6642 | 5.513 | 5.5163 | 5.5574 | 5.5486 | 5.6025 | 5.6803 | 5.7243 | 5.7848 | 5.7911 | 5.8158 | 5.8311 | 5.8284 | 5.8424 | 5.8915 | 5.9339 | 5.9686 | 6.0036 | 6.0387
$500 - $1,000 | 13.2 | 13.2 | 13.3542 | 13.38 | 13.4715 | 13.1121 | 13.1198 | 13.2177 | 13.1967 | 13.3249 | 13.51 | 13.6145 | 13.7585 | 13.7734 | 13.8321 | 13.8685 | 13.8621 | 13.8955 | 14.0121 | 14.113 | 14.1956 | 14.2789 | 14.3623
$1,000 - $7,500 | 0.5 | 0.5 | 0.50584 | 0.50682 | 0.51029 | 0.49667 | 0.49696 | 0.50067 | 0.49988 | 0.50473 | 0.51174 | 0.5157 | 0.52116 | 0.52172 | 0.52394 | 0.52532 | 0.52508 | 0.52635 | 0.53076 | 0.53458 | 0.53771 | 0.54087 | 0.54403
$7,500 - MPC | 2.29 | 2.29 | 2.3168 | 2.3212 | 2.3371 | 2.2748 | 2.2761 | 2.2931 | 2.2894 | 2.3117 | 2.3438 | 2.3619 | 2.3869 | 2.3895 | 2.3997 | 2.406 | 2.4049 | 2.4107 | 2.4309 | 2.4484 | 2.4627 | 2.4772 | 2.4916
MPC | 1.667 | 1.667 | 1.6864 | 1.6897 | 1.7012 | 1.6559 | 1.6568 | 1.6692 | 1.6665 | 1.6827 | 1.7061 | 1.7193 | 1.7375 | 1.7394 | 1.7468 | 1.7514 | 1.7506 | 1.7548 | 1.7695 | 1.7822 | 1.7927 | 1.8032 | 1.8137

## Battery aggregation
Battery aggregation
Aggregation of household battery installations by NEM participants for arbitrage and emergency response
Neutral capacity growth (all small-scale batteries, MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 51.1715 | 132.3957 | 251.0873 | 408.3105 | 564.9804 | 720.2539 | 876.4304 | 1030.7444 | 1179.2732 | 1324.3986 | 1465.4044 | 1602.2097 | 1736.6534 | 1851.5224 | 1943.8412 | 2031.7912 | 2121.0056 | 2209.3601 | 2299.1551 | 2387.5435 | 2474.5391 | 2518.3189 | 2606.5984
Qld | 27.5232 | 71.1952 | 136.6617 | 225.2731 | 305.4816 | 380.0425 | 448.2543 | 512.3848 | 572.3935 | 630.8497 | 688.6573 | 745.9152 | 802.763 | 859.2998 | 915.5918 | 970.5279 | 1025.3244 | 1080.0373 | 1131.9736 | 1181.5158 | 1228.6442 | 1272.4562 | 1314.5075
SA | 9.303 | 24.2339 | 46.8963 | 77.2947 | 107.6628 | 137.991 | 168.2939 | 199.6773 | 231.0309 | 262.3368 | 293.6127 | 324.9129 | 356.262 | 386.5733 | 414.761 | 440.8414 | 461.5247 | 480.1193 | 498.8368 | 516.0165 | 533.2747 | 550.4545 | 567.7418
Tas | 2.2753 | 5.7848 | 11.0526 | 17.4899 | 23.3605 | 29.7184 | 33.1579 | 35.4296 | 36.4053 | 37.374 | 38.1208 | 38.6558 | 39.2733 | 39.9055 | 40.5519 | 41.2095 | 41.8764 | 42.5502 | 43.2289 | 43.9107 | 44.5933 | 45.2727 | 45.9541
Vic | 29.0616 | 78.6476 | 155.4434 | 249.0048 | 322.1125 | 388.1533 | 449.1835 | 510.1272 | 568.8432 | 626.1623 | 680.8783 | 734.4836 | 788.4321 | 842.7818 | 897.5925 | 951.5177 | 1001.653 | 1048.4621 | 1092.3559 | 1132.9627 | 1171.0446 | 1206.1579 | 1239.3811
Strong capacity growth (all small-scale batteries, MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 47.3991 | 79.1544 | 121.3374 | 167.7588 | 230.4651 | 306.2132 | 398.3386 | 504.8265 | 627.7756 | 765.0044 | 915.4665 | 1079.4152 | 1258.7397 | 1462.998 | 1697.1756 | 1965.6771 | 2276.1157 | 2636.5453 | 3036.817 | 3468.6874 | 3889.3611 | 4267.623 | 4590.4484
Qld | 47.3056 | 75.4576 | 115.214 | 163.6495 | 223.0687 | 292.902 | 375.0192 | 467.526 | 569.8549 | 684.2927 | 808.8914 | 946.4078 | 1108.1498 | 1298.7704 | 1532.7767 | 1815.0791 | 2145.6653 | 2512.8671 | 2872.0233 | 3191.0258 | 3454.5573 | 3670.2723 | 3851.677
SA | 29.3453 | 49.5456 | 75.7799 | 107.6032 | 145.2399 | 187.0912 | 232.0715 | 282.1929 | 336.7334 | 398.007 | 468.5544 | 547.9523 | 629.4095 | 704.2329 | 772.2185 | 835.381 | 894.784 | 951.2647 | 1004.9796 | 1055.8335 | 1103.7031 | 1149.4092 | 1191.877
Tas | 2.6025 | 4.2463 | 6.5075 | 9.4378 | 13.1771 | 17.8563 | 23.601 | 31.2604 | 40.2812 | 50.6909 | 62.6975 | 76.0416 | 90.6383 | 106.3983 | 123.6859 | 142.2183 | 162.1509 | 184.1957 | 208.8757 | 236.144 | 266.2201 | 298.8538 | 333.4101
Vic | 30.5885 | 51.2284 | 79.4063 | 116.746 | 169.3875 | 235.2992 | 318.4423 | 417.8303 | 536.1291 | 671.4232 | 822.782 | 990.3998 | 1180.4713 | 1396.8429 | 1652.3354 | 1971.8358 | 2370.1291 | 2856.4074 | 3413.8589 | 3999.0365 | 4577.0567 | 5082.1924 | 5509.1401
Aggregation trajectories
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
45% | 0% | 5.663% | 10.02% | 13.73% | 16.97% | 19.83% | 22.37% | 24.64% | 26.68% | 28.51% | 30.17% | 31.66% | 33.02% | 34.24% | 35.36% | 36.37% | 37.3% | 38.14% | 38.91% | 39.61% | 40.25% | 40.84% | 41.37%
90% | 0% | 11.33% | 20.04% | 27.46% | 33.94% | 39.66% | 44.74% | 49.28% | 53.36% | 57.02% | 60.33% | 63.32% | 66.03% | 68.49% | 70.72% | 72.75% | 74.6% | 76.28% | 77.82% | 79.22% | 80.5% | 81.67% | 82.74%
10% | 0% | 1.259% | 2.226% | 3.052% | 3.771% | 4.406% | 4.971% | 5.476% | 5.928% | 6.336% | 6.704% | 7.036% | 7.337% | 7.61% | 7.858% | 8.083% | 8.289% | 8.476% | 8.646% | 8.802% | 8.944% | 9.074% | 9.193%
Neutral capacity growth, 45% aggregation by 2050 (MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 0 | 7.498 | 25.1568 | 56.0691 | 95.8798 | 142.8159 | 196.0542 | 253.9814 | 314.6069 | 377.6072 | 442.051 | 507.2804 | 573.3688 | 634.0407 | 687.346 | 739.0638 | 791.1104 | 842.6658 | 894.5687 | 945.6946 | 995.9981 | 1028.3607 | 1078.3672
Qld | 0 | 4.032 | 13.6923 | 30.9345 | 51.8416 | 75.3569 | 100.2728 | 126.2546 | 152.7033 | 179.8653 | 207.739 | 236.1665 | 265.0381 | 294.2611 | 323.755 | 353.0294 | 382.4341 | 411.934 | 440.4349 | 467.9928 | 494.5274 | 519.6101 | 543.8206
SA | 0 | 1.3724 | 4.6986 | 10.6141 | 18.2709 | 27.3616 | 37.6467 | 49.2016 | 61.6345 | 74.7964 | 88.5706 | 102.8717 | 117.6225 | 132.3793 | 146.6603 | 160.356 | 172.1433 | 183.121 | 194.0903 | 204.3917 | 214.6422 | 224.7792 | 234.8786
Tas | 0 | 0.32761 | 1.1074 | 2.4017 | 3.9644 | 5.8927 | 7.4173 | 8.7301 | 9.7122 | 10.6559 | 11.4994 | 12.2389 | 12.9664 | 13.6654 | 14.3392 | 14.99 | 15.6194 | 16.229 | 16.8197 | 17.3928 | 17.9487 | 18.4872 | 19.0115
Vic | 0 | 4.454 | 15.5741 | 34.1933 | 54.664 | 76.9652 | 100.4807 | 125.6983 | 151.7562 | 178.5289 | 205.3924 | 232.5471 | 260.3066 | 288.6046 | 317.3904 | 346.1144 | 373.6049 | 399.891 | 425.0202 | 448.7611 | 471.3436 | 492.537 | 512.7402
Neutral capacity growth, 90% aggregation by 2050 (MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 0 | 14.9959 | 50.3135 | 112.1383 | 191.7596 | 285.6319 | 392.1085 | 507.9628 | 629.2138 | 755.2145 | 884.102 | 1014.5609 | 1146.7376 | 1268.0814 | 1374.692 | 1478.1275 | 1582.2208 | 1685.3315 | 1789.1374 | 1891.3891 | 1991.9963 | 2056.7214 | 2156.7344
Qld | 0 | 8.064 | 27.3846 | 61.869 | 103.6833 | 150.7139 | 200.5457 | 252.5092 | 305.4067 | 359.7307 | 415.478 | 472.3329 | 530.0762 | 588.5222 | 647.51 | 706.0588 | 764.8681 | 823.8679 | 880.8698 | 935.9855 | 989.0548 | 1039.2202 | 1087.6411
SA | 0 | 2.7449 | 9.3972 | 21.2282 | 36.5418 | 54.7233 | 75.2934 | 98.4033 | 123.269 | 149.5928 | 177.1413 | 205.7433 | 235.245 | 264.7586 | 293.3206 | 320.712 | 344.2867 | 366.2419 | 388.1807 | 408.7833 | 429.2845 | 449.5584 | 469.7572
Tas | 0 | 0.65522 | 2.2148 | 4.8034 | 7.9288 | 11.7855 | 14.8346 | 17.4601 | 19.4244 | 21.3119 | 22.9989 | 24.4779 | 25.9328 | 27.3307 | 28.6784 | 29.9799 | 31.2388 | 32.4579 | 33.6395 | 34.7857 | 35.8974 | 36.9744 | 38.023
Vic | 0 | 8.9081 | 31.1482 | 68.3866 | 109.328 | 153.9304 | 200.9614 | 251.3966 | 303.5124 | 357.0578 | 410.7848 | 465.0942 | 520.6132 | 577.2093 | 634.7808 | 692.2289 | 747.2098 | 799.7819 | 850.0405 | 897.5222 | 942.6873 | 985.0741 | 1025.4805
Neutral capacity growth, 10% aggregation by 2050 (MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 0 | 1.6662 | 5.5904 | 12.4598 | 21.3066 | 31.7369 | 43.5676 | 56.4403 | 69.9126 | 83.9127 | 98.2336 | 112.729 | 127.4153 | 140.8979 | 152.7436 | 164.2364 | 175.8023 | 187.2591 | 198.793 | 210.1543 | 221.3329 | 228.5246 | 239.6372
Qld | 0 | 0.896 | 3.0427 | 6.8743 | 11.5204 | 16.746 | 22.2829 | 28.0566 | 33.9341 | 39.9701 | 46.1642 | 52.4814 | 58.8974 | 65.3914 | 71.9456 | 78.451 | 84.9853 | 91.5409 | 97.8744 | 103.9984 | 109.895 | 115.4689 | 120.849
SA | 0 | 0.30499 | 1.0441 | 2.3587 | 4.0602 | 6.0804 | 8.3659 | 10.9337 | 13.6966 | 16.6214 | 19.6824 | 22.8604 | 26.1383 | 29.4176 | 32.5912 | 35.6347 | 38.2541 | 40.6935 | 43.1312 | 45.4204 | 47.6983 | 49.9509 | 52.1952
Tas | 0 | 0.072803 | 0.24608 | 0.53371 | 0.88097 | 1.3095 | 1.6483 | 1.94 | 2.1583 | 2.368 | 2.5554 | 2.7198 | 2.8814 | 3.0367 | 3.1865 | 3.3311 | 3.471 | 3.6064 | 3.7377 | 3.8651 | 3.9886 | 4.1083 | 4.2248
Vic | 0 | 0.98979 | 3.4609 | 7.5985 | 12.1476 | 17.1034 | 22.329 | 27.933 | 33.7236 | 39.6731 | 45.6428 | 51.6771 | 57.8459 | 64.1344 | 70.5312 | 76.9143 | 83.0233 | 88.8647 | 94.4489 | 99.7247 | 104.743 | 109.4527 | 113.9423
Strong capacity growth, 90% aggregation by 2050 (MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 0 | 8.9655 | 24.3139 | 46.0732 | 78.222 | 121.4353 | 178.2137 | 248.7844 | 334.9564 | 436.23 | 552.3156 | 683.5138 | 831.1642 | 1001.9866 | 1200.249 | 1430.0296 | 1697.9294 | 2011.1945 | 2363.165 | 2747.8609 | 3130.9236 | 3485.3851 | 3798.1984
Qld | 0 | 8.5468 | 23.0869 | 44.9447 | 75.7116 | 116.1565 | 167.7808 | 230.4022 | 304.0521 | 390.2056 | 488.0172 | 599.2901 | 731.7275 | 889.5094 | 1083.9856 | 1320.4695 | 1600.6164 | 1916.8511 | 2234.9272 | 2527.9001 | 2780.9079 | 2997.5264 | 3186.9291
SA | 0 | 5.6118 | 15.185 | 29.5521 | 49.2958 | 74.1949 | 103.8271 | 139.0679 | 179.6677 | 226.9563 | 282.6864 | 346.9777 | 415.6083 | 482.3191 | 546.1159 | 607.7394 | 667.4881 | 725.6383 | 782.0467 | 836.4212 | 888.4776 | 938.7272 | 986.175
Tas | 0 | 0.48096 | 1.304 | 2.592 | 4.4724 | 7.0813 | 10.5589 | 15.4055 | 21.4925 | 28.9056 | 37.8264 | 48.1515 | 59.8498 | 72.8707 | 87.4712 | 103.4638 | 120.9608 | 140.5072 | 162.5411 | 187.071 | 214.3064 | 244.0751 | 275.8679
Vic | 0 | 5.8024 | 15.9116 | 32.0631 | 57.4917 | 93.3129 | 142.4687 | 205.9116 | 286.0574 | 382.867 | 496.3976 | 627.1469 | 779.4824 | 956.6779 | 1168.5379 | 1434.51 | 1768.0612 | 2178.9085 | 2656.5683 | 3167.9984 | 3684.5164 | 4150.6473 | 4558.3362
Typical non-aggregated battery daily charge and discharge profile | 2025-26: Percentage aggregation trajectory

## Base LRET
Large-scale Renewable Energy Target
Source: http://www.cleanenergyregulator.gov.au/RET/Scheme-participants-and-industry/the-renewable-power-percentage
Calendar year | Target (GWh, Australia) | Target (GWh, NEM)1 | Financial year3 | Target (GWh, NEM) | With 1997 baseline4
2017 | 26031 | 21840.009 | 2016-17
2018 | 28637 | 24026.443 | 2017-18 | 22933.226 | 37359.206
2019 | 31244 | 26213.716 | 2018-19 | 25120.0795 | 39546.0595
2020 | 33850 | 28400.15 | 2019-20 | 27306.933 | 41732.913
2021 | 33000 | 27687 | 2020-21 | 28043.575 | 42469.555
2022 | 33000 | 27687 | 2021-22 | 27687 | 42112.98
2023 | 33000 | 27687 | 2022-23 | 27687 | 42112.98
2024 | 33000 | 27687 | 2023-24 | 27687 | 42112.98
2025 | 33000 | 27687 | 2024-25 | 27687 | 42112.98
2026 | 33000 | 27687 | 2025-26 | 27687 | 42112.98
2027 | 33000 | 27687 | 2026-27 | 27687 | 42112.98
2028 | 33000 | 27687 | 2027-28 | 27687 | 42112.98
2029 | 33000 | 27687 | 2028-29 | 27687 | 42112.98
2030 2 | 33000 | 27687 | 2029-30 | 27687 | 42112.98
1. Assumes NEM share of Australia-wide energy consumption of 83.9% (See Table L, 2016 Australian Energy Statistics).
2. The LRET target is undefined after 2030
3. LRET targets are defined on a calendar year basis, however modelling is performed on financial year basis
4. A baseline of 14425.98 GWh from NEM renewable generation existing prior to establishment of the target

## ACT auction
ACT auction
Generators with auctioned PPA agreements with the ACT government do not participate in the LRET
Generator | Commencement | Capacity (MW) | Annual Energy (GWh)
Hornsdale 1 | 2017-02-01 | 100 | 414
Ararat | 2017-04-01 | 80.5 | 271
Hornsdale 2 | 2018-12-01 | 100 | 404
Sapphire | 2018-05-01 | 100 | 350
Hornsdale 3 | 2019-10-01 | 109 | 414
Crookwell 2 | 2018-09-01 | 91 | 304
1. ACT Government Renewable energy target legislation and reporting

## Desalination
Electricity Consumption for Desalination (GWh)
Desalination plants typically procure 100% renewable energy in addition to the LRET, with the exception of Wonthaggi
| Wonthaggi Desalination Plant Full Operation1 | Wonthaggi Desalination Plant Projected1 | Wonthaggi Desalination Plant Renewable | Sydney Desalination Plant Operation mode2 | Sydney Desalination Plant Security mode2 | Sydney Desalination Plant3 | Tugun Desalination Plant Operation Mode4 | Tugun Desalination Plant Hot Standby Mode5 | Tugun Desalination Plant | Adelaide Desalination Plant Operation Mode | Adelaide Desalination Plant6 | Total
Renewable Portion |  |  | 0.2 |  |  | 1 |  |  | 1 |  | 1
2017-18 | 675 | 197.346 | 39.4692 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 102.6132
2018-19 | 675 | 199.678 | 39.9356 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 103.0796
2019-20 | 676.734 | 193.062 | 38.6124 | 355.844 | 5.014 | 5.014 | 150.902 | 3.394 | 3.394 | 501.369 | 54.9 | 101.9204
2020-21 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2021-22 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2022-23 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2023-24 | 676.734 | 190.225 | 38.045 | 355.844 | 5.014 | 5.014 | 150.902 | 3.394 | 3.394 | 501.369 | 54.9 | 101.353
2024-25 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2025-26 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2026-27 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2027-28 | 676.734 | 190.225 | 38.045 | 355.844 | 5.014 | 5.014 | 150.902 | 3.394 | 3.394 | 501.369 | 54.9 | 101.353
2028-29 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
2029-30 | 675 | 190.225 | 38.045 | 354.871 | 5 | 5 | 150.489 | 3.394 | 3.394 | 500 | 54.75 | 101.189
1. Essential Services Commission, Melbourne Water Price Review 2016, Table 3.5
2. Sydney Desalination Plant Regulatory Proposal to IPART 2017
3. Sydney Desalination Plant currently operates in water security mode and is assumed to continue to do so.
4. Based on 412.3MWh per day in full operation
5. Estimated 3ML/day
6. Estimated 30ML/day and 5MWh/ML

## GreenPower
GreenPower
Energy generated to satisfy GreenPower requirements is additional to LRET targets
Calendar Year | Green Power1 | Financial year | Green Power2 | Actual | Projected3
2008 | 1985 | 2007-08
2009 | 2195 | 2008-09 | 2090 | 2090
2010 | 2195 | 2009-10 | 2195 | 2195
2011 | 2094 | 2010-11 | 2144.5 | 2144.5
2012 | 1820 | 2011-12 | 1957 | 1957
2013 | 1446 | 2012-13 | 1633 | 1633
2014 | 1279 | 2013-14 | 1362.5 | 1362.5
2015 | 1092 | 2014-15 | 1185.5 | 1185.5
2016 | 949 | 2015-16 | 1020.5 |  | 1020.5
2017 | 818 | 2016-17 | 883.5 |  | 883.5
2018 | 705 | 2017-18 | 761.5 |  | 761.5
2019 | 608 | 2018-19 | 656.5 |  | 656.5
2020 | 524 | 2019-20 | 566 |  | 566
2021 | 451 | 2020-21 | 487.5 |  | 487.5
2022 | 389 | 2021-22 | 420 |  | 420
2023 | 335 | 2022-23 | 362 |  | 362
2024 | 289 | 2023-24 | 312 |  | 312
2025 | 249 | 2024-25 | 269 |  | 269
2026 | 215 | 2025-26 | 232 |  | 232
2027 | 185 | 2026-27 | 200 |  | 200
2028 | 160 | 2027-28 | 172.5 |  | 172.5
2029 | 138 | 2028-29 | 149 |  | 149
2030 | 119 | 2029-30 | 128.5 |  | 128.5
1. GreenPower annual audit reports, 2008 to 2015. Available at http://www.greenpower.gov.au/search%20results?keyword=audit
2. Actual and projected subscriptions are reported on a calendar year basis and converted to financial year basis for modelling.
3. Subscription to GreenPower has declined since 2011. Projected subscriptions continue the trend on an exponential curve fitted to 2011 to 2015 data.

## Effective LRET
Large-scale Renewable Energy Target
Financial year | Base Target (including grandfathered hydro) (GWh) | GreenPower (GWh) | Desalination (GWh) | Effective Target (GWh) | Penalty Price ($/MWh)1
2017-18 | 37359.206 | 761.5 | 102.6132 | 38223 | 92.8571
2018-19 | 39546.0595 | 656.5 | 103.0796 | 40306 | 90.5923
2019-20 | 41732.913 | 566 | 101.9204 | 42401 | 88.3828
2020-21 | 42469.555 | 487.5 | 101.189 | 43058 | 86.2271
2021-22 | 42112.98 | 420 | 101.189 | 42634 | 84.124
2022-23 | 42112.98 | 362 | 101.189 | 42576 | 82.0722
2023-24 | 42112.98 | 312 | 101.353 | 42526 | 80.0704
2024-25 | 42112.98 | 269 | 101.189 | 42483 | 78.1175
2025-26 | 42112.98 | 232 | 101.189 | 42446 | 76.2122
2026-27 | 42112.98 | 200 | 101.189 | 42414 | 74.3533
2027-28 | 42112.98 | 172.5 | 101.353 | 42387 | 72.5399
2028-29 | 42112.98 | 149 | 101.189 | 42363 | 70.7706
2029-30 | 42112.98 | 128.5 | 101.189 | 42343 | 69.0445
1. Penalty price is calculated as an uplift of the $65 nominal penalty scaled by a 30% corporate tax rate and a 2.5% annual CPI adjustment

## QRET
Queensland Renewable Energy Target
50% of Queensland consumption to be provided by renewable generation by 2030 target
Queensland large-scale renewable generation (GWh)
Financial year | Neutral BAU | Fast Change | Slow Change | High DER
2020-21 | 0 | 0 | 0 | 0
2021-22 | 0 | 400 | 0 | 700
2022-23 | 2400 | 2900 | 1400 | 3100
2023-24 | 4700 | 5500 | 3400 | 5600
2024-25 | 7200 | 8200 | 5400 | 8000
2025-26 | 10100 | 11000 | 7500 | 10800
2026-27 | 12600 | 14300 | 9600 | 13200
2027-28 | 15200 | 17300 | 11500 | 15400
2028-29 | 17800 | 20300 | 13400 | 17500
2029-30 | 20500 | 23600 | 15500 | 19500
Trajectory of total large scale generation of renewable energy required, including Q400 auction eligible, as calculated by the QLD Government Expert Panel report: https://www.dnrm.qld.gov.au/__data/assets/pdf_file/0018/1259010/qreep-renewable-energy-target-report.pdf
To deliver reasonable technological diversity, wind generation is assumed to provide at least 25% of the annual targets

## VRET
Victorian Renewable Energy Target
25% renewable energy generation by 2020, 40% renewable energy generation by 2025
New entry renewable capacity (MW)
| Solar | Wind | Total
2019-20 | 200 | 500 | 700
2020-21 | 360 | 900 | 1260
2021-22 | 520 | 1300 | 1820
2022-23 | 680 | 1700 | 2380
2023-24 | 840 | 2100 | 2940
2024-25 | 1000 | 2500 | 3500

## Emission Trajectory
Emissions Target Trajectories
Emissions reduction targets are expressed as a percentage of total emissions across all sectors. This table includes electricity NEM generation emissions only.
Financial Year | 28% to 70% Emissions Reduction Target | 52% to 90% Emissions Reduction Target
(Mt CO2-e)
2020-21 | 142 | 142
2021-22 | 140.5296 | 136.2446
2022-23 | 139.0592 | 130.4891
2023-24 | 137.5887 | 124.7337
2024-25 | 136.1183 | 118.9783
2025-26 | 134.6479 | 113.2228
2026-27 | 133.1775 | 107.4674
2027-28 | 131.7071 | 101.712
2028-29 | 130.2366 | 95.9566
2029-30 | 128.7662 | 90.2011
2030-31 | 127.2958 | 84.4764
2031-32 | 123.3412 | 81.065
2032-33 | 119.3866 | 77.6536
2033-34 | 115.4319 | 74.2423
2034-35 | 111.4773 | 70.8309
2035-36 | 107.5227 | 67.4195
2036-37 | 103.5681 | 64.0081
2037-38 | 99.6134 | 60.5968
2038-39 | 95.6588 | 57.1854
2039-40 | 91.7042 | 53.774
2040-41 | 87.7496 | 50.3627
2041-42 | 83.7949 | 46.9513
2042-43 | 79.8403 | 43.5399
2043-44 | 75.8857 | 40.1285
2044-45 | 71.9311 | 36.7172
2045-46 | 67.9764 | 33.3058
2046-47 | 64.0218 | 29.8944
2047-48 | 60.0672 | 26.483
2048-49 | 56.1125 | 23.0717
2049-50 | 52.1579 | 19.6603
2030 emissions reduction targets are calculated from 2005 levels.
2050 emissions reduction targets are calculated from 2005 levels for the 90% trajectory, and 2016 levels for the 70% trajectory.
The emissions trajectory starts at estimated emissions for 2020-21.

## Interconnector Capability
Interconnector Transfer Capability (MW)
Worst-case transfer limits at times of peak demand in the receiving region. Used in capacity expansion modelling1
Interconnector | Forward Direction | Forward capability1,2 | Reverse Capability1,2
QNI | NSW to QLD | 310 | 1025
Terranora | NSW to QLD | 50 | 150
VIC-NSW | VIC to NSW | 700 | 400
Heywood | VIC to SA | 650 | 650
Murraylink2 | VIC to SA | 220 | 200
Basslink | TAS to VIC | 478 | 478
1. Time-sequential modelling uses higher thermal limits combined with constraint equations to better capture network conditions impacting flow capability. In real time operation transfer capability is determined by constraint equations.
2. Forward capability is limited by thermal limitations in the Victorian 220kV transmission network. Reverse capability is limited by thermal limitations in the South Australian 132kV transmission network.
3. Further details are available in the 2017 Interconnector Capabilities report.

## Proportioning factors
Proportioning Factors for Inter-Regional Losses
Losses due to interconnector flow are assigned asymmetrically to regions either side of the interconnector1
Notional Interconnector | Proportioning Factor | Region applied to
Queensland - New South Wales (QNI) | 0.62 | New South Wales
Queensland - New South Wales (Terranora) | 0.61 | New South Wales
Victoria - New South Wales | 0.2 | New South Wales
Victoria - South Australia (Heywood) | 0.44 | Victoria
Victoria - South Australia (Murraylink) | 0.65 | Victoria
Tasmania - Victoria (Basslink)2 | 0.5 | Victoria
1. For derivation of loss factors, see Regional Boundaries and Marginal Loss Factors for the 2017-18 Financial Year
2. Basslink is not a regulated interconnector. A value of 0.5 has been assumed. The same proportioning factors to new interconnector developments as are calculated for the existing interconnectors between the same regions. Connection between New South Wales and South Australia via Riverlink assumed a proportioning factor of 0.5.

## Augmentation options
Interconnector augmentation options
Long-term modelling considers the following potential options for augmenting transmission between NEM regions in all core scenarios except the Snowy 2.0 and Battery of the Nation sensitivity.
Interconnector | Option label | Project description | Forward Direction | Notional Limit |  | Cost Estimate ($ millions) | Earliest commissioning year1
|  |  |  | Forward direction | Reverse direction
QNI | Do Nothing | Do nothing | NSW to QLD | 310 | 1025 | 0 | #N/A
| QNI-Option 1 | Establish a mid-way switching station for both transmission lines between Armidale and Dumaresq substations. Establish a mid-way switching station for both Dumaresq and Bulli Creek substations. | NSW to QLD | 310 | 1111 | 40 | 2020
| QNI-Option 2 | Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Second SVC at Armidale 330 kV. | NSW to QLD | 610 | 1075 | 63 | 2020
| QNI-Option 3 | Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Install SVCs at Dumaresq and Tamworth substations. Install shunt capacitor banks at Tamworth, Armidale and Dumaresq substations. | NSW to QLD | 770 | 1215 | 142 | 2020
| QNI-Option 4 | Second HVAC interconnector at 330 kV Establish three new switching stations at Narrabri/Gunnedah area, west of Armidale and west of Dumaresq. Install Bayswater-Narrabri/Gunnedah site-Armidale west-Dumaresq west-Bulli Creek-Western Down 330 kV new double circuit line. Install Narrabri/Gunnedah site-Tamworth, west of Armidale-Armidale and west of Dumaresq-Dumaresq 330 kV new single circuit line. Augment existing substations/switching stations at Bayswater, Tamworth, Armidale, Dumaresq, Bulli Creek and Western Downs. | NSW to QLD | 1860 | 2000 | 1330 | 2023
| QNI-Option 5 | New Armidale-Bulli Creek HVAC at 330 kV Install Armidale-Dumaresq and Dumaresq-Bulli Creek additional new 330 kV double circuit line. Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Augment existing substations/switching stations at Armidale, Dumaresq and Bulli Creek. | NSW to QLD | 770 | 1593 | 560 | 2023
| QNI-Option 6 | 500 kV HVAC QLD-NSW interconnector Establish three new 500/330 kV substations at Dumaresq, Armidale and Gunnedah/Narrabri area. Augment Bulli Creek substation to establish 500 kV switchyard. Install Bayswater/Wollar - Gunnedah/Narrabri site - west of Armidale-west of Dumaresq - Bulli Creek - Western Downs 500 kV new double circuit line. Install new 330 kV single circuit lines from new 500/330 kV substations to existing 330 kV substations. Augment Dumaresq, Armidale Tamworth and Bulli Creek 330 kV substations, Bayswater 500/330 kV and Western Downs 275 kV substations. | NSW to QLD | 2400 | 2500 | 2360 | 2024
VIC-NSW | Do Nothing | Do nothing | VIC-NSW | 700 | 400 | 0 | #N/A
| VIC-NSW Option 1 (Dederang-Lower Tumut path VIC to NSW export) | Install second 500/330 kV 1000 MVA transformer at South Morang. Install a braking resister at Loy Yang or battery storage or FACTS device to increase transient stability. Uprate Dederang-South Morang 330 kV lines and series capacitors. Uprate Canberra-Upper Tumut 330 kV line. | VIC-NSW | 870 | 400 | 78.5 | 2020
| VIC-NSW Option 3 (Dederang-Lower Tumut path NSW to VIC NSW export) | Series compensation on Wodonga-Dederang 330 kV line (50% series compensation). Phase angle regulator on the Jindera-Wodonga 330 kV line (1000 MVA). Uprate Dederang-South Morang 330 kV lines and series capacitors. Install fourth 330/220 kV 340 MVA transformer at Dederang. 2x150 MVAr 330 kV shunt capacitor banks at Wodonga, Jindera or Wagga. | VIC-NSW | 700 | 800 | 115 | 2020
| VIC-NSW Option 4 | New Wagga-Yass, Wagga-Jindera and Jindera-Dederang 330 kV single circuit configuration. Uprate Canberra-Upper Tumut 330 kV circuit. Uprate Yass-Marulan 330 kV circuits. Uprate Dederang-South Morang 330 kV circuits and series capacitors. Install second 500/330 kV 1000 MVA transformer at South Morang. Install fourth 330/220 kV 340 MVA transformer at Dederang. Phase angle regulator on Lower Tumut-Wagga 330 kV line (1000 MVA) 2x150 MVAr 330 kV shunt capacitor banks at Wodonga, Jindera or Wagga | VIC-NSW | 1300 | 800 | 530 | 2023
| VIC-NSW Option 5 (South Morang-Murray path) | New Murray-Dederang 330 kV single circuit line. New Dederang-South Morang 330 kV single circuit with series capacitors Install second 500/330 kV 1000 MVA transformer at South Morang Install fourth 330/220 kV 340 MVA transformer at Dederang Uprate Canberra-Upper Tumut 330 kV circuit Uprate Yass-Marulan 330 kV circuits 2x150 MVAr 330 kV shunt capacitor banks at Wodonga, Jindera or Wagga | VIC-NSW | 1100 | 1400 | 525 | 2023
| VIC-NSW Option 6 (Bendigo-Wagga path) | New Sydenham-Bendigo-Wagga 500 kV double circuit line. New Wagga-Snowy 2.0-Bannaby-Wagga 500 kV single circuit line. Establish 500/220 kV terminal station at Bendigo, 500/330 kV substation at Wagga and Snowy 2.0. Cut-in Lower Tumut and Upper Tumut 330 kV line at Snowy 2.0. 2x500/220 kV 1000 MVA transformers at Bendigo. 2x500/330 kV 1000 MVA transformers at Wagga. 2x500/330 kV 1500 MVA transformers at Snowy 2.0. Power flow controller on Bannaby-Sydney West 330 kV line. | VIC-NSW | 2400 | 2400 | 2200 | 2023
| VIC-NSW Option 7 (Kerang-Darlington path) | New Sydenham-Ballarat-Bendigo-Kerang-Darlington Point-Wagga 500 kV double circuit line. New Wagga-Snowy 2.0-Bannaby-Wagga 500 kV single circuit line. Cut-in Lower Tumut and Upper Tumut 330 kV line at Snowy 2.0. 2x500/220 kV 1000 MVA transformers at Ballarat, Bendigo and Kerang. 2x500/330 kV 1000 MVA transformers at Darlington Point and Wagga. 2x500/330 kV 1500 MVA transformers at Snowy 2.0. Power flow controller on Bannaby-Sydney West 330 kV line. | VIC-NSW | 2800 | 2200 | 2700 | 2023
| VIC-NSW Option 8 | New Ballarat-Kerang-Darlington Point 330 kV double line. Additional new Darlington Point-Wagga 330 kV single circuit line. New Ballarat-Sydenham/Moorabool 500 kV double circuit line. New Wagga-Snowy 2.0-Bannaby-Wagga 500 kV single circuit line. Cut-in Lower Tumut and Upper Tumut 330 kV line at Snowy 2.0. 2x330/220 kV 600 MVA transformers at Ballarat and Kerang. 2x500/330 kV 1000 MVA transformers at Ballarat. 2x500/330 kV 1000 MVA transformers at Wagga. 2x500/330 kV 1500 MVA transformers at Snowy 2.0. Power flow controller on Bannaby-Sydney West 330 kV line. | VIC-NSW | 1500 | 1200 | 2300 | 2023
VIC-TAS | Do Nothing | Do nothing | TAS to VIC | 478 | 478 |  | #N/A
| VIC-TAS Second IC - Stage 1 | A ±320 kV, 600 MW monopole HVDC (voltage source converter) transmission system between Port Latta/Smithton (Tasmania) and East Geelong (Victoria). New 220 kV double circuit line between Sheffield and Port Latta/Smithton in Tasmania. Uprate 220 kV circuits between Geelong and East Geelong. | TAS to VIC | 1178 | 1178 | 888 | 2025
| VIC-TAS Third IC - Stage 2 | VIC-TAS Second IC Stage 1 plus A ±320 kV, 600 MW monopole HVDC (voltage source converter) transmission system between Sheffield (Tasmania) and Tyabb (Victoria). | TAS to VIC | 1878 | 1878 | 1776 | 2025
VIC - SA (Heywood) | Do Nothing | Do nothing | VIC-SA | 650 | 650 | 0 | #N/A
SA-NSW | SA-NSW Riverlink option (see note 2 & 3) | New Robertstown-Buronga-Darlington Point 330 kV double circuit line. An additional 330 kV single circuit from Darlington Point-Wagga. 2x275/330 kV transformers at Robertstown. 4x330 kV Phase Shift transformers at Buronga. A new 330/220 kV transformer at Buronga. Reactive compensation. (Heywood transfer limit) ((Combined Heywood+Riverlink transfer limit)) | NSW-SA (VIC-SA) ((NSW/VIC-SA)) | 750 (750) ((1300)) | 750 (750) ((1500)) | 1270 | 2021
VIC-SA | SA-VIC Horsham link option (see note 2 & 3) | New Tungkillo-Horsham 275 kV double circuit line. Replacing existing Horsham-Ballarat 220 kV single circuit line to a double circuit 220 kV line. An additional 220 kV double circuit line from Ballarat to Moorabool. New 275/220 kV phase shifting transformers at Horsham. | VIC-SA (VIC-SA) ((VIC-SA)) | 650 (750) ((950)) | 650 (750) ((1150)) | 993 | 2021
SA-QLD | SA-QLD Option 1 (see note 2, 3 & 4) | A new HVDC VSC bi-pole from Davenport (SA) to Bulli Creek (QLD). 700 MVA HVDC overhead lines. HVAC transformer at Davenport and Bulli Creek. (Heywood transfer limit) ((Combined Heywood + SA to QLD link limit)) [QNI transfer limit] | QLD-SA (VIC-SA) ((QLD-SA+VIC-SA)) [NSW-QLD] | 700 (900) ((1350)) [560] | 700 (900) ((1350)) [1400] | 1445 | 2023
Note:
1. Option cannot be built before this date, to account for development lead times
2. With a second SA interconnector to Eastern States, VIC-SA Heywood transfer limit would be raised. This is given within brackets ( )
3. Values in double bracket (( )) represent the total transfer level with the existing VIC-SA Heywood interconnector and a new SA interconnector to Eastern States.
4. A HVDC interconnector between SA and QLD would increase transfer levels on QNI and VIC-SA Heywood interconnector limits.
The following potential VIC-NSW and VIC-TAS options are considered in the Snowy 2.0 and Battery of the Nation sensitivity to replace the VIC-NSW option 5-8 and VIC-TAS Second and Third IC options in the table above.
Interconnector | Option label | Project description | Forward Direction | Notional Limit |  | Cost Estimate ($ millions) | Earliest commissioning year1
|  |  |  | Forward direction | Reverse direction
VIC-NSW (see note 6) | VIC-NSW Option 5A (South Morang-Murray path) | New Murray-Dederang 330 kV double circuit line. New Dederang-South Morang 330 kV single circuit with series capacitors. Install second 500/330 kV 1000 MVA transformer at South Morang. Install fourth 330/220 kV 340 MVA transformer at Dederang. 2x150 MVAr 330 kV shunt capacitor banks at Wodonga, Jindera or Wagga. | VIC-NSW | 1250 (see note 5) | 1400 | 542 | 2024
| VIC-NSW Option 6A (Bendigo-Wagga path) | New Sydenham-Bendigo-Wagga 500 kV double circuit line. Establish 500/220 kV terminal station at Bendigo. 2x500/220 kV 1000 MVA transformers at Bendigo. 1x500/330 kV 1000 MVA transformers at Wagga. | VIC-NSW | 2400 (see note 5) | 2400 | 1050 | 2024
| VIC-NSW Option 7A (Kerang-Darlington path) | New Sydenham-Ballarat-Bendigo-Kerang-Darlington Point-Wagga 500 kV double circuit line. 2x500/220 kV 1000 MVA transformers at Ballarat, Bendigo and Kerang. 2x500/330 kV 1000 MVA transformers at Darlington Point. 1x500/330 kV 1000 MVA transformer at Wagga. | VIC-NSW | 2800 (see note 5) | 2200 | 1550 | 2024
| VIC-NSW Option 8A | New Ballarat-Kerang-Darlington Point 330 kV double line. Additional new Darlington Point-Wagga 330 kV single circuit line. New Ballarat-Sydenham/Moorabool 500 kV double circuit line. 2x330/220 kV 600 MVA transformers at Ballarat and Kerang. 2x500/330 kV 1000 MVA transformers at Ballarat. 1x500/330 kV 1000 MVA transformers at Wagga. | VIC-NSW | 1200 (see note 5) | 900 | 1150 | 2024
VIC-TAS | VIC-TAS Battery of the Nation - Stage 1 (see note 7) | A ±320 kV, 600 MW monopole HVDC (voltage source converter) transmission system between Port Latta/Smithton (Tasmania) and East Geelong (Victoria). New 220 kV double circuit line between Sheffield and Port Latta/Smithton in Tasmania. Uprate 220 kV circuits between Geelong and East Geelong. | TAS to VIC | 1178 | 1178 | 888 | 2024
| VIC-TAS Battery of the Nation - Stage 2 | VIC-TAS Second IC Stage 1 plus A ±320 kV, 600 MW monopole HVDC (voltage source converter) transmission system between Sheffield (Tasmania) and Tyabb (Victoria). | TAS to VIC | 1878 | 1878 | 888 | 2024
Note:
5. Total flow (VNI) + Upper/Lower Tumut generation + Snowy 2.0 generation <= 5100 MW all time from 2024.
6. VIC-NSW with Snowy 2.0. It is assumed 500 kV network expansion in place to connect Snowy 2.0 to Bannaby. A 500 kV single circuit from Snowy 2.0-Wagga-Bannaby-Snowy 2.0 and connection of Snowy 2.0 on to the Lower Tumut and Upper Tumut 300 kV line.
7. VIC-TAS - It is assumed VIC-TAS second interconnector in place as part of Battery of the Nation project.

## Hydro Inflows
Hydroelectric Storage Inflows (GWh)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Blowering | - | - | - | - | - | - | - | - | 6.3 | 24.6 | 30.7 | 34.3
Eucumbene | 328 | 330 | 100 | 329 | 434 | 750 | 749 | 434 | 435 | 434 | 154 | 293
Fitzroy Falls | bar: Jan to Dec
Guthega | 4.6 | 1.6 | 0.3 | 0.8 | 4 | 7.3 | 9.3 | 14.8 | 20.6 | 33.5 | 25.3 | 14.2
Koombooloomba Dam | 15.6 | 21.5 | 22.6 | 16.8 | 22.5 | 40 | 35.9 | 72.8 | 62.7 | 50.7 | 35.9 | 44.5
Kuranda Weir | 31.2 | 25.3 | 29.4 | 17 | 28.7 | 27.3 | 17.4 | 12.5 | 30 | 18.5 | 16.3 | 12.6
Split Yard Creek Dam | bar: Jan to Dec
Eildon | 3.8 | 1.8 | 1.9 | 3.4 | 5.5 | 18.8 | 33.7 | 45.7 | 48.6 | 33.4 | 16.5 | 6.5
Dartmouth | 10.1 | 7.7 | 4.1 | 5 | 9.7 | 20.9 | 32.1 | 42.7 | 58.8 | 50.8 | 26.4 | 16.7
Derwent | 13.3 | 11.5 | 4.1 | 44 | 281.4 | 263.7 | 297.5 | 254.9 | 537.3 | 541.2 | 102.6 | 118.6
Anthony/Pieman Pond | 46.3 | 35.6 | 45.7 | 66.3 | 324.2 | 211.9 | 246.8 | 136.4 | 323.9 | 277.3 | 54.6 | 103.2
Burbury | 9.3 | 14.4 | 15.1 | 35.3 | 132 | 65.9 | 65.1 | 35.1 | 114.1 | 86.6 | 5.3 | 42.4
Lake Gordon | 23.9 | 26 | 34.3 | 69.4 | 264.7 | 143 | 156.4 | 75.1 | 242.1 | 191.5 | 11.8 | 119.5
Great Lake/Trevallyn pond | 3.7 | 2.7 | 3.7 | 9.3 | 197.2 | 133.9 | 312.5 | 144 | 295.2 | 163.7 | 92.2 | 5.2
Mersey Forth Pond | 7.9 | 8.8 | 10.3 | 26.4 | 163.7 | 141.5 | 260.2 | 133 | 272.1 | 237.6 | 93.1 | 60.6
Tasmania | Aug: Victoria
Snowy | Aug: Queensland

## Storage Initial Level
Hydroelectric Storage Initial Reservoir Levels (May 2017)
Reservoir | Initial Volume (1000 m³) | Maximum capacity (1000 m³)
Blowering | 1100667 | 1610000
Guthega | 739 | 1400
Koombooloomba Dam | 94427.1 | 184500
Kuranda Weir | 1179 | 1387
Jounama Pondage | 5705 | 27800
Murray Pondage | 5895 | 13100
Murray2Pondage | 677 | 1500
Talbingo | 113741 | 160400
Tumut Pondage | 31111 | 50000
Tumut2Pondage | 788 | 1500
Bendeela Pondage | 343 | 780
Fitzroy Falls | 711.04 | 880
Lake Yarrunga | 21600 | 36000
Split Yard Creek Dam | 4408 | 10018
Wivenhoe | 1145999 | 1165000
Anthony-Pieman Pond | 262961 | 294430
Burbury | 103219 | 233000
Derwent | 686778 | 1848200
Great Lake-Trevallyn Pond | 1008330 | 6567000
Lake Gordon | 103219 | 4699000
Mersey Forth Pond | 104582 | 227000
Dartmouth | 3002437 | 3906000
Eildon | 2176144 | 3387000
Hume Dam | 1874062 | 3040000

## Maximum capacity
Maximum capacity
Maximum capacity is used to report capacity factors and calculate fixed operating costs. It may not correspond to "installed capacity" listed in Generation Information workbooks, when maximum seasonal ratings differ.
Existing generators |  | Committed Projects 1
Generator | Installed capacity (MW) | Generator | Installed capacity (MW) | Indicative commissioning date2
Bayswater | 2640 | Barker Inlet | 216 | 2019-03-01
Eraring | 2880 | Bodangora WF | 113 | 2018-08-01
Liddell | 1800 | Crookwell 2 WF | 91 | 2018-09-01
Mount Piper | 1400 | Sapphire WF | 270 | 2018-07-01
Vales Point | 1320 | Silverton WF | 199 | 2018-07-01
Callide B | 700 | Mt Emerald | 180 | 2018-09-01
Callide Power Plant | 840 | BULGANAWF | 196 | 2019-07-01
Gladstone | 1680 | CROWLANDSWF | 80 | 2019-07-01
Kogan Creek | 744 | Mt Gellibrand WF | 132 | 2018-06-01
Millmerran | 852 | Salt Creek WF | 54 | 2018-07-01
Stanwell | 1460 | Stockyard Hill WF | 530 | 2019-12-01
Tarong | 1400 | Griffith Solar | 30 | 2019-01-01
Tarong North | 443 | Manildra Solar | 50 | 2018-07-01
Loy Yang A | 2210 | Clare Solar | 150 | 2018-05-01
Loy Yang B | 1070 | Hamilton Solar | 58 | 2018-03-01
Yallourn | 1528 | Oakey Solar | 25 | 2018-08-01
Colongra | 724 | Ross River Solar | 116 | 2018-05-01
Smithfield 1 | 109 | Rugby Run Solar | 65 | 2019-01-01
Tallawarra | 440 | Sun Metals Solar | 125 | 2018-04-01
Uranquinty | 688 | Teebar Solar | 53 | 2018-03-01
Barcaldine | 37 | Whitsunday Solar | 58 | 2018-03-01
Braemar | 1023 | Bannerton Solar | 88 | 2018-06-01
Condamine | 100 | Gannawarra Solar | 55 | 2018-04-01
Darling Downs | 633 | Karadoc Solar | 90 | 2018-04-01
Oakey | 346 | Wemen Solar | 88 | 2018-02-01
Roma | 68 | Yatpool Solar | 81 | 2018-04-01
Swanbank E2 | 365 | Bungala Solar | 110 | 2018-08-01
Yabulu | 243 | Bungala Solar Stage 2 | 220 | 2019-01-01
Yarwun | 180 | Collinsville Solar Power Station | 43 | 2019-01-01
Somerton | 162 | Darling Downs Solar | 110 | 2018-09-01
Bairnsdale | 84 | Kennedy Energy Park Solar | 15 | 2018-12-01
Jeeralang A | 224 | Kennedy Energy Park Wind | 43 | 2018-12-01
Jeeralang B | 255 | Lilyvale Solar | 100 | 2019-01-01
Laverton North | 340 | Coopers Gap WF | 453 | 2019-06-01
Mortlake | 584 | Lincoln Gap Wind Farm | 126 | 2018-10-01
Newport | 510 | Willogoleche WF | 119 | 2018-08-01
Valley Power | 336 | Beryl Solar | 100 | 2019-07-01
Hallett GT | 216 | Daydream Solar | 167 | 2018-08-01
Dry Creek | 143 | Hayman Solar | 58 | 2018-05-01
Ladbroke Grove | 84 | 1. Committed project list reflects Generation Information update from 29 December 2017.
Mintaro | 90
Osborne | 188
Pelican Point | 474
Quarantine | 220
Torrens Island A | 480
Torrens Island B | 800
Bell Bay Three | 105
Tamar Valley CCGT | 208
Tamar Valley OCGT | 58
Hunter Valley GT | 50
Mackay GT | 34
Mount Stuart | 423
Angaston | 50
Lonsdale | 20.7
Port Lincoln | 50
Port Lincoln 3 | 23.5
Port Stanvac | 57.6
Snuggery | 63
Blowering | 80
Guthega | 68
Hume | 58
Shoalhaven | 240
Tumut 1 | 328
Tumut 2 | 288
Tumut 3 | 1800
Barron Gorge | 66
Kareeya | 86.4
Wivenhoe | 500
Bogong | 150
Dartmouth | 170
Eildon | 113
McKay Creek | 150
Murray 1 | 950
Murray 2 | 560
West Kiewa | 68
Bastyan | 81
Catagunya | 50
Cethana | 95
Devils Gate | 63
Fisher | 46
Gordon | 371
John Butters | 140
Liapootah | 84
Lake Echo | 30
Lemonthyme | 54
Mackintosh | 81
Meadowbank | 44
Poatina | 342
Reece | 232
Tarraleah | 90
Trevallyn | 103
Tribute | 88
Tungatinah | 131
Wilmot | 30.6
Wayatinah | 38.4
Boco Rock WF | 113
Capital WF | 141
Cullerin Range WF | 30
Gullen Range WF | 166
Gunning WF | 47
Taralga WF | 106.8
Woodlawn WF | 48.3
Ararat WF | 240
Bald Hills WF | 107
Challicum Hills WF | 52.5
Macarthur WF | 420
Mortons Lane | 19.5
Mount Mercer WF | 131
Oaklands Hill WF | 63
PWEP 1 Yambuk WF | 30
PWEP 2 Cape Bridgewater WF | 58
PWEP 3 Cape Nelson South WF | 44
PWEP 4 Cape Nelson North WF | 47.2
Waubra WF | 192
Canunda WF | 46
Cathedral Rocks WF | 66
Clements Gap WF | 57
Hallett 1 Brown Hill WF | 95
Hallett 2 Hallett Hill WF | 74
Hallett 3 North Brown Hill WF | 132
Hallett 4 The Bluff WF | 53
Hornsdale S1 WF | 100
Hornsdale S2 WF | 100
Hornsdale S3 WF | 109
Lake Bonney 1 WF | 81
Lake Bonney 2 WF | 159
Lake Bonney 3 WF | 39
Mount Millar WF | 70
Snowtown 1 WF | 99
Snowtown 2 North WF | 144
Snowtown 2 South WF | 126
Starfish Hill WF | 35
Waterloo WF | 131
Waterloo S2 WF | 19
Wattle Point WF | 91
Musselroe WF | 168
Woolnorth WF | 140
Broken Hill Solar Plant | 53
Moree Solar | 56
Nyngan Solar | 102
Parkes Solar | 91
Kidston Solar | 50
White Rock WF | 175
Kiata WF | 31
1. Smithfield operating as a fast start OCGT from late 2017
2. Swanbank E return to service in 2018

## Firm capacity
Firm capacity
Firm capacity is power assumed to be available at times of peak demand. The ISP uses AEMO Generation Information page (2017 December release) for firm capacities for the first 10 years of the model period.
Existing and committed generators |  | Wind and solar peak contribution factor1
Generator | Firm capacity (MW) | Generator | Summer | Not summer
Bayswater1 | 2520 | Qld wind2 | - | -
Eraring | 2720 | NSW wind2 | 6.7% | 3.7%
Liddell | 1800 | Vic wind2 | 8.1% | 7.3%
Mount Piper | 1300 | SA wind2 | 9.4% | 6.7%
Vales Point | 1320 | Tas wind2 | 10.5% | 7.3%
Callide B | 700 | Solar; existing and committed to 2020-213 | 11% | 11%
Callide Power Plant | 840 | New solar, 2020-21 to 2025-26 | 5.5% | 5.5%
Gladstone | 1680 | New solar, post 2025-26 | 0% | 0%
Kogan Creek | 730
Millmerran | 760
Stanwell | 1460 | 1. Peak contribution factor refers to the percentage of total capacity expected to be available at the time of peak demand
Tarong | 1400 | 2. The ISP uses 2017 South Australian Renewable Energy Report wind contribution factors for the entire modelling horizon.
Tarong North | 443 | http://aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/SA_Advisory/2017/South-Australian-Renewable-Energy-Report-2017.pdf
Loy Yang A | 2121 | 3. As solar penetration increases, peak demand moves away from times where solar energy is available
Loy Yang B2 | 980
Yallourn | 1420
Colongra | 648
Smithfield | 162
Tallawarra | 378
Uranquinty | 640
Barcaldine | 34
Braemar | 966
Condamine | 90
Darling Downs | 580
Oakey | 281.78
Roma | 54
Swanbank E | 365
Yabulu | 233
Yarwun | 180
Somerton | 134
Bairnsdale | 78
Jeeralang A | 192
Jeeralang B | 216
Laverton North | 300
Mortlake | 518
Newport | 475
Valley Power | 270
Hallett GT | 193
Dry Creek | 112
Ladbroke Grove | 68
Mintaro | 68
Osborne | 172
Pelican Point | 458
Quarantine | 186
Torrens Island A | 480
Torrens Island B | 780
Bell Bay Three | 105
Tamar Valley CCGT | 208
Tamar Valley OCGT | 58
Hunter Valley GT | 44
Mackay GT | 34
Mount Stuart | 398
Angaston | 50
Lonsdale | 20.7
Port Lincoln | 38
Port Lincoln 3 | 18
Port Stanvac | 57.6
Snuggery | 54
Blowering | 80
Guthega | 68
Hume | 0
Shoalhaven | 240
Tumut 1 | 328
Tumut 2 | 288
Tumut 3 | 1800
Barron Gorge | 66
Kareeya | 86.4
Wivenhoe | 500
Bogong | 150
Dartmouth3 | 170
Eildon | 113
McKay Creek | 150
Murray 1 | 950
Murray 2 | 650
West Kiewa | 68
Bastyan | 81
Catagunya | 50
Cethana | 95
Devils Gate | 63
Fisher | 46
Gordon3 | 371
John Butters | 140
Liapootah | 84
Lake Echo | 30
Lemonthyme | 54
Mackintosh | 81
Meadowbank | 44
Poatina | 342
Reece | 232
Tarraleah | 90
Trevallyn | 103
Tribute | 88
Tungatinah | 131
Wilmot | 32
Wayatinah | 40
Barker Inlet | 216
New entrant OCGT | 300
New entrant CCGT | 400
New entrant Biomass | 25
1. Committed upgrades will increase the firm capacity of each of the four Bayswater units by 25MW per year from 2018-19 (an increase on the above quoted value)
2. Committed upgrade will increase the firm capacity by 78MW from 2020-21 (an increase on the above quoted value)
3. Water limited unit

## Generation limits
Modelling assumptions
The following modelling assumptions are based on internal analysis on historical generator performance.
Generating unit | Minimum Load (MW) | Generator | Minimum Capacity Factors | End time | Generator | Max Capacity Factors
BW01 | 310.5 | Tallawarra | 40% | 2020-07-01 | Liddell | 50%
BW02 | 310.5 | Condamine | 50% | 2020-07-01 | Biomass | 50%
BW03 | 310.5 | Darling Downs | 50% | 2020-07-01
BW04 | 310.5 | Yabulu | 25% | 2020-07-01
ER01 | 230 | Yarwun | 70% | 2020-07-01
ER02 | 230 | Osborne* | 60% | Depending on timing of SA interconnector expansion
ER03 | 230 | Pelican Point* | 50% | Depending on timing of SA interconnector expansion
ER04 | 230 | Torrens Island A* | 15% | Until retirement
LD01 | 260
LD02 | 260 | * South Australian minimum capacity factors are reduced consistent with the timing of a possible second synchronous interconnector.
MP1 | 280
MP2 | 280
VP5 | 250
VP6 | 250
CALL_B_1 | 175
CALL_B_2 | 175
CPP_3 | 225
CPP_4 | 225
GSTONE1 | 120
GSTONE2 | 120
GSTONE3 | 120
GSTONE4 | 120
KPP_1 | 362
MPP_1 | 170
MPP_2 | 170
STAN-1 | 180
STAN-2 | 180
STAN-3 | 180
TARONG#1 | 175
TARONG#2 | 175
TARONG#3 | 175
TNPS1 | 220
LOYYB1 | 240
LOYYB2 | 240
LYA1 | 410
LYA2 | 300
LYA3 | 410
LYA4 | 410
YWPS1 | 216
YWPS2 | 216
YWPS3 | 228
YWPS4 | 228
CPSA | 60
YARWUN_1 | 118
Torrens Island B* | 160
* Torrens Island B minimum load is reduced upon the development of a second synchronous interconnector (as appropriate)

## Reserves
Initial Regional Reserve
Each region must have firm capacity reserves in excess of maximum demand plus the largest generating unit, per region
Region | Regional Reserve Requirements (MW)
NSW | 673.2
QLD | 666.08
SA | 273
TAS | 194
VIC | 498
1. Values track changes in the capacity of the largest unit in each region (from 1 July 2020)

## Seasonal ratings
Seasonal ratings
Generator capacity may vary with weather conditions. The ISP uses AEMO Generation Information page (2017 December release) for seasonal ratings for the first 10 years of the model period.
Not all committed or advanced projects have ratings listed in Generation Information. Where information is absent Maximum Capacity is used.
Existing generators |  |  | Committed and advanced projects
Generator | Summer (MW) | Not summer (MW) | Generator | Summer (MW) | Not summer (MW)
Bayswater1 | 2520 | 2640 | Mt Emerald WF | 181 | 181
Eraring | 2720 | 2880 | Mt Gellibrand WF | 132 | 132
Liddell | 1800 | 1800 | Manildra Solar | 50 | 50
Mount Piper | 1300 | 1400 | Clare Solar | 150 | 150
Vales Point | 1320 | 1320 | Hamilton Solar | 57.5 | 57.5
Callide B | 700 | 700 | Hayman Solar | 57.5 | 57.5
Callide Power Plant | 840 | 840 | Whitsunday Solar | 57.5 | 57.5
Gladstone | 1680 | 1680 | Gannawarra Solar | 50 | 50
Kogan Creek | 730 | 744 | Bungala Solar | 220 | 220
Millmerran | 760 | 852 | Bannerton Solar | 88 | 88
Stanwell | 1460 | 1460 | Crowlands WF | 80 | 80
Tarong | 1400 | 1400 | Yatpool Solar | 81 | 81
Tarong North | 443 | 443 | Beryl Solar | 100 | 100
Loy Yang A | 2121 | 2210 | Bodangora WF | 113 | 113
Loy Yang B2 | 980 | 1070 | Sapphire WF | 270 | 270
Yallourn | 1420 | 1528 | Silverton WF | 199 | 199
Colongra | 648 | 724 | Collinsville Solar | 42.5 | 42.5
Smithfield | 104 | 109 | Coopers Gap WF | 453 | 453
Tallawarra | 378 | 440 | Darling Downs Solar | 110 | 110
Uranquinty | 640 | 688 | Daydream Solar | 167.5 | 167.5
Barcaldine | 34 | 37 | Kennedy Energy Park Wind | 43.2 | 43.2
Braemar | 966 | 1023 | Kennedy Energy Park Solar | 15 | 15
Condamine | 90 | 100 | Kidston Solar Stage 1 | 50 | 50
Darling Downs | 580 | 633 | Lilyvale Solar | 100 | 100
Oakey | 282 | 346 | Ross River Solar | 116 | 116
Roma | 54 | 68 | Rugby Run Solar | 65 | 65
Swanbank E | 365 | 365 | Sun Metals Solar | 125 | 125
Yabulu | 233 | 243 | Lincoln Gap Stage 1 WF | 126 | 126
Yarwun | 180 | 180 | Willogoleche WF | 119 | 119
Somerton | 134 | 162
Bairnsdale | 78 | 84
Jeeralang A | 192 | 224
Jeeralang B | 216 | 255
Laverton North | 300 | 340
Mortlake | 518 | 584
Newport | 475 | 510
Valley Power | 270 | 336
Hallett GT | 193 | 216
Dry Creek | 112 | 143
Ladbroke Grove | 68 | 84
Mintaro | 68 | 90
Osborne | 172 | 188
Pelican Point | 458 | 474
Quarantine | 186 | 220
Torrens Island A | 480 | 480
Torrens Island B | 780 | 800
Bell Bay Three | 105 | 105
Tamar Valley CCGT | 208 | 208
Tamar Valley OCGT | 58 | 58
Hunter Valley GT | 44 | 50
Mackay GT | 34 | 34
Mount Stuart | 398 | 423
Angaston | 50 | 50
Lonsdale | 20.7 | 20.7
Port Lincoln | 38 | 50
Port Lincoln 3 | 18 | 23.5
Port Stanvac | 57.6 | 57.6
Snuggery | 54 | 63
Blowering | 80 | 80
Guthega | 68 | 68
Hume | 58 | 0
Shoalhaven | 240 | 240
Tumut 1 | 328 | 328
Tumut 2 | 288 | 288
Tumut 3 | 1800 | 1800
Barron Gorge | 66 | 66
Kareeya | 86.4 | 86.4
Wivenhoe | 500 | 500
Bogong | 150 | 150
Dartmouth | 170 | 160
Eildon | 113 | 113
McKay Creek | 150 | 150
Murray 1 | 950 | 950
Murray 2 | 650 | 560
West Kiewa | 68 | 68
Bastyan | 81 | 81
Catagunya | 50 | 50
Cethana | 95 | 95
Devils Gate | 63 | 63
Fisher | 46 | 46
Gordon | 371 | 371
John Butters | 140 | 140
Liapootah | 84 | 84
Lake Echo | 30 | 30
Lemonthyme | 54 | 54
Mackintosh | 81 | 81
Meadowbank | 44 | 44
Poatina | 342 | 342
Reece | 232 | 232
Tarraleah | 90 | 90
Trevallyn | 103 | 103
Tribute | 88 | 88
Tungatinah | 131 | 131
Wilmot | 32 | 32
Wayatinah | 40 | 40
Boco Rock WF | 113 | 113
Capital WF | 141 | 141
Cullerin Range WF | 30 | 30
Gullen Range WF | 166 | 166
Gunning WF | 47 | 47
Taralga WF | 106.8 | 106.8
White Rock WF | 173 | 173
Woodlawn WF | 48.3 | 48.3
Ararat WF | 240 | 240
Bald Hills WF | 107 | 107
Challicum Hills WF | 52.5 | 52.5
Kiata WF | 31 | 31
Macarthur WF | 420 | 420
Mortons Lane | 19.5 | 19.5
Mount Mercer WF | 131 | 131
Oaklands Hill WF | 63 | 63
PWEP 1 Yambuk WF | 30 | 30
PWEP 2 Cape Bridgewater WF | 58 | 58
PWEP 3 Cape Nelson South WF | 44 | 44
PWEP 4 Cape Nelson North WF | 47.2 | 47.2
Waubra WF | 192 | 192
Canunda WF | 46 | 46
Cathedral Rocks WF | 66 | 66
Clements Gap WF | 57 | 57
Hallett 1 Brown Hill WF | 95 | 95
Hallett 2 Hallett Hill WF | 74 | 74
Hallett 3 North Brown Hill WF | 132 | 132
Hallett 4 The Bluff WF | 53 | 53
Hornsdale S1 WF | 100 | 100
Hornsdale S2 WF | 100 | 100
Hornsdale S3 WF | 109 | 109
Lake Bonney 1 WF | 81 | 81
Lake Bonney 2 WF | 159 | 159
Lake Bonney 3 WF | 39 | 39
Mount Millar WF | 70 | 70
Snowtown 1 WF | 99 | 99
Snowtown 2 North WF | 144 | 144
Snowtown 2 South WF | 126 | 126
Starfish Hill WF | 35 | 35
Waterloo WF | 131 | 131
Waterloo S2 WF | 19 | 19
Wattle Point WF | 91 | 91
Musselroe WF | 168 | 168
Woolnorth WF | 140 | 140
Broken Hill Solar Plant | 53 | 53
Moree Solar | 56 | 56
Nyngan Solar | 102 | 102
Parkes Solar | 55 | 54
Hornsdale Battery | 100 | 100
1. Committed upgrades will increase the firm capacity of each of the four Bayswater units by 25MW per year from 2018-19 (an increase on the above quoted value)
2. Committed upgrade will increase the firm capacity by 78MW from 2020-21 (an increase on the above quoted value)

## Generator Reliability Settings
Generator Reliability Settings
All units take the outage rate of their respective fuel type.
| Forced Outage Rate (%) 2 |  | Mean time to repair (hrs) 3 |  | Partial Outage Derating Factor 4
Fuel type | Full outage % of time | Partial outage % of time | Full outage | Partial outage
Black Coal (Qld) | 1.53% | 13.56% | 36.11 | 16.4 | 22.17%
Black Coal (NSW) | 3.99% | 25.39% | 91.91 | 19.44 | 16.82%
Brown Coal (Vic) | 4.2% | 13.59% | 29.78 | 9.29 | 21.27%
Hydro | 1.47% | 0.01% | 14.24 | 6.74 | 14.17%
Liquid Fuel | 2.5% | 0.22% | 10.69 | 19.08 | 29.49%
Gas-powered steam turbine1 | 2.82% | 3.31% | 38.89 | 121.36 | 14.85%
CCGT | 0.99% | 0.3% | 15.1 | 41.91 | 42.71%
OCGT | 2.5% | 0.22% | 10.69 | 19.08 | 29.49%
1. Gas-powered steam turbines include Darling Downs, Newport and Torrens Island A and B
2. The percentage of time per year that a generator is expected to be out of service due to forced outage.
3. The average time take to return a generating unit to service
4. The loss of capacity during a partial outage, relative to generator unit rating. If the outage factor is 20%, the generator will operate at 80% capacity during a partial outage.

## Maintenance
Maintenance rate
The percentage of time per year that a generator is expected to be out of service for maintenance.
All units take the maintenance rate of their respective fuel type
Fuel type | % of time out | Events per year
Black Coal | 5.48% | 5
Brown Coal | 5.48% | 5
Hydro | 0% | 5
Liquid Fuel | 1.37% | 5
CCGT | 5.48% | 5
OCGT | 1.37% | 5

## Build cost
Build cost ($/kW) real 2017 dollars
Cost to construct new generation, not including connection costs. Battery installations assume energy storage of 2kWh/kW. Pumped hydro installations assume energy storage of 6kWh/kW
Slow and rapid scenarios use the Neutral cost trajectories, except for technologies specified
Neutral
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Biomass | 3779.1486 | 3770.8243 | 3757.6489 | 3755.9227 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.7801 | 3752.5528 | 3752.1573 | 3752.1474 | 3752.1366 | 3752.1091 | 3752.0975 | 3752.0854 | 3752.0728 | 3752.0728 | 3752.0404 | 3752.0404 | 3752.0404 | 3752.0404 | 3751.9792 | 3751.9623 | 3751.9448 | 3751.9448 | 3751.9448 | 3751.8905
CCGT | 1500.6846 | 1500.6624 | 1500.6624 | 1500.4145 | 1500.3039 | 1499.9895 | 1499.6865 | 1499.3946 | 1499.1134 | 1498.456 | 1497.4522 | 1496.4858 | 1495.5554 | 1494.6599 | 1493.7982 | 1492.9691 | 1492.1715 | 1491.4045 | 1490.667 | 1490.3155 | 1488.7953 | 1487.3373 | 1485.9391 | 1484.5985 | 1483.3133 | 1482.0814 | 1480.9007 | 1479.7694 | 1478.6855 | 1477.2459 | 1475.5843 | 1475.5843 | 1475.5843
OCGT | 1019.607 | 1014.509 | 1009.4364 | 1004.3893 | 999.3673 | 994.3705 | 989.3986 | 984.4516 | 979.5294 | 974.6317 | 969.7586 | 964.9098 | 960.0852 | 955.2848 | 950.5084 | 945.7558 | 941.0271 | 936.3219 | 931.6403 | 926.9821 | 922.3472 | 917.7355 | 913.1468 | 908.581 | 904.0381 | 899.518 | 895.0204 | 890.5453 | 886.0925 | 881.6621 | 877.2538 | 872.8675 | 868.5032
Single-axis Tracking Solar PV2 | 1952.049 | 1733.2469 | 1634.6664 | 1492.4994 | 1421.3914 | 1363.0129 | 1316.6232 | 1270.0631 | 1228.59 | 1183.7564 | 1148.2644 | 1081.5469 | 1033.6937 | 989.6477 | 953.6746 | 913.4105 | 870.3858 | 850.5489 | 816.4325 | 798.3259 | 781.6109 | 766.1268 | 751.6697 | 737.7197 | 725.3562 | 714.8698 | 703.2892 | 692.3296 | 681.6254 | 674.1411 | 666.4251 | 658.3432 | 652.4225
Solar Thermal Central Receiver (6 hrs storage) | 4434.4078 | 3677.6191 | 3299.1963 | 3299.1963 | 3299.1963 | 3299.1963 | 3299.1963 | 3299.1963 | 3296.3035 | 3137.4812 | 3031.7736 | 2905.3182 | 2835.991 | 2794.2686 | 2789.7773 | 2692.789 | 2622.7371 | 2569.813 | 2528.4551 | 2495.2748 | 2468.0895 | 2445.4299 | 2426.2708 | 2409.8747 | 2395.6979 | 2383.3305 | 2372.4576 | 2334.1176 | 2298.9135 | 2267.3974 | 2239.0479 | 2213.4376 | 2190.2124
Wind | 1945.0567 | 1940.4151 | 1933.9305 | 1924.7814 | 1921.1002 | 1908.5778 | 1901.2725 | 1899.6705 | 1899.0957 | 1899.0103 | 1898.9173 | 1898.7687 | 1875.9565 | 1852.5714 | 1837.1539 | 1824.6411 | 1814.8729 | 1796.4291 | 1765.9848 | 1754.9462 | 1745.0069 | 1736.3499 | 1728.2481 | 1710.769 | 1707.1788 | 1704.1995 | 1701.7303 | 1699.6252 | 1696.3642 | 1691.3517 | 1684.7944 | 1679.1997 | 1674.5803
Pumped Hydro (6hrs storage) | 1386.112 | 1379.1814 | 1372.2855 | 1365.4241 | 1358.597 | 1351.804 | 1345.045 | 1338.3198 | 1331.6282 | 1324.97 | 1318.3452 | 1311.7534 | 1305.1947 | 1298.6687 | 1292.1754 | 1285.7145 | 1279.2859 | 1272.8895 | 1266.525 | 1260.1924 | 1253.8914 | 1247.622 | 1241.3839 | 1235.177 | 1229.0011 | 1222.8561 | 1216.7418 | 1210.6581 | 1204.6048 | 1198.5818 | 1192.5889 | 1186.6259 | 1180.6928
Large Scale Battery Storage (2hrs storage) | 1480.1775 | 1313.1353 | 1208.3908 | 1166.7655 | 1143.4248 | 1120.7213 | 1099.3606 | 1078.215 | 1057.298 | 1036.7828 | 1008.1032 | 986.9842 | 967.0117 | 948.3075 | 929.0063 | 910.1732 | 891.5126 | 873.1456 | 856.3527 | 840.3539 | 824.9679 | 810.2556 | 795.8776 | 781.906 | 768.1502 | 754.2991 | 741.1234 | 728.2991 | 715.8426 | 703.5834 | 691.6065 | 679.8824 | 668.3988
Black Coal (HELE) | 3268.4196 | 3263.886 | 3249.4252 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5049 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009 | 3233.5009
Slow
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Single-axis Tracking Solar PV2 | 1952.049 | 1842.6479 | 1793.3577 | 1722.2742 | 1686.7202 | 1657.5309 | 1634.3361 | 1611.056 | 1590.3195 | 1567.9027 | 1550.1567 | 1516.7979 | 1492.8713 | 1470.8484 | 1452.8618 | 1432.7298 | 1411.2174 | 1401.299 | 1384.2407 | 1375.1875 | 1366.83 | 1359.0879 | 1351.8594 | 1344.8843 | 1338.7026 | 1333.4594 | 1327.6691 | 1322.1893 | 1316.8372 | 1313.095 | 1309.2371 | 1305.1961 | 1302.2358
Solar Thermal Central Receiver (6 hrs storage) | 4434.4078 | 4056.0134 | 3866.802 | 3866.802 | 3866.802 | 3866.802 | 3866.802 | 3866.802 | 3865.3556 | 3785.9445 | 3733.0907 | 3669.863 | 3635.1994 | 3614.3382 | 3612.0926 | 3563.5984 | 3528.5725 | 3502.1104 | 3481.4315 | 3464.8413 | 3451.2486 | 3439.9189 | 3430.3393 | 3422.1413 | 3415.0529 | 3408.8691 | 3403.4327 | 3384.2627 | 3366.6607 | 3350.9026 | 3336.7279 | 3323.9227 | 3312.3101
Wind | 1945.0567 | 1942.7359 | 1939.4936 | 1934.9191 | 1933.0785 | 1926.8172 | 1923.1646 | 1922.3636 | 1922.0762 | 1922.0335 | 1921.987 | 1921.9127 | 1910.5066 | 1898.8141 | 1891.1053 | 1884.8489 | 1879.9648 | 1870.7429 | 1855.5208 | 1850.0015 | 1845.0318 | 1840.7033 | 1836.6524 | 1827.9128 | 1826.1177 | 1824.6281 | 1823.3935 | 1822.3409 | 1820.7105 | 1818.2042 | 1814.9256 | 1812.1282 | 1809.8185
Large Scale Battery Storage (2hrs storage) | 1480.1775 | 1396.6564 | 1344.2841 | 1323.4715 | 1311.8012 | 1300.4494 | 1289.7691 | 1279.1963 | 1268.7377 | 1258.4802 | 1244.1403 | 1233.5809 | 1223.5946 | 1214.2425 | 1204.5919 | 1195.1753 | 1185.845 | 1176.6615 | 1168.2651 | 1160.2657 | 1152.5727 | 1145.2165 | 1138.0276 | 1131.0418 | 1124.1638 | 1117.2383 | 1110.6504 | 1104.2383 | 1098.01 | 1091.8804 | 1085.892 | 1080.03 | 1074.2882
Rapid
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Solar Thermal Central Receiver (6 hrs storage) | 4434.4078 | 3299.2247 | 2731.5905 | 2731.5905 | 2731.5905 | 2731.5905 | 2731.5905 | 2731.5905 | 2727.2513 | 2489.018 | 2330.4565 | 2140.7733 | 2036.7826 | 1974.199 | 1967.4621 | 1821.9797 | 1716.9018 | 1637.5156 | 1575.4788 | 1525.7083 | 1484.9303 | 1450.941 | 1422.2023 | 1397.6082 | 1376.343 | 1357.7918 | 1341.4826 | 1283.9724 | 1231.1664 | 1183.8922 | 1141.368 | 1102.9525 | 1068.1148
Pumped Hydro (6hrs storage) | 1386.112 | 1375.7162 | 1365.3723 | 1355.0802 | 1344.8395 | 1334.65 | 1324.5115 | 1314.4236 | 1304.3862 | 1294.399 | 1284.4617 | 1274.5742 | 1264.736 | 1254.947 | 1245.207 | 1235.5157 | 1225.8729 | 1216.2782 | 1206.7315 | 1197.2326 | 1187.7812 | 1178.377 | 1169.0198 | 1159.7094 | 1150.4456 | 1141.2281 | 1132.0567 | 1122.9311 | 1113.8512 | 1104.8166 | 1095.8273 | 1086.8829 | 1077.9832
Large Scale Battery Storage (2hrs storage) | 1480.1775 | 1229.6142 | 1072.4974 | 1010.0595 | 975.0485 | 940.9932 | 908.9522 | 877.2338 | 845.8582 | 815.0855 | 772.066 | 740.3876 | 710.4288 | 682.3726 | 653.4207 | 625.171 | 597.1801 | 569.6296 | 544.4403 | 520.4421 | 497.3631 | 475.2946 | 453.7277 | 432.7703 | 412.1365 | 391.3599 | 371.5963 | 352.3599 | 333.6751 | 315.2863 | 297.321 | 279.7349 | 262.5095

## Connection cost
Initial connection costs ($/kW) real 2017 dollars
Build costs are adjusted according to NEM planning zone to account for proximity to transmission assets
Final connection costs will be subject to modelling outcomes
Renewable Energy Zone | Wind | Solar | Biomass | Batteries | Pumped hydro | NEM Zone | Gas
Broken Hill | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | NQ | 83.3081
Central NSW Tablelands | 91.333 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | CQ | 83.3081
Central West NSW | 91.333 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | SWQ | 81.9458
Murray River | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | SEQ | 83.3081
North West NSW | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | NNS | 77.8739
Northern NSW Tablelands | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | NCEN | 75.5489
Riverland | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | CAN | 74.1584
Southern NSW Tablelands | 101.4811 | 81.1849 | 81.1849 | 101.4811 | 101.4811 | SWNSW | 77.8739
Barcaldine | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | NVIC | 67.0372
Darling Downs | 96.7043 | 71.7026 | 81.1849 | 101.4811 | 101.4811 | LV | 65.6392
Fitzroy | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | MEL | 81.9458
Isaac | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | CVIC | 81.9458
North Qld Clean Energy Hub | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | NSA | 71.0368
Northern Qld | 101.4811 | 101.4811 | 81.1849 | 101.4811 | 101.4811 | ADE | 71.0368
Eastern Eyre Peninsula | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811 | SESA | 192.8142
Leigh Creek | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811 | TAS | 91.333
Mid-North SA | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811
Northern SA | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811
Roxby Downs | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811
South East SA | 172.5179 | 172.5179 | 81.1849 | 101.4811 | 101.4811 | NEM Region | Gas | Shadow NEM zone for Gas | Black Coal (HELE)
Western Eyre Peninsula | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811
Yorke Peninsula | 131.9255 | 81.1849 | 81.1849 | 101.4811 | 101.4811 | TAS | 91.333 | TAS
King island | 121.7774 | 121.7774 | 81.1849 | 101.4811 | 101.4811 | QLD | 83.3081 | NQ/CQ/SEQ | 136.34
North East Tasmania | 121.7774 | 121.7774 | 81.1849 | 101.4811 | 101.4811 | SA | 71.0368 | NSA/ADE | 136.34
North West Tasmania | 121.7774 | 121.7774 | 81.1849 | 101.4811 | 101.4811 | NSW | 77.8739 | NNS/SWNSW | 136.34
Tasmania Midlands | 121.7774 | 121.7774 | 81.1849 | 101.4811 | 101.4811 | VIC | 65.6392 | LV
Gippsland | 121.7774 | 121.7774 | 81.1849 | 101.4811 | 101.4811
Moyne | 111.6293 | 91.333 | 81.1849 | 101.4811 | 101.4811 | 1. Regional connection costs for gas are derived from shadow NEM zone connection cost.
Western Victoria | 111.6293 | 91.333 | 81.1849 | 101.4811 | 101.4811

## Build limits
Initial Build limits (MW)
Potential in each zone to build new renewable energy capacity
This will be moderated by transmission expansion choices in each scenario, loss factor impacts, etc
| Region | NTNDP zone | Wind bubble 2010-2016 | Wind |  | Solar1 | Transmission-limited total build2 | Indicative transmission expansion cost ($M/MW)3 | Opening of indicative additional generation capacity in REZs along the interconnector routes
|  |  |  | High | Medium |  |  |  | QNI-Option 4 | QNI-Option 6 | VNI Option 4 | VNI Option 5 | VNI Option 6 | VNI Option 7 | VNI Option 8 | Riverlink option | VIC-TAS Second IC | VIC-TAS second and third ICs
Far North QLD | QLD | NQ | FNQ |  |  | 0 | 700 | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North QLD Clean Energy Hub | QLD | NQ | FNQ | 2320 | 6955 | 4000 | 0 | 1.2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northern QLD | QLD | NQ | FNQ |  |  | 1750 | 2500 | 0.86667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barcaldine | QLD | CQ | CQ | 475 | 1435 | 4000 | 0 | 0.92857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Isaac | QLD | NQ | NQ | 465 | 1395 | 3500 | 2800 | 0.66667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fitzroy | QLD | CQ | CQ | 220 | 670 | 2000 | 3000 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Darling Downs | QLD | SWQ | SWQ | 695 | 2090 | 4000 | 3000 | 0.16667 | 1500 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North West New South Wales | NSW | NNS | NEN |  |  | 3250 | 100 | 0.285 | 1000 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northern NSW Tablelands | NSW | NNS | NEN | 900 | 2760 | 1750 | 300 | 0.285 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Central NSW Tablelands | NSW | NCEN | HUN | 400 | 1200 | 3000 | 1000 | 0.285 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Central West NSW | NSW | NCEN | WEN | 355 | 1065 | 3750 | 100 | 0.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Southern NSW Tablelands | NSW | CAN | MRN | 575 | 1735 | 1000 | 1000 | 0.224 | 0 | 0 | 500 | 500 | 2000 | 2000 | 3500 | 0 | 0 | 0
Tumut | NSW | CAN | - |  |  | 0 | 0 | 0.224 | 0 | 0 | [5 empty] | 0 | 0 | 0
Murray River (NSW) | NSW | SWNSW | MUN | 1055 | 3140 | 6000 | 0 | 0.52 | 0 | 0 | 0 | 0 | 0 |  |  | 1200 | 0 | 0
Murray River (VIC) | VIC | CVIC | MUN |  |  |  | 300 | 0.376 | 0 | 0 | 0 | 0 | 2000 | 2000 | 1000 |  | 0 | 0
Riverland (NSW) | NSW | SWNSW | FWN | 155 | 465 | 2000 | 200 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Riverland (SA) | SA | NSA | MNS |  |  |  | 250 | 0.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Broken Hill | NSW | SWNSW | FWN | 620 | 1870 | 4000 | 100 | 0.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New England | NSW | NNS | - |  |  | 0 | 300 | 0.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooma-Monaro | NSW | CAN | - |  |  | 0 | 200 | 0.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Western Victoria | VIC | CVIC | NWV | 395 | 1185 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 2000 | 2000 | 0 | 0 | 0
Moyne | VIC | MEL | SWV | 570 | 1725 | 0 | 2000 | 0.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gippsland | VIC | LV | SEV | 35 | 105 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ovens Murray | VIC | NVIC | - |  |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
South East SA | SA | SESA | CS | 455 | 1355 | 0 | 500 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mid-North SA | SA | ADE | MNS | 605 | 1820 | 0 | 1000 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yorke Peninsula | SA | NSA | YPS | 155 | 465 | 0 | 50 | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northern SA | SA | NSA | MNS |  |  | 1500 | 1000 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leigh Creek | SA | NSA | MNS | 295 | 895 | 3250 | 10 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roxby Downs | SA | NSA | - |  |  | 1700 | 960 | 0.29324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eastern Eyre Peninsula | SA | NSA | EPS | 290 | 870 | 2500 | 500 | 0.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Western Eyre Peninsula | SA | NSA | WCS | 175 | 540 | 2000 | 0 | 0.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
King Island | TAS | TAS | NWT | 150 | 450 | 0 | 0 | 1.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North East Tasmania | TAS | TAS | NET | 75 | 230 | 0 | 0 | 0.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North West Tasmania | TAS | TAS | NWT | 500 | 1500 | 0 | 200 | 0.2242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1000
Tasmania Midlands | TAS | TAS | ST | 430 | 1300 | 0 | 1000 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000
1. Solar build limit determined by an assumed 0.25% of the approximate land area of the Renewable Energy Zones, allowing for typical land area requirements for solar PV, up to 4,000MW per REZ.
2. Intraregional transmission augmentations may be selected by the model if economic to access larger new renewable resource locations
3. Indicative transmission cost represents indicative network expansion to connect the REZ to the nearest major load centre.

## Lead Time
Lead time
Amount of time from start of simulation before specific technologies can be first built
Technology | Lead time (years)
Batteries | 1
Solar PV | 1
Wind | 1
OCGT | 2
CCGT | 4
Pumped hydro | 6
Black Coal (HELE) | 8
Biomass | 1
Solar Thermal Central Receiver (6 hrs storage) | 1

## WACC
Weighted average cost of capital (WACC)
WACC expresses the costs incurred to obtain finance for capital expenditure
WACC is assumed to return to typical historical values, corresponding to reduction of debt and increase in equity. Estimate is intentionally conservative, corresponding to a marginally optimistic capital investment cost, faster change in mix and higher need for responsiveness from the market. Value represents real, pre tax WACC.
Asset class | WACC
All new generation and transmission | 6%

## Storage properties
Battery properties
Property | Value
Maximum power1 | 1 | MW
Energy capacity | 2 | MWh
Charge efficiency (household) | 90%
Charge efficiency (utility) | 80%
Technical life | 15 | years
1. Power and capacity are defined as a 1:2 ratio. The model is free to build utility-scale batteries up to defined build limits
Pumped hydro properties
Property | Value
Maximum power | 100 | MW
Energy capacity | 6 | hours
Pump efficiency | 80%
Economic life | 50 | years
For those scenarios which explore specific large scale storage projects:
Snowy 2.0 properties
Property | Value
Maximum power / Maximum pump load | 2000 / 2000 | MW
Storage capacity | 168 | hours
Pump efficiency | 80%
Economic life | 50 | years
Transmission connection | Includes 500kV development from Snowy 2.0/Wagga to Bannaby and 330kV connection of Snowy 2.0
Battery of the Nation properties
Property | Value
Maximum power / Maximum pump load | 1500 / 1500 | MW
Storage capacity | 24 | hours
Pump efficiency | 80%
Economic life | 50 | years
Transmission connection | Includes commitment of 700MW bi-directional Basslink augmentation. Model decision as to whether to expand Basslink capacity beyond a second link

## Coal and Biomass price
Coal price ($/GJ, real 2017 dollars)
Generator | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bayswater | 1.5 | 1.54 | 1.63 | 1.63 | 1.65 | 1.7 | 1.75 | 1.82 | 1.82 | 2 | 2.4 | 2.66 | 2.79 | 2.89 | 2.93 | 2.98 | 3.03 | 3.1 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
Eraring | 2.34 | 2.49 | 2.67 | 2.84 | 2.9 | 2.95 | 3.03 | 3.18 | 3.31 | 3.34 | 3.44 | 3.56 | 3.69 | 3.78 | 3.84 | 3.9 | 3.97 | 4.06 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11
Liddell | 1.5 | 1.54 | 1.63 | 1.63 | 1.65 | 1.7 | 1.75 | 1.82 | 1.82 | 2 | 2.4 | 2.66 | 2.79 | 2.89 | 2.93 | 2.98 | 3.03 | 3.1 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14 | 3.14
Mount Piper | 2.03 | 2.12 | 2.28 | 2.4 | 2.45 | 2.51 | 2.57 | 2.71 | 2.82 | 2.9 | 3.05 | 3.17 | 3.31 | 3.43 | 3.48 | 3.52 | 3.57 | 3.65 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
Vales Point | 2.25 | 2.39 | 2.57 | 2.74 | 2.8 | 2.95 | 3.03 | 3.18 | 3.31 | 3.34 | 3.44 | 3.56 | 3.69 | 3.78 | 3.84 | 3.9 | 3.97 | 4.06 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11 | 4.11
Callide B | 2.04 | 2.04 | 2.08 | 2.12 | 2.16 | 2.18 | 2.2 | 2.22 | 2.27 | 2.3 | 2.31 | 2.34 | 2.37 | 2.42 | 2.67 | 2.9 | 2.96 | 3.04 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
Callide Power Plant | 2.04 | 2.04 | 2.08 | 2.12 | 2.16 | 2.18 | 2.2 | 2.22 | 2.27 | 2.3 | 2.31 | 2.34 | 2.37 | 2.42 | 2.67 | 2.9 | 2.96 | 3.04 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07
Gladstone | 2.26 | 2.44 | 2.67 | 2.81 | 2.86 | 2.93 | 3 | 3.15 | 3.27 | 3.3 | 3.36 | 3.46 | 3.61 | 3.7 | 3.75 | 3.81 | 3.88 | 3.97 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02
Kogan Creek | 1.54 | 1.55 | 1.56 | 1.56 | 1.56 | 1.58 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
Millmerran | 1.28 | 1.28 | 1.28 | 1.29 | 1.29 | 1.3 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.33 | 1.34 | 1.34 | 1.34
Stanwell | 2.18 | 2.28 | 2.36 | 2.42 | 2.45 | 2.47 | 2.49 | 2.51 | 2.53 | 2.68 | 3.05 | 3.33 | 3.47 | 3.6 | 3.65 | 3.7 | 3.76 | 3.86 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
Tarong | 2.79 | 2.79 | 2.8 | 2.81 | 2.81 | 2.83 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85
Tarong North | 2.79 | 2.79 | 2.8 | 2.81 | 2.81 | 2.83 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85
Loy Yang A | 0.62 | 0.62 | 0.65 | 0.65 | 0.65 | 0.65 | 0.66 | 0.66 | 0.66 | 0.66 | 0.67 | 0.67 | 0.67 | 0.68 | 0.68 | 0.69 | 0.69 | 0.7 | 0.7 | 0.71 | 0.71 | 0.72 | 0.73 | 0.73
Loy Yang B | 0.62 | 0.62 | 0.65 | 0.65 | 0.65 | 0.65 | 0.66 | 0.66 | 0.66 | 0.66 | 0.67 | 0.67 | 0.67 | 0.68 | 0.68 | 0.69 | 0.69 | 0.7 | 0.7 | 0.71 | 0.71 | 0.72 | 0.73 | 0.73
Yallourn | 0.62 | 0.62 | 0.63 | 0.64 | 0.64 | 0.65 | 0.65 | 0.65 | 0.65 | 0.66 | 0.66 | 0.66 | 0.67 | 0.67 | 0.67 | 0.68 | 0.68 | 0.69 | 0.69 | 0.7 | 0.7 | 0.71 | 0.72 | 0.72
New entrant coal | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Lower estimate | 2.79 | 2.79 | 2.8 | 2.81 | 2.81 | 2.83 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85 | 2.85
Central estimate | 4.8606 | 4.7543 | 4.0637 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716 | 3.7716
*Lower estimate equivalent to estimated contract price paid by existing generators in QLD
*Central estimate equivalent to forecast export coal price, as per June 2018 Resources and Energy Quarterly report, converted to AU$/GJ - @6000kCal/kg, 1USD=0.75AUD).
Biomass price | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Biomass | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5

## Gas and Liquid fuel price
Gas price ($/GJ, real 2017 dollars)
Prices are the sum of wholesale price and transportation cost.
The below prices are a guide only. The outputs from AEMO's integrated gas and electricity model will be used for GPG fuel costs, ensuring maximum internal consistency between gas and electricity markets.
Neutral
Generator | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bairnsdale | 9.5096 | 10.0096 | 10.5096 | 11.0096 | 10.5096 | 10.2814 | 10.0531 | 9.8249 | 9.5966 | 9.5966 | 9.5966 | 9.5966 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762
Barcaldine | 9.6916 | 9.6916 | 9.6916 | 9.6916 | 9.6916 | 9.3562 | 9.0208 | 8.6854 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35 | 8.35
Barker Inlet | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.2146 | 8.9293 | 8.6439 | 8.3585 | 8.3821 | 9.1658 | 9.1658 | 9.1655 | 9.1658 | 9.1658 | 9.1657 | 9.1657 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656
Bell Bay Three | 10 | 10 | 10 | 10 | 10 | 10.2012 | 10.4024 | 10.6036 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048
Braemar | 9.0988 | 9.0988 | 9.0988 | 9.0988 | 9.0988 | 8.9385 | 8.7782 | 8.618 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577
Braemar 2 | 9.0988 | 9.0988 | 9.0988 | 9.0988 | 9.0988 | 8.9385 | 8.7782 | 8.618 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577
Colongra | 10.0133 | 10.0133 | 10.0133 | 10.0133 | 10.0133 | 9.8137 | 9.614 | 9.4144 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148
Condamine | 9.0988 | 9.0988 | 9.0988 | 9.0988 | 9.0988 | 8.9385 | 8.7782 | 8.618 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577
Darling Downs | 9.7077 | 9.7077 | 9.7077 | 9.7077 | 9.7077 | 9.1414 | 8.5751 | 8.0088 | 7.4425 | 7.4425 | 7.4425 | 7.4425 | 7.4425 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577
Dry Creek | 10.6378 | 10.6378 | 10.6378 | 10.6378 | 10.6378 | 10.2656 | 9.8933 | 9.5211 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489
Hallett | 9.682 | 9.682 | 9.682 | 9.682 | 9.682 | 9.5562 | 9.4304 | 9.3047 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789
Jeeralang | 9.6691 | 10.1691 | 10.6691 | 11.1691 | 10.6691 | 10.401 | 10.1328 | 9.8647 | 9.5966 | 9.5966 | 9.5966 | 9.5966 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762
Ladbroke Grove | 9.5667 | 9.5667 | 9.5667 | 9.5667 | 9.5667 | 9.2126 | 8.8584 | 8.5043 | 8.1501 | 8.1503 | 8.1506 | 8.1506 | 8.1503 | 9.1658 | 9.1658 | 9.1657 | 9.1657 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656
Laverton North | 9.5074 | 10.0074 | 10.5074 | 11.0074 | 10.5074 | 10.2793 | 10.0511 | 9.823 | 9.5949 | 9.5949 | 9.5949 | 9.5949 | 9.6744 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745
Mintaro | 10.6646 | 10.6646 | 10.6646 | 10.6646 | 10.6646 | 10.2932 | 9.9218 | 9.5503 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789 | 9.1789
Mortlake OCGT | 9.8486 | 10.3486 | 10.8486 | 11.3486 | 10.8486 | 10.503 | 10.1573 | 9.8117 | 9.4661 | 9.4661 | 9.4661 | 9.4661 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456 | 9.5456
Newport | 9.6669 | 10.1669 | 10.6669 | 11.1669 | 10.6669 | 10.3989 | 10.1309 | 9.8629 | 9.5949 | 9.5949 | 9.5949 | 9.5949 | 9.6744 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745
Oakey | 9.641 | 9.641 | 9.641 | 9.641 | 9.641 | 9.1435 | 8.6459 | 8.1484 | 7.6509 | 7.6743 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577
Osborne | 9.5667 | 9.5667 | 9.5667 | 9.5667 | 9.5667 | 9.2126 | 8.8584 | 8.5043 | 8.1501 | 8.1503 | 8.1506 | 8.1506 | 8.1503 | 9.1658 | 9.1658 | 9.1657 | 9.1657 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656
Pelican Point | 10.6378 | 10.6378 | 10.6378 | 10.6378 | 10.6378 | 10.2656 | 9.8933 | 9.5211 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489 | 9.1489
Quarantine | 9.5667 | 9.5667 | 9.5667 | 9.5667 | 9.5667 | 9.2126 | 8.8584 | 8.5043 | 8.1501 | 8.1503 | 8.1506 | 8.1506 | 8.1503 | 9.1658 | 9.1658 | 9.1657 | 9.1657 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656
Roma | 9 | 9 | 9 | 9 | 9 | 8.4337 | 7.8674 | 7.3011 | 6.7348 | 6.7348 | 6.7348 | 6.7348 | 6.7348 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75 | 7.75
Smithfield | 10.0133 | 10.0088 | 10.0088 | 10.0088 | 10.0088 | 9.7219 | 9.435 | 9.1481 | 8.8611 | 8.8614 | 8.863 | 8.8629 | 8.8624 | 9.1996 | 9.1997 | 9.1997 | 9.1998 | 9.1999 | 9.1999 | 9.1999 | 9.1999 | 9.1999 | 9.19 | 9.19
Somerton | 9.5 | 10 | 10.5 | 11 | 10.5 | 10.072 | 9.644 | 9.216 | 8.7881 | 8.8114 | 9.5949 | 9.5949 | 9.6744 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745 | 9.6745
Swanbank E | 9 | 9 | 9 | 9 | 9 | 8.8644 | 8.7288 | 8.5933 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577 | 8.4577
Tallawarra | 10.0133 | 10.0133 | 10.0133 | 10.0133 | 10.0133 | 9.8137 | 9.614 | 9.4144 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148 | 9.2148
Tamar Valley | 10 | 10 | 10 | 10 | 10 | 10.2012 | 10.4024 | 10.6036 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048
Torrens Island | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.2146 | 8.9293 | 8.6439 | 8.3585 | 8.3821 | 9.1658 | 9.1658 | 9.1655 | 9.1658 | 9.1658 | 9.1657 | 9.1657 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656 | 9.1656
Townsville | 9.9847 | 9.9847 | 9.9847 | 9.9847 | 9.9847 | 8.9015 | 7.8183 | 6.7351 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 8.394 | 8.394 | 8.394 | 8.394 | 8.394 | 8.394
Uranquinty | 10 | 10 | 10 | 10 | 10 | 9.5384 | 9.0769 | 8.6153 | 8.1538 | 8.1546 | 8.1594 | 8.1592 | 8.1576 | 9.1693 | 9.1695 | 9.1696 | 9.1697 | 9.1701 | 9.1701 | 9.1701 | 9.1701 | 9.1701 | 9.1403 | 9.1403
Valley Power | 9.5096 | 10.0096 | 10.5096 | 11.0096 | 10.5096 | 10.2814 | 10.0531 | 9.8249 | 9.5966 | 9.5966 | 9.5966 | 9.5966 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762 | 9.6762
Yarwun | 9.2246 | 9.2246 | 9.2246 | 9.2246 | 9.2246 | 8.1414 | 7.0582 | 5.975 | 4.8918 | 4.8918 | 4.8918 | 4.8918 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7
QLD new entrants | 9.3546 | 9.3546 | 9.3546 | 9.3546 | 9.3546 | 9.3546 | 8.8798 | 8.4049 | 7.9301 | 7.4553 | 7.4576 | 7.5359 | 7.5359 | 7.9168 | 8.1198 | 8.1198 | 8.1198 | 8.1198 | 8.1198 | 8.394 | 8.394 | 8.394 | 8.394 | 8.394
NSW new entrants | 10.01 | 10.0088 | 10.0088 | 10.0088 | 10.0088 | 10.0088 | 9.7219 | 9.435 | 9.1481 | 8.8611 | 8.8614 | 8.863 | 8.8629 | 8.8624 | 9.1996 | 9.1997 | 9.1997 | 9.1998 | 9.1999 | 9.1999 | 9.1999 | 9.1999 | 9.1999 | 9.19
VIC new entrants | 9.11 | 9.61 | 10.11 | 10.61 | 11.11 | 10.61 | 10.3272 | 10.0444 | 9.7616 | 9.4788 | 9.4817 | 9.5797 | 9.5797 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592 | 9.6592
SA new entrants | 9.9247 | 9.9247 | 9.9247 | 9.9247 | 9.9247 | 9.9247 | 9.6053 | 9.2859 | 8.9664 | 8.647 | 8.6523 | 8.8266 | 8.8265 | 8.8264 | 9.165 | 9.1649 | 9.1649 | 9.1649 | 9.1649 | 9.1649 | 9.1649 | 9.1649 | 9.1649 | 9.1649
TAS new entrants | 10 | 10 | 10 | 10 | 10 | 10 | 10.2012 | 10.4024 | 10.6036 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048 | 10.8048
Strong
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bairnsdale | 10.5096 | 11.0096 | 11.5096 | 12.0096 | 11.5096 | 11.3119 | 11.1143 | 10.9166 | 10.719 | 10.719 | 10.719 | 10.719 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985
Barcaldine | 10.6916 | 10.6916 | 10.6916 | 10.6916 | 10.6916 | 10.3469 | 10.0021 | 9.6573 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125 | 9.3125
Barker Inlet | 10.5043 | 10.5043 | 10.5043 | 10.5043 | 10.5043 | 10.1711 | 9.8378 | 9.5046 | 9.1713 | 9.2015 | 10.1901 | 10.19 | 10.1898 | 10.19 | 10.19 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899
Bell Bay Three | 11 | 11 | 11 | 11 | 11 | 11.2043 | 11.4086 | 11.613 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173
Braemar | 10.0988 | 10.0988 | 10.0988 | 10.0988 | 10.0988 | 9.9291 | 9.7595 | 9.5898 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202
Braemar 2 | 10.0988 | 10.0988 | 10.0988 | 10.0988 | 10.0988 | 9.9291 | 9.7595 | 9.5898 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202
Colongra | 11.0133 | 11.0133 | 11.0133 | 11.0133 | 11.0133 | 10.812 | 10.6107 | 10.4094 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208
Condamine | 10.0988 | 10.0988 | 10.0988 | 10.0988 | 10.0988 | 9.9291 | 9.7595 | 9.5898 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202
Darling Downs | 10.7077 | 10.7077 | 10.7077 | 10.7077 | 10.7077 | 10.0658 | 9.424 | 8.7821 | 8.1403 | 8.1403 | 8.1403 | 8.1403 | 8.1403 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202
Dry Creek | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4183 | 10.3365 | 10.2548 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731
Hallett | 10.6863 | 10.6863 | 10.6863 | 10.6863 | 10.6863 | 10.5655 | 10.4447 | 10.3239 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031
Jeeralang | 10.669 | 11.169 | 11.669 | 12.169 | 11.669 | 11.4315 | 11.194 | 10.9565 | 10.719 | 10.719 | 10.719 | 10.719 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985
Ladbroke Grove | 10.571 | 10.571 | 10.571 | 10.571 | 10.571 | 10.1557 | 9.7403 | 9.325 | 8.9097 | 8.9098 | 8.9102 | 8.9101 | 8.9099 | 10.19 | 10.19 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899
Laverton North | 10.5074 | 11.0074 | 11.5074 | 12.0074 | 11.5074 | 11.3098 | 11.1123 | 10.9148 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 10.7968 | 10.7968 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969
Mintaro | 10.5269 | 10.5269 | 10.5269 | 10.5269 | 10.5269 | 10.4459 | 10.365 | 10.284 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031 | 10.2031
Mortlake OCGT | 10.8486 | 11.3486 | 11.8486 | 12.3486 | 11.8486 | 11.5335 | 11.2185 | 10.9035 | 10.5885 | 10.5885 | 10.5885 | 10.5885 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668 | 10.668
Newport | 10.6668 | 11.1668 | 11.6668 | 12.1668 | 11.6668 | 11.4294 | 11.192 | 10.9546 | 10.7173 | 10.7173 | 10.7173 | 10.7173 | 10.7968 | 10.7968 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969
Oakey | 10.641 | 10.641 | 10.641 | 10.641 | 10.641 | 10.0813 | 9.5215 | 8.9617 | 8.402 | 8.432 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202
Osborne | 10.571 | 10.571 | 10.571 | 10.571 | 10.571 | 10.1557 | 9.7403 | 9.325 | 8.9097 | 8.9098 | 8.9102 | 8.9101 | 8.9099 | 10.19 | 10.19 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899
Pelican Point | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4183 | 10.3365 | 10.2548 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731 | 10.1731
Quarantine | 10.571 | 10.571 | 10.571 | 10.571 | 10.571 | 10.1557 | 9.7403 | 9.325 | 8.9097 | 8.9098 | 8.9102 | 8.9101 | 8.9099 | 10.19 | 10.19 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899
Roma | 10 | 10 | 10 | 10 | 10 | 9.3581 | 8.7163 | 8.0744 | 7.4326 | 7.4326 | 7.4326 | 7.4326 | 7.4326 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125 | 8.7125
Smithfield | 11.0133 | 11.0088 | 11.0088 | 11.0088 | 11.0088 | 10.6982 | 10.3875 | 10.0768 | 9.7662 | 9.7664 | 9.768 | 9.7679 | 9.7674 | 10.1929 | 10.193 | 10.193 | 10.193 | 10.1932 | 10.1932 | 10.1932 | 10.1932 | 10.1932 | 10.1832 | 10.1832
Somerton | 10.5 | 11 | 11.5 | 12 | 11.5 | 11.0498 | 10.5995 | 10.1493 | 9.699 | 9.729 | 10.7173 | 10.7173 | 10.7968 | 10.7968 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969 | 10.7969
Swanbank E | 10 | 10 | 10 | 10 | 10 | 9.855 | 9.7101 | 9.5651 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202 | 9.4202
Tallawarra | 11.0133 | 11.0133 | 11.0133 | 11.0133 | 11.0133 | 10.812 | 10.6107 | 10.4094 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208 | 10.208
Tamar Valley | 11.5695 | 11.5695 | 11.5695 | 11.5695 | 11.5695 | 11.6315 | 11.6934 | 11.7554 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173
Torrens Island | 10.5043 | 10.5043 | 10.5043 | 10.5043 | 10.5043 | 10.1711 | 9.8378 | 9.5046 | 9.1713 | 9.2015 | 10.1901 | 10.19 | 10.1898 | 10.19 | 10.19 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899 | 10.1899
Townsville | 10.9847 | 10.9847 | 10.9847 | 10.9847 | 10.9847 | 9.6515 | 8.3183 | 6.9851 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 9.3565 | 9.3565 | 9.3565 | 9.3565 | 9.3565 | 9.3565 | 9.3565
Uranquinty | 11 | 11 | 11 | 11 | 11 | 10.4706 | 9.9412 | 9.4118 | 8.8824 | 8.8832 | 8.8879 | 8.8878 | 8.8862 | 10.1626 | 10.1628 | 10.1629 | 10.163 | 10.1634 | 10.1634 | 10.1634 | 10.1634 | 10.1634 | 10.1336 | 10.1336
Valley Power | 10.5096 | 11.0096 | 11.5096 | 12.0096 | 11.5096 | 11.3119 | 11.1143 | 10.9166 | 10.719 | 10.719 | 10.719 | 10.719 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985 | 10.7985
Yarwun | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 10.2246 | 8.8914 | 7.5582 | 6.225 | 4.8918 | 4.8918 | 4.8918 | 4.8918 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625 | 9.6625
QLD new entrants | 10.3546 | 10.3546 | 10.3546 | 10.3546 | 10.3546 | 10.3546 | 9.8037 | 9.2529 | 8.702 | 8.1512 | 8.1542 | 8.253 | 8.253 | 8.7301 | 8.9861 | 8.9861 | 8.9861 | 8.9861 | 9.3565 | 9.3565 | 9.3565 | 9.3565 | 9.3565 | 9.3565
NSW new entrants | 11.01 | 11.0088 | 11.0088 | 11.0088 | 11.0088 | 11.0088 | 10.6982 | 10.3875 | 10.0768 | 9.7662 | 9.7664 | 9.768 | 9.7679 | 9.7674 | 10.1929 | 10.193 | 10.193 | 10.193 | 10.1932 | 10.1932 | 10.1932 | 10.1932 | 10.1932 | 10.1832
VIC new entrants | 10.11 | 10.61 | 11.11 | 11.61 | 12.11 | 11.61 | 11.3512 | 11.0924 | 10.8336 | 10.5747 | 10.5785 | 10.702 | 10.702 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816 | 10.7816
SA new entrants | 10.5483 | 10.5483 | 10.5483 | 10.5483 | 10.5483 | 10.5483 | 10.2952 | 10.0422 | 9.7891 | 9.536 | 9.5428 | 9.7625 | 9.7625 | 9.7624 | 10.1892 | 10.1891 | 10.1891 | 10.1891 | 10.1891 | 10.1891 | 10.1891 | 10.1891 | 10.1891 | 10.1891
TAS new entrants | 11.2848 | 11.2848 | 11.2848 | 11.2848 | 11.2848 | 11.2848 | 11.4179 | 11.551 | 11.6842 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173 | 11.8173
Weak
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bairnsdale | 8.5022 | 9.0022 | 9.5022 | 10.0022 | 9.5022 | 9.214 | 8.9257 | 8.6375 | 8.3492 | 8.3492 | 8.3492 | 8.3492 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288
Barcaldine | 8.4671 | 8.4671 | 8.4671 | 8.4671 | 8.4671 | 8.1659 | 7.8648 | 7.5636 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625 | 7.2625
Barker Inlet | 8.5788 | 8.5788 | 8.5788 | 8.5788 | 8.5788 | 8.4356 | 8.2924 | 8.1492 | 8.006 | 8.0112 | 8.0166 | 8.0166 | 8.0163 | 8.0166 | 8.0165 | 8.0165 | 8.0165 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164
Bell Bay Three | 9 | 9 | 9 | 9 | 9 | 9.1668 | 9.3336 | 9.5005 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673
Braemar | 8.9933 | 8.9933 | 8.9933 | 8.9933 | 8.9933 | 8.5875 | 8.1818 | 7.776 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702
Braemar 2 | 8.9933 | 8.9933 | 8.9933 | 8.9933 | 8.9933 | 8.5875 | 8.1818 | 7.776 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702
Colongra | 9 | 9 | 9 | 9 | 9 | 8.7741 | 8.5483 | 8.3224 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965
Condamine | 8.9933 | 8.9933 | 8.9933 | 8.9933 | 8.9933 | 8.5875 | 8.1818 | 7.776 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702
Darling Downs | 8.7604 | 8.7604 | 8.7604 | 8.7604 | 8.7604 | 8.4128 | 8.0653 | 7.7177 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702
Dry Creek | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 9.0917 | 8.7277 | 8.3637 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996
Hallett | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.3824 | 8.2648 | 8.1472 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296
Jeeralang | 8.6617 | 9.1617 | 9.6617 | 10.1617 | 9.6617 | 9.3336 | 9.0055 | 8.6773 | 8.3492 | 8.3492 | 8.3492 | 8.3492 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288
Ladbroke Grove | 8.662 | 8.662 | 8.662 | 8.662 | 8.662 | 8.5005 | 8.3391 | 8.1776 | 8.0161 | 8.0163 | 8.0166 | 8.0166 | 8.0163 | 8.0166 | 8.0165 | 8.0165 | 8.0165 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164
Laverton North | 8.5 | 9 | 9.5 | 10 | 9.5 | 9.2119 | 8.9237 | 8.6356 | 8.3475 | 8.3475 | 8.3475 | 8.3475 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271
Mintaro | 9.4826 | 9.4826 | 9.4826 | 9.4826 | 9.4826 | 9.1194 | 8.7561 | 8.3929 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296 | 8.0296
Mortlake OCGT | 8.8412 | 9.3412 | 9.8412 | 10.3412 | 9.8412 | 9.4356 | 9.03 | 8.6243 | 8.2187 | 8.2187 | 8.2187 | 8.2187 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983 | 8.2983
Newport | 8.6595 | 9.1595 | 9.6595 | 10.1595 | 9.6595 | 9.3315 | 9.0035 | 8.6755 | 8.3475 | 8.3475 | 8.3475 | 8.3475 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271
Oakey | 8.6772 | 8.6772 | 8.6772 | 8.6772 | 8.6772 | 8.3479 | 8.0187 | 7.6894 | 7.3601 | 7.3651 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702
Osborne | 8.662 | 8.662 | 8.662 | 8.662 | 8.662 | 8.5005 | 8.3391 | 8.1776 | 8.0161 | 8.0163 | 8.0166 | 8.0166 | 8.0163 | 8.0166 | 8.0165 | 8.0165 | 8.0165 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164
Pelican Point | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 9.0917 | 8.7277 | 8.3637 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996 | 7.9996
Quarantine | 8.662 | 8.662 | 8.662 | 8.662 | 8.662 | 8.5005 | 8.3391 | 8.1776 | 8.0161 | 8.0163 | 8.0166 | 8.0166 | 8.0163 | 8.0166 | 8.0165 | 8.0165 | 8.0165 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164
Roma | 8.0527 | 8.0527 | 8.0527 | 8.0527 | 8.0527 | 7.7051 | 7.3576 | 7.01 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625 | 6.6625
Smithfield | 9.088 | 9.088 | 9.088 | 9.088 | 9.088 | 8.8363 | 8.5846 | 8.333 | 8.0813 | 8.0815 | 8.0831 | 8.0831 | 8.0826 | 8.0814 | 8.0815 | 8.0815 | 8.0815 | 8.0816 | 8.0816 | 8.0816 | 8.0816 | 8.0816 | 8.0717 | 8.0717
Somerton | 8.7534 | 9.2534 | 9.7534 | 10.2534 | 9.7534 | 9.3994 | 9.0454 | 8.6914 | 8.3374 | 8.3424 | 8.3475 | 8.3475 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271 | 8.4271
Swanbank E | 8 | 8 | 8 | 8 | 8 | 7.8425 | 7.6851 | 7.5276 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702 | 7.3702
Tallawarra | 9 | 9 | 9 | 9 | 9 | 8.7741 | 8.5483 | 8.3224 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965 | 8.0965
Tamar Valley | 9 | 9 | 9 | 9 | 9 | 9.1668 | 9.3336 | 9.5005 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673
Torrens Island | 8.5788 | 8.5788 | 8.5788 | 8.5788 | 8.5788 | 8.4356 | 8.2924 | 8.1492 | 8.006 | 8.0112 | 8.0166 | 8.0166 | 8.0163 | 8.0166 | 8.0165 | 8.0165 | 8.0165 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164 | 8.0164
Townsville | 8.7601 | 8.7601 | 8.7601 | 8.7601 | 8.7601 | 7.9831 | 7.206 | 6.429 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 5.6519 | 7.3065 | 7.3065 | 7.3065 | 7.3065 | 7.3065 | 7.3065 | 7.3065
Uranquinty | 9.264 | 9.264 | 9.264 | 9.264 | 9.264 | 8.9607 | 8.6574 | 8.3541 | 8.0508 | 8.0516 | 8.0563 | 8.0561 | 8.0546 | 8.0511 | 8.0513 | 8.0514 | 8.0515 | 8.0519 | 8.0519 | 8.0519 | 8.0519 | 8.0519 | 8.0221 | 8.0221
Valley Power | 8.5022 | 9.0022 | 9.5022 | 10.0022 | 9.5022 | 9.214 | 8.9257 | 8.6375 | 8.3492 | 8.3492 | 8.3492 | 8.3492 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288 | 8.4288
Yarwun | 8 | 8 | 8 | 8 | 8 | 7.223 | 6.4459 | 5.6689 | 4.8918 | 4.8918 | 4.8918 | 4.8918 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125 | 7.6125
QLD new entrants | 8.5697 | 8.5697 | 8.5697 | 8.5697 | 8.5697 | 8.5697 | 8.1443 | 7.7189 | 7.2934 | 6.868 | 6.8685 | 6.869 | 6.869 | 7.1411 | 7.1411 | 7.1411 | 7.1411 | 7.1411 | 7.3065 | 7.3065 | 7.3065 | 7.3065 | 7.3065 | 7.3065
NSW new entrants | 9.066 | 9.088 | 9.088 | 9.088 | 9.088 | 9.088 | 8.8363 | 8.5846 | 8.333 | 8.0813 | 8.0815 | 8.0831 | 8.0831 | 8.0826 | 8.0814 | 8.0815 | 8.0815 | 8.0815 | 8.0816 | 8.0816 | 8.0816 | 8.0816 | 8.0816 | 8.0717
VIC new entrants | 8.1352 | 8.6352 | 9.1352 | 9.6352 | 10.1352 | 9.6352 | 9.3092 | 8.9831 | 8.6571 | 8.331 | 8.3316 | 8.3323 | 8.3323 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118 | 8.4118
SA new entrants | 8.8931 | 8.8931 | 8.8931 | 8.8931 | 8.8931 | 8.8931 | 8.6731 | 8.4531 | 8.2332 | 8.0132 | 8.0144 | 8.0157 | 8.0157 | 8.0156 | 8.0157 | 8.0157 | 8.0157 | 8.0157 | 8.0156 | 8.0156 | 8.0156 | 8.0156 | 8.0156 | 8.0156
TAS new entrants | 9 | 9 | 9 | 9 | 9 | 9 | 9.1668 | 9.3336 | 9.5005 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673 | 9.6673
$6/GJ lower bound sensitivity
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
QLD | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507 | 5.7507
NSW | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626 | 6.2626
VIC | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
SA | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898 | 5.8898
TAS | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189 | 6.4189
Liquid fuel price | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Liquid fuel | 35.1044 | 35.3182 | 35.0145 | 34.5644 | 34.0309 | 33.4955 | 33.0053 | 32.5528 | 32.1326 | 31.7645 | 31.4368 | 31.1066 | 30.7857 | 30.4894 | 30.2211 | 29.9766 | 29.7488 | 29.5326 | 29.3245 | 29.123 | 28.927 | 28.7344 | 28.5453 | 28.1835

## Refurbishment
Refurbishment
Unit refurbishment is staggered within a power station, one unit at a time at six month intervals. In a power station with 4 units, for example, the fourth unit is not refurbished until 18 months after the given date.
Refurbishment timing
Generator | First refurbishment | Second refurbishment
Bayswater | 2025
Eraring | 2024
Mount Piper | 2023 | 2033
Vales Point | 2022
Callide B | 2028
Callide Power Plant | 2031 | 2041
Kogan Creek | 2037 | 2047
Millmerran | 2032 | 2042
Stanwell | 2026 | 2036
Tarong | 2026
Tarong North | 2033 | 2043
Loy Yang A | 2028 | 2038
Loy Yang B | 2026 | 2036
Yallourn | 2022 | 2032
Refurbishment cost
Generator class | Refurbishment cost ($/MW)1
Black coal | 152545
Brown coal | 249353
Steam Turbine Gas | 101696.6667
1. Costs are applied as an additional fixed cost for the duration of the refurbishment event.

## Retirement
Retirement
Announced and end-of-technical-life retirement. End of life retirements are determined according to equipment age. Units may be retired earlier by the model if determined as least cost to the power system.
Generator | Financial year beginning | Generator | Retirement/Rehabilitation Cost (real 2017 $/MW)
Announced retirement |  | Black Coal | 52439.9
Mackay GT1 | 2021 | Brown Coal | 83903.84
Liddell1 | 2022 | OCGT | 5243.99
Bayswater2 | 2035 | CCGT | 10487.98
Loy Yang A2 | 2048 | Pumped hydro | 104879.8
1. Data source: AEMO generation information page |  | Wind | 10487.98
2. Data source: AGL announcement |  | Single-axis tracking solar | 20975.96
https://www.agl.com.au/about-agl/sustainability/rehabilitation
End of technical life
Bayswater | 2035
Eraring | 2034
Mount Piper | 2043
Vales Point | 2028
Callide B | 2038
Callide Power Plant | 2051
Gladstone | 2029
Kogan Creek | 2057
Millmerran | 2052
Stanwell | 2046
Tarong | 2036
Tarong North | 2053
Loy Yang B | 2056
Yallourn1 | 2032
Newport | 2031
Torrens Island A | 2021
1. Assumed retirement upon conclusion of current mine coal supply agreement

## Heat rates
Heat rates
Encapsulates the efficiency of thermal generators (as-generated, HHV)
Existing generators |  | Generic new entrant units
Generator | Heat rate (GJ/MWh) |  | Heat rates (GJ/MWh)
Bayswater | 9.46 | OCGT | 10.15
Eraring | 9.549 | CCGT | 6.93
Liddell | 10.144 | Biomass | 12.66
Mount Piper | 9.266 | Black Coal (HELE) | 8.664
Vales Point | 9.685
Callide B | 9.149
Callide Power Plant | 9.305
Gladstone | 9.47
Kogan Creek | 8.807
Millmerran | 9.204
Stanwell | 9.073
Tarong | 9.208
Tarong North | 8.664
Loy Yang A | 12.142
Loy Yang B | 12.531
Yallourn | 13.926
Colongra | 11.139
Smithfield | 8.362
Tallawarra | 6.99
Uranquinty | 11.139
Barcaldine | 12.73
Braemar | 11.881
Condamine | 7.282
Darling Downs | 7.383
Oakey | 10.934
Roma | 11.881
Swanbank E | 7.436
Yabulu (Townsville) | 7.598
Yarwun | 10.381
Somerton | 14.851
Bairnsdale | 10.483
Jeeralang A | 15.263
Jeeralang B | 15.263
Laverton North | 11.497
Mortlake | 11.139
Newport | 10.296
Valley Power | 14.851
Hallett GT | 14.851
Barker Inlet | 7.411
Dry Creek | 13.709
Ladbroke Grove | 11.881
Mintaro | 12.73
Osborne | 8.163
Pelican Point | 7.353
Quarantine | 10.714
Torrens Island A | 11.429
Torrens Island B | 10.714
Bell Bay Three | 12.052
Tamar Valley CCGT | 7.282
Tamar Valley OCGT | 12.73
Hunter Valley GT | 12.73
Mackay GT | 12.73
Mount Stuart | 11.881
Angaston | 13
Lonsdale | 13
Port Lincoln | 12.821
Port Lincoln 3 | 12.821
Port Stanvac | 13
Snuggery | 13.443
Tailem Bend | 13

## Auxiliary
Auxiliary load
Auxiliary load is also called "parasitic load" or "self load" and refers to energy generated for use within power stations
Existing generators |  | New entrants
Generator | % auxiliary load | Generator | % auxiliary load
Bayswater | 6 | Wind | 1
Eraring | 6 | Solar PV | 1
Liddell | 5 | CCGT | 3
Mount Piper | 5 | OCGT | 1
Vales Point | 5 | Reciprocating engine | 3
Callide B | 9 | Biomass | 8
Callide Power Plant | 6 | Pumped Hydro | 1
Gladstone | 8 | Black Coal (HELE) | 6
Kogan Creek | 9 | Solar Thermal Central Receiver (6 hrs storage) | 1
Millmerran | 6
Stanwell | 9
Tarong | 8
Tarong North | 6
Loy Yang A | 9
Loy Yang B | 8
Yallourn | 10
Colongra | 1
Smithfield | 5
Tallawarra | 3
Uranquinty | 1
Barcaldine | 1
Braemar | 1
Condamine | 3
Darling Downs | 6
Oakey | 1
Roma | 1
Swanbank E | 3
Yabulu (Townsville) | 3
Yarwun | 2
Somerton | 1
Bairnsdale | 1
Jeeralang A | 3
Jeeralang B | 3
Laverton North | 3
Mortlake | 1
Newport | 5
Valley Power | 1
Hallett GT | 1
Dry Creek | 1
Ladbroke Grove | 1
Mintaro | 1
Osborne | 5
Pelican Point | 2
Quarantine | 5
Torrens Island A | 5
Torrens Island B | 5
Bell Bay Three | 3
Tamar Valley | 1
Hunter Valley GT | 1
Mackay GT | 1
Mount Stuart | 1
Angaston | 2.5
Lonsdale | 2.5
Port Lincoln | 8
Port Lincoln 3 | 8
Port Stanvac | 2.5
Snuggery | 3
All hydro | 1
All wind | 1
All solar | 1

## Fixed OPEX
Fixed operating cost (real 2017 dollars)
Costs that are incurred regardless of energy generated. Scaled by 2.7% from 2015 values to account for CPI increase.
Existing and Committed generators |  | New entrant technologies
Generator | Fixed OPEX ($/kW/year) | Generator | Fixed OPEX ($/kW/year)
Bayswater | 54.8635 | Wind | 47.2
Eraring | 54.8635 | Solar PV | 30.44
Liddell | 58.2539 | OCGT | 4.06
Mount Piper | 54.8635 | CCGT | 10.15
Vales Point | 54.8635 | Pumped hydro | 5
Callide B | 55.48 | Biomass | 126.85
Callide Power Plant | 55.48 | Solar Thermal w/ 6hr Storage | 75.6
Gladstone | 58.2539 | Reciprocating engine | 15.12
Kogan Creek | 56.0039 | Black Coal (HELE) | 53.7334
Millmerran | 53.7334 | Large Scale Battery Storage (2hrs storage) | 0
Stanwell | 54.8635
Tarong | 55.48
Tarong North | 53.7334
Loy Yang A | 145.5835
Loy Yang B | 115.0695
Yallourn | 151.2342
Colongra | 14.5892
Smithfield | 10.2741
Tallawarra | 10.2741
Uranquinty | 14.5892
Barcaldine | 14.5892
Braemar | 14.5892
Condamine | 10.2741
Darling Downs | 10.2741
Oakey | 14.5892
Roma | 14.5892
Swanbank E | 10.2741
Yabulu (Townsville) | 10.2741
Yarwun | 10.2741
Somerton | 14.5892
Bairnsdale | 14.5892
Jeeralang A | 14.5892
Jeeralang B | 14.5892
Laverton North | 14.5892
Mortlake | 14.5892
Newport | 44.7949
Valley Power | 14.5892
Hallett GT | 14.5892
Dry Creek | 14.5892
Ladbroke Grove | 14.5892
Mintaro | 14.5892
Osborne | 10.2741
Pelican Point | 10.2741
Quarantine | 14.5892
Torrens Island A | 43.6648
Torrens Island B | 43.6648
Bell Bay Three | 14.5892
Tamar Valley | 14.5892
Hunter Valley GT | 14.5892
Mackay GT | 14.5892
Mount Stuart | 14.5892
Angaston | 15.1234
Lonsdale | 14.5892
Port Lincoln | 14.5892
Port Lincoln 3 | 14.5892
Port Stanvac | 15.1234
Snuggery | 14.5892
All hydro | 58.2539
All wind | 45.1
All solar | 25.7

## Variable OPEX
Variable operating cost (real 2017 dollars)
Costs that can be expressed in terms of energy generated, not including fuel costs. Scaled by 2.7% from 2015 values to account for CPI increase.
Existing and Committed generators |  | New entrant technologies
Generator | Variable OPEX ($/MWh)1 | Generator | Variable OPEX ($/MWh)
Bayswater | 1.03 | Wind | 15.73
Eraring | 1.03 | Solar PV | 0
Liddell | 1.03 | OCGT | 10.15
Mount Piper | 1.03 | CCGT | 7.1
Vales Point | 1.03 | Pumped hydro | 5
Callide B | 1.03 | Biomass | 8.12
Callide Power Plant | 1.03 | Solar Thermal w/ 6hr Storage | 5.985
Gladstone | 1.03 | Reciprocating engine | 11.18
Kogan Creek | 0.51 | Black Coal (HELE) | 1.03
Millmerran | 3.18 | Large Scale Battery Storage (2hrs storage) | 0
Stanwell | 3.18
Tarong | 3.18
Tarong North | 1.03
Loy Yang A | 1.03
Loy Yang B | 1.03
Yallourn | 1.03
Colongra | 8.53
Smithfield | 7.19
Tallawarra | 7.19
Uranquinty | 10.69
Barcaldine | 10.69
Braemar | 10.69
Condamine | 7.19
Darling Downs | 7.19
Oakey | 10.69
Roma | 10.69
Swanbank E | 7.19
Yabulu (Townsville) | 7.19
Yarwun | 7.19
Somerton | 10.69
Bairnsdale | 10.69
Jeeralang A | 10.69
Jeeralang B | 10.69
Laverton North | 10.69
Mortlake | 10.69
Newport | 12.84
Valley Power | 10.69
Hallett GT | 10.69
Dry Creek | 10.69
Ladbroke Grove | 10.69
Mintaro | 10.69
Osborne | 7.19
Pelican Point | 7.19
Quarantine | 10.69
Torrens Island A | 2.16
Torrens Island B | 2.16
Bell Bay Three | 10.69
Tamar Valley | 10.69
Hunter Valley GT | 10.69
Mackay GT | 10.69
Mount Stuart | 10.69
Angaston | 11.18
Lonsdale | 11.18
Port Lincoln | 10.69
Port Lincoln 3 | 10.69
Port Stanvac | 11.18
Snuggery | 10.69
All hydro | 7.19
All wind | 10.39
All solar | 0
1. In capacity expansion simulations, variable OPEX may be varied by a small amount ($0.01) on a unit-by-unit basis within a power station to encourage model-driven retirement to occur on a per-unit basis

## Emissions
Emissions
Existing generators |  |  |  | Generic new entrant units, committed and advanced projects
Generator | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh) | Generator | Emissions (kg/MWh)
Bayswater | 865.5122 | 47.1309 | 912.6431 | Wind | 0
Eraring | 862.3464 | 47.7966 | 910.1431 | Solar PV | 0
Liddell | 930 | 50.5917 | 980.5917 | Biomass | 57.13
Mount Piper | 862.3022 | 46.2162 | 908.5184 | Barker Inlet2 | 500.46
Vales Point | 860 | 48.3051 | 908.3051 | Solar Thermal Central Receiver (6 hrs storage) | 0
Callide B | 920 | 11.3435 | 931.3435 | Pumped Hydro (6hrs storage) / Large Scale Battery Storage (2hrs storage) | 0
Callide Power Plant | 895.323 | 11.589 | 906.912 | New entrant combustion emissions3
Gladstone | 960 | 11.7614 | 971.7614 |  | Emissions (kg/GJ)
Kogan Creek | 820 | 11.04 | 831.04 | OCGT | 51.53
Millmerran | 830.1346 | 11.4634 | 841.598 | CCGT | 51.53
Stanwell | 860.94 | 11.25 | 872.19 | Black Coal (HELE) | 96.14
Tarong | 860.0221 | 11.4365 | 871.4586
Tarong North | 832.9647 | 10.7908 | 843.7555 | New entrant fugitive emissions
Loy Yang A | 1150 | 4.8176 | 1154.8176 |  | Gas Emissions (kg/GJ) | Coal Emissions (kg/GJ)
Loy Yang B | 1136.0409 | 4.9805 | 1141.0214 | Qld | 7.8 | 1.25
Yallourn | 1310 | 5.5149 | 1315.5149 | NSW | 12.8 | 5
Colongra | 640 | 142.56 | 782.56 | Vic | 3.9
Smithfield | 480.9688 | 106.7707 | 587.7395 | SA | 10.4 | 2.5
Tallawarra | 358.1395 | 89.3952 | 447.5347 | Tas | 3.9
Uranquinty | 581.7116 | 142.56 | 724.2716
Barcaldine | 999.9566 | 99.2829 | 1099.2394 | Derived new entrant emissions (kg/MWh)
Braemar | 570.4776 | 92.664 | 663.1416 | New entrant | Emissions4
Condamine | 454.3237 | 56.745 | 511.0687 | Qld OCGT | 602.1995
Darling Downs | 420.2045 | 57.3809 | 477.5854 | Qld CCGT | 411.1569
Oakey | 760 | 85.2736 | 845.2736 | NSW OCGT | 652.9495
Roma | 663.8544 | 92.664 | 756.5184 | NSW CCGT | 445.8069
Swanbank E | 370 | 57.9523 | 427.9523 | Vic OCGT | 562.6145
Yabulu | 450 | 59.2122 | 509.2122 | Vic CCGT | 384.1299
Yabulu Steam Turbine | 450 | 59.2122 | 509.2122 | SA OCGT | 628.5895
Yarwun | 532.3129 | 80.9365 | 613.2494 | SA CCGT | 429.1749
Somerton | 760 | 57.915 | 817.915 | Tas OCGT | 562.6145
Bairnsdale | 524.3273 | 40.8812 | 565.2085 | Tas CCGT | 384.1299
Jeeralang A | 819.9338 | 59.4707 | 879.4045 | Qld Coal (HELE) | 843.787
Jeeralang B | 819.9338 | 59.4707 | 879.4045 | NSW Coal (HELE) | 876.277
Laverton North | 745.3812 | 44.7987 | 790.1799 | SA Coal (HELE) | 803.4127
Mortlake | 530 | 43.4362 | 573.4362
Newport | 530 | 40.0541 | 570.0541
Valley Power | 813.6315 | 57.915 | 871.5465
Hallett GT | 1020 | 154.44 | 1174.44
Dry Creek | 1200 | 142.56 | 1342.56 | 2. Based on emissions factor of gas, modelled heat rate and fugitive emissions profile of Torrens Island A
Ladbroke Grove | 530 | 123.552 | 653.552 | 3. New entrant gas units use standard emissions rate for natural gas combined with heat rates to derive emissions.
Mintaro | 820 | 132.3771 | 952.3771 | 4. Based on a new entrant with 2017 heat rate
Osborne | 460 | 84.6857 | 544.6857
Pelican Point | 397.2675 | 76.44 | 473.7075
Quarantine | 688.8094 | 111.15 | 799.9594
Torrens Island A | 590 | 118.56 | 708.56
Torrens Island B | 570 | 111.15 | 681.15
Bell Bay Three | 617.7228 | 46.9614 | 664.6841
Tamar Valley GT | 652.9757 | 49.6414 | 702.6171
Tamar Valley ST | 410.3827 | 28.3725 | 438.7552
Hunter Valley GT | 887.1814 | 45.8229 | 933.0043
Mackay GT | 1000 | 45.8229 | 1045.8229
Mount Stuart | 955.8648 | 42.768 | 998.6328
Angaston1 | 940.2 | 73.4 | 1013.6
Lonsdale1 | 1442 | 49.8 | 1491.8
Port Lincoln | 1400 | 45.8585 | 1445.8585
Port Lincoln 3 | 1400 | 45.8585 | 1445.8585
Port Stanvac1 | 1442 | 49.8 | 1491.8
Snuggery | 1400 | 48.3508 | 1448.3508
Tailem Bend | 940.2 | 73.4 | 1013.6
All hydro | 0 | 0 | 0
All wind | 0 | 0 | 0
All solar | 0 | 0 | 0
1. Not present in source material; previous (2014) value retained
No price on carbon emissions has been assumed in the modelling

## MLF
Marginal Loss Factors (MLFs)
Marginal loss factors represent the impact of network losses on spot prices. No impacts on long term generation expansion, however, marginal loss factors do impact the short term dispatch modelling.
See http://aemo.com.au/-/media/Files/Electricity/NEM/Security_and_Reliability/Loss_Factors_and_Regional_Boundaries/2017/Marginal-Loss-Factors-for-the-2017-18-Financial-Year.pdf
Existing generators |  | Committed and advanced projects |  |  | Generic new entrant units
Generator | Marginal loss factor | Generator | Marginal loss factor | Shadow connection point | Generator | Marginal loss factor | Shadow connection point
Bayswater units 1,2 | 0.952 | Barker Inlet | 1.0016 | Torrens Island A | Barcaldine solar | 0.9431 | Gladstone
Bayswater units 3,4 | 0.9532 | Bodangora WF | 0.9831 | Colongra | Barcaldine wind | 0.9431 | Gladstone
Eraring units 1,2 | 0.982 | Crookwell 2 WF | 1.001 | Gullen Range | Broken Hill wind | 1.2757 | Broken Hill
Eraring units 3,4 | 0.9846 | Sapphire WF | 0.9509 | Liddell | Central NSW Tablelands solar | 0.8911 | Moree
Liddell | 0.9509 | Silverton WF | 1.2757 | Broken Hill | Central NSW Tablelands wind | 0.9509 | Liddell
Mount Piper | 0.9725 | White Rock WF | 0.9509 | Liddell | Central West NSW solar | 0.8911 | Moree
Vales Point | 0.9845 | Mt Emerald WF | 1.0238 | Barron Gorge | Central West NSW wind | 0.9725 | Mount Piper
Callide B | 0.9235 | Bulgana WF | 1.0019 | Ararat | Darling Downs solar | 0.9607 | Darling Downs
Callide Power Plant | 0.9211 | Crowlands WF | 1.0019 | Ararat | Darling Downs wind | 0.9607 | Darling Downs
Gladstone units 1,2,5,6 | 0.9431 | Kiata WF | 1.0473 | Horsham 66kV | Eastern Eyre Peninsula solar | 1.0048 | Davenport
Gladstone units 3,4 | 0.9402 | Mt Gellibrand WF | 1.02 | 500kV east of Mortlake | Eastern Eyre Peninsula wind | 0.9172 | Mount Millar
Kogan Creek | 0.9635 | Salt Creek WF | 1.0322 | Morton's Lane | Fitzroy solar | 0.9431 | Gladstone
Millmerran | 0.9737 | Stockyard Hill WF | 1.003 | 500kV east of Mortlake | Fitzroy wind | 0.9431 | Gladstone
Stanwell | 0.9329 | Hornsdale S3 WF | 0.9841 | Hornsdale | Gippsland wind | 0.9886 | Morwell TS
Tarong | 0.9712 | Griffith Solar | 1.1321 | Griffith 33kV | Isaac solar | 1.0035 | Yabulu
Tarong North | 0.9713 | Manildra Solar | 1.0374 | Orange 132kV | Isaac wind | 1.0035 | Yabulu
Loy Yang A | 0.9801 | Parkes Solar | 0.9831 | Parkes 66kV | King Island wind | 0.9025 | Woolnorth
Loy Yang B | 0.9801 | Clare Solar | 1.0457 | Clare 66kV | Leigh Creek solar | 1.0048 | Davenport
Yallourn unit 1 | 0.9702 | Hamilton Solar | 1.0126 | Collinsville 33kV | Leigh Creek wind | 0.982 | Hallett 1
Yallourn units 2,3,4 | 0.9558 | Kidston Solar | 1.07 | Proponent's estimate | Mid-North SA wind | 0.982 | Hallett 1
Blowering | 1.0506 | Oakey Solar | 0.9779 | Oakey 110kV | Moyne wind | 0.9997 | Waubra
Guthega | 0.9658 | Ross River Solar | 0.9964 | Mount Stuart | Murray River solar (NSW) | 0.9831 | Nyngan
Hume (NSW) | 1.1055 | Sun Metals Solar | 0.9964 | Mount Stuart | Murray River solar (VIC) | 0.8964 | Murray
Hume (Vic) | 0.8911 | Teebar Solar | 0.987 | Teebar Creek 132kV | Murray River wind (NSW) | 1.0087 | Uranquinty
Shoalhaven | 0.9931 | Whitsunday Solar | 1.0126 | Collinsville 33kV | Murray River wind (VIC) | 1.0019 | Ararat
Tumut 1 | 1.0356 | Bannerton Solar | 1.1068 | Red Cliffs 66kV | North East Tasmania wind | 0.9133 | Musselroe
Tumut 2 | 1.0356 | Gannawarra Solar | 1.0755 | Kerang 66kV | North QLD Clean Energy Hub solar | 1.0035 | Yabulu
Tumut 3 | 1.0155 | Karadoc Solar | 1.1068 | Red Cliffs 66kV | North QLD Clean Energy Hub wind | 1.0541 | Woree 132kV
Barron Gorge | 1.0238 | Wemen Solar | 1.1068 | Red Cliffs 66kV | North West New South Wales solar | 0.8911 | Moree
Kareeya | 1.0181 | Yatpool Solar | 1.1068 | Red Cliffs 66kV | North West New South Wales wind | 0.902 | Armidale 66kV
Wivenhoe | 0.9935 | Bungala Solar | 1.0038 | Playford 132kV | North West Tasmania wind | 0.9025 | Woolnorth
Bogong | 0.9213 | Tailem Bend Solar | 0.9936 | Tailem Bend 33kV | Northern NSW Tablelands solar | 0.8911 | Moree
Dartmouth | 0.9372 | Collinsville Solar | 1.0126 | Collinsville 33kV | Northern NSW Tablelands wind | 0.902 | Armidale 66kV
Eildon | 0.9696 | Darling Downs Solar | 0.9607 | Darling Downs | Northern QLD solar | 1.0035 | Yabulu
McKay Creek | 0.9213 | Emerald Solar | 0.98 | Lilyvale substation | Northern SA solar | 1.0048 | Davenport
Murray | 0.8964 | Kennedy Energy Park Solar | 1.0192 | 66kV near Hughenden | Northern SA wind | 0.982 | Hallett 1
West Kiewa | 0.954 | Kennedy Energy Park Wind | 1.0192 | 66kV near Hughenden | NSW pumped hydro | 1 | -
Bastyan | 0.9486 | Lilyvale Solar | 0.98 | Lilyvale substation | NSW thermal generation | 0.9509 | -
Catagunya | 0.9919 | Coopers Gap WF | 0.9712 | Tarong | QLD pumped hydro | 1 | -
Cethana | 0.963 | Lincoln Gap WF | 1.0048 | Davenport | QLD thermal generation | 0.9431 | -
Devils Gate | 0.9703 | Cattle Hill WF | 0.9487 | Lake Echo | Riverland solar (NSW) | 0.9831 | Nyngan
Fisher | 0.9671 | Snowy2.0 | 1.0356 | Tumut | Riverland solar (SA) | 1.0048 | Davenport
Gordon | 0.9594 | Battery of the Nation | 1 | - | Riverland wind (NSW) | 1.2757 | Broken Hill
John Butters | 0.9445 |  |  |  | Riverland wind (SA) | 0.982 | Hallett 1
Liapootah | 0.9919 |  |  |  | Roxby Downs solar | 1.0048 | Davenport
Lake Echo | 0.9487 |  |  |  | SA pumped hydro | 1 | -
Lemonthyme | 0.9711 |  |  |  | SA thermal generation | 0.917 | -
Mackintosh | 0.9402 |  |  |  | South East SA wind | 0.9936 | Tailem Bend
Meadowbank | 0.977 |  |  |  | Southern NSW Tablelands solar | 0.8911 | Moree
Poatina units 1,2 | 0.9677 |  |  |  | Southern NSW Tablelands wind | 1.0163 | Capital
Poatina units 3,4,5,6 | 0.9813 |  |  |  | TAS pumped hydro | 1 | -
Reece unit 1 | 0.9399 |  |  |  | TAS thermal generation | 1.001 | -
Reece unit 2 | 0.9402 |  |  |  | Tasmania Midlands wind | 0.9487 | Lake Echo
Tarraleah | 0.9338 |  |  |  | VIC pumped hydro | 1 | -
Trevallyn | 0.9898 |  |  |  | VIC thermal generation | 0.9801 | -
Tribute | 0.9466 |  |  |  | Western Eyre Peninsula solar | 1.0048 | Davenport
Tungatinah | 0.9233 |  |  |  | Western Eyre Peninsula wind | 1.0118 | Wudina
Wilmot | 0.9711 |  |  |  | Western Victoria wind | 1.0019 | Ararat
Wayatinah | 0.9919 |  |  |  | Yorke Peninsula wind | 0.833 | Wattle Point
Colongra | 0.9831
Smithfield | 1.0041
Tallawarra | 1.0013
Uranquinty | 1.0087
Barcaldine | 0.9507
Braemar | 0.9607
Condamine | 0.9688
Darling Downs | 0.9607
Oakey | 0.9667
Roma | 0.9623
Swanbank E | 1.0019
Yabulu | 1.0035
Yabulu Steam Turbine | 0.9778
Yarwun | 0.9435
Somerton | 0.9968
Bairnsdale | 0.9863
Jeeralang A | 0.983
Jeeralang B | 0.983
Laverton North | 1.0081
Mortlake | 1.005
Newport | 0.999
Valley Power | 0.9801
Hallett GT | 0.982
Dry Creek | 1.0019
Ladbroke Grove | 0.917
Mintaro | 0.9941
Osborne | 0.9988
Pelican Point | 1.0012
Quarantine | 0.9856
Torrens Island A | 1.0016
Torrens Island B | 1.0016
Bell Bay Three | 1.0001
Tamar Valley | 1.0001
Hunter Valley GT | 0.9582
Mackay GT | 0.9577
Mount Stuart | 0.9964
Angaston | 1.0121
Lonsdale | 1.0047
Port Lincoln | 1.0158
Port Lincoln 3 | 1.051
Port Stanvac | 1.0047
Snuggery | 0.9318
Tailem Bend | 1
Boco Rock | 1.0167
Capital | 1.0163
Cullerin Range | 1.0135
Gullen Range | 1.001
Gunning | 1.0135
Taralga | 0.9998
Woodlawn | 1.0163
Ararat | 1.0019
Bald Hills | 0.9886
Challicum Hills | 1.0322
Macarthur | 1.0017
Mortons Lane | 1.0322
Mount Mercer | 1.001
Oaklands Hill | 1.0322
Portland stage 1 | 1.0322
Portland stage 2,3,4 | 1.0121
Waubra | 0.9997
Canunda | 0.8967
Cathedral Rocks | 0.8965
Clements Gap | 0.9787
Hallett Brown Hill | 0.982
Hallett Hill | 0.9818
Hallett North Brown Hill | 0.9798
Hallett The Bluff | 0.9798
Hornsdale | 0.9841
Lake Bonney | 0.8906
Mount Millar | 0.9172
Snowtown 1 | 0.9296
Snowtown 2 | 0.9869
Starfish Hill | 1.0047
Waterloo | 0.9751
Wattle Point | 0.833
Musselroe | 0.9133
Woolnorth | 0.9025
Broken Hill Solar | 1.2456
Nyngan | 0.9831
Moree | 0.8911