## Inputs
Base Assumptions
Discount rate | 6%
Asset life (years) | 30
O&M | 2%
Sensitivities | Low | High
Cost | 70% | 130%
Discount rate | 3.5% | 8.5%
Reasonable scenarios
Scenario | Weighting_Base | Weighting_Fast | Weighting_Slow
Neutral | 50% | 25% | 25%
Fast | 25% | 50% | 25%
Slow | 25% | 25% | 50%
Solution | Name | Year | MVAr | Capital Cost ($M)
Option 1A | KTS 220 kV | 2021 | 100 | 6.4
Option 1A | KTS 220 kV | 2022 | 100 | 6.4
Option 1A | MTS 220 kV | 2022 | 100 | 6.3
Option 1B | KTS 220 kV | 2021 | 100 | 6.4
Option 1B | KTS 220 kV | 2022 | 100 | 6.4
Option 1B | MTS 220 kV | 2023 | 100 | 6.3
Option 1B | MTS 220 kV | 2023 | 100 | 6.3
Option 1C | KTS 220 kV | 2021 | 100 | 6.4
Option 1C | KTS 220 kV | 2022 | 100 | 6.4
Option 1C | MTS 220 kV | 2022 | 100 | 6.3
Option 1C | MTS 220 kV | 2023 | 100 | 6.3
Option 1C | MTS 220 kV | 2023 | 100 | 6.3
Option 1D | KTS 220 kV | 2021 | 100 | 6.4
Option 1D | KTS 220 kV | 2022 | 100 | 6.4
Option 1D | MTS 220 kV | 2022 | 100 | 6.3
Option 1D | MTS 220 kV | 2023 | 100 | 6.3
Option 1D | MTS 220 kV | 2023 | 100 | 6.3
Option 1D | SMTS 220 kV | 2024 | 100 | 7.1
Option 2 | KTS 220 kV | 2021 | 100 | 6.4
Option 2 | KTS 220 kV | 2022 | 100 | 6.4
Option 2 | MTS 220 kV | 2023 | 100 | 6.3
Option 2 | MTS 220 kV | 2023 | 100 | 6.3
Option 2 | SMTS 330 kV SynCon | 2022 | 100 | 59.3

## Summary
Cost and net market benefits for base case assumptions (weighting, discount rate and cost)
Option | Capital Cost, $M (2019-20) | Capital + O&M Cost, $M (NPV) | Neutral - Net Market Benefit $M (NPV) | Fast Change - Net Market Benefit $M (NPV) | Slow Change - Net Market Benefit $M (NPV) | Weighted - Net market benefit $M (NPV)
1A | 19.1 | 16.6863 | 48.2364 | 14.928 | 144.1109 | 63.8779
1B | 25.4 | 21.4709 | 53.0492 | 15.098 | 165.4284 | 71.6562
1C | 31.7 | 26.8663 | 53.5098 | 13.8093 | 178.9044 | 74.9333
1D | 38.8 | 32.278 | 51.3734 | 10.7997 | 185.2226 | 74.6923
2 | 84.7 | 72.2561 | 64.9033 | 18.4927 | 208.6975 | 89.2492
Weighted net market benefits NPV ($M)
Option | Base | High Cost | Low Cost | High Discount Rate | Low Discount Rate | Slow Weighting | Fast Weighting
1A | 63.8779 | 58.872 | 68.8838 | 42.6671 | 98.0991 | 87.8465 | 55.5508
1B | 71.6562 | 65.2149 | 78.0975 | 47.1592 | 111.628 | 99.751 | 62.1684
1C | 74.9333 | 66.8734 | 82.9932 | 48.3505 | 118.4145 | 106.282 | 65.0082
1D | 74.6923 | 65.0089 | 84.3757 | 47.0757 | 120.2611 | 108.1546 | 64.5489
2 | 89.2492 | 67.5723 | 110.926 | 50.6759 | 153.105 | 125.1978 | 77.6465

## Option 1A
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Neutral | Fast | Slow | Weighting_Base | Weighting_Fast | Weighting_Slow
Base | 6% | 100% | 19.1 | 16.6863 | 48.2364 | 14.928 | 144.1109 | 63.8779 | 55.5508 | 87.8465
High Discount rate | 8.5% | 100% | 19.1 | 15.687 | 31.2762 | 7.6097 | 100.5062 | 42.6671 | 36.7505 | 59.9746
Low Discount rate | 3.5% | 100% | 19.1 | 17.7777 | 75.7273 | 26.9775 | 213.9644 | 98.0991 | 85.9117 | 132.6584
High Cost | 6% | 130% | 19.1 | 21.6922 | 43.2305 | 9.9221 | 139.105 | 58.872 | 50.5449 | 82.8406
Low Cost | 6% | 70% | 19.1 | 11.6804 | 53.2423 | 19.9339 | 149.1168 | 68.8838 | 60.5567 | 92.8524
Base
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 16.6863 |  | NPV | [7 empty] | 64.9227 | NPV | [7 empty] | 31.6143 | NPV | [7 empty] | 160.7972
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.43863 | 0.0087727 | 5.7107 | 0.44741 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 25.8864 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 11.688 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 64.1396 | 0.79408
2022 | 200 | 12.7 | 0.87042 | 0.017408 | 11.5786 | 1.3352 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 52.8984 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 23.8843 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 131.0682 | 2.9131
2023 | 0 | 0 | 0 | 0 | 0 | 1.3352 |  | 2023 | 160 | 23 | 2.3338 | 0.12955 | 0 | 2.4634 | 0 | 2.4634 | 2023 | 103 | 15 | 1.4794 | 0.082313 | 0 | 1.5617 | 0 | 1.5617 | 2023 | 442 | 63 | 6.0391 | 0.32955 | 0 | 6.3686 | 0 | 6.3686
2024 | 0 | 0 | 0 | 0 | 0 | 1.3352 |  | 2024 | 237 | 34 | 3.5389 | 0.19408 | 0 | 3.733 | 0 | 3.733 | 2024 | 161 | 23 | 2.3972 | 0.1318 | 0 | 2.529 | 0 | 2.529 | 2024 | 663 | 94 | 9.4993 | 0.50415 | 0 | 10.0035 | 0 | 10.0035
2025 | 0 | 0 | 0 | 0 | 0 | 1.3352 |  | 2025 | 244 | 35 | 3.6494 | 0.19687 | 0 | 3.8463 | 0 | 3.8463 | 2025 | 159 | 23 | 2.3666 | 0.12867 | 0 | 2.4953 | 0 | 2.4953 | 2025 | 726 | 103 | 10.5011 | 0.55155 | 0 | 11.0526 | 0 | 11.0526
2026 | 0 | 0 | 0 | 0 | 0 | 1.3352 |  | 2026 | 321 | 45 | 5.0889 | 0.27307 | 0 | 5.3619 | 0 | 5.3619 | 2026 | 178 | 25 | 2.7768 | 0.15039 | 0 | 2.9272 | 0 | 2.9272 | 2026 | 927 | 131 | 13.4255 | 0.70226 | 0 | 14.1277 | 0 | 14.1277
2027 | 0 | 0 | 0 | 0 | 0 | 1.3352 |  | 2027 | 387 | 56 | 5.7023 | 0.30627 | 0 | 6.0086 | 0 | 6.0086 | 2027 | 171 | 24 | 2.4545 | 0.13367 | 0 | 2.5881 | 0 | 2.5881 | 2027 | 1107 | 156 | 14.122 | 0.74249 | 0 | 14.8645 | 0 | 14.8645
2028 | 0 | 0 | 0 | 0 | 0 | 1.3352 |  | 2028 | 435 | 62 | 6.5319 | 0.35015 | 0 | 6.8821 | 0 | 6.8821 | 2028 | 176 | 25 | 2.5851 | 0.14084 | 0 | 2.726 | 0 | 2.726 | 2028 | 1207 | 170 | 15.4252 | 0.80763 | 0 | 16.2328 | 0 | 16.2328
Total | 300 | 19.1 | 1.3091 | 0.026181 | 17.2894 | 17.2894 |  | Total | 1948 | 279 | 29.1273 | 1.5778 | 0 | 30.7051 | 78.7849 | 78.7849 |  | 1081 | 155 | 15.9115 | 0.87146 | 0 | 16.783 | 35.5723 | 35.5723 |  | 5343 | 756 | 72.5227 | 3.8344 | 0 | 76.357 | 195.2078 | 195.2078
High Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 15.687 |  | NPV | [7 empty] | 46.9633 | NPV | [7 empty] | 23.2968 | NPV | [7 empty] | 116.1932
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.54887 | 0.010977 | 5.9588 | 0.55985 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 21.586 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 9.7463 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 53.4844 | 0.79408
2022 | 200 | 12.7 | 1.0892 | 0.021783 | 12.0091 | 1.6708 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 43.846 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 19.797 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 108.6387 | 2.9131
2023 | 0 | 0 | 0 | 0 | 0 | 1.6708 |  | 2023 | 160 | 23 | 2.3338 | 0.12955 | 0 | 2.4634 | 0 | 2.4634 | 2023 | 103 | 15 | 1.4794 | 0.082313 | 0 | 1.5617 | 0 | 1.5617 | 2023 | 442 | 63 | 6.0391 | 0.32955 | 0 | 6.3686 | 0 | 6.3686
2024 | 0 | 0 | 0 | 0 | 0 | 1.6708 |  | 2024 | 237 | 34 | 3.5389 | 0.19408 | 0 | 3.733 | 0 | 3.733 | 2024 | 161 | 23 | 2.3972 | 0.1318 | 0 | 2.529 | 0 | 2.529 | 2024 | 663 | 94 | 9.4993 | 0.50415 | 0 | 10.0035 | 0 | 10.0035
2025 | 0 | 0 | 0 | 0 | 0 | 1.6708 |  | 2025 | 244 | 35 | 3.6494 | 0.19687 | 0 | 3.8463 | 0 | 3.8463 | 2025 | 159 | 23 | 2.3666 | 0.12867 | 0 | 2.4953 | 0 | 2.4953 | 2025 | 726 | 103 | 10.5011 | 0.55155 | 0 | 11.0526 | 0 | 11.0526
2026 | 0 | 0 | 0 | 0 | 0 | 1.6708 |  | 2026 | 321 | 45 | 5.0889 | 0.27307 | 0 | 5.3619 | 0 | 5.3619 | 2026 | 178 | 25 | 2.7768 | 0.15039 | 0 | 2.9272 | 0 | 2.9272 | 2026 | 927 | 131 | 13.4255 | 0.70226 | 0 | 14.1277 | 0 | 14.1277
2027 | 0 | 0 | 0 | 0 | 0 | 1.6708 |  | 2027 | 387 | 56 | 5.7023 | 0.30627 | 0 | 6.0086 | 0 | 6.0086 | 2027 | 171 | 24 | 2.4545 | 0.13367 | 0 | 2.5881 | 0 | 2.5881 | 2027 | 1107 | 156 | 14.122 | 0.74249 | 0 | 14.8645 | 0 | 14.8645
2028 | 0 | 0 | 0 | 0 | 0 | 1.6708 |  | 2028 | 435 | 62 | 6.5319 | 0.35015 | 0 | 6.8821 | 0 | 6.8821 | 2028 | 176 | 25 | 2.5851 | 0.14084 | 0 | 2.726 | 0 | 2.726 | 2028 | 1207 | 170 | 15.4252 | 0.80763 | 0 | 16.2328 | 0 | 16.2328
Total | 300 | 19.1 | 1.638 | 0.032761 | 17.9679 | 17.9679 |  | Total | 1948 | 279 | 29.1273 | 1.5778 | 0 | 30.7051 | 65.432 | 65.432 |  | 1081 | 155 | 15.9115 | 0.87146 | 0 | 16.783 | 29.5433 | 29.5433 |  | 5343 | 756 | 72.5227 | 3.8344 | 0 | 76.357 | 162.123 | 162.123
Low Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 17.7777 |  | NPV | [7 empty] | 93.505 | NPV | [7 empty] | 44.7552 | NPV | [7 empty] | 231.7421
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.33621 | 0.0067242 | 5.3834 | 0.34293 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 31.8366 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 14.3746 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 78.8825 | 0.79408
2022 | 200 | 12.7 | 0.66717 | 0.013343 | 11.0019 | 1.0234 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 65.5761 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 29.6083 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 162.48 | 2.9131
2023 | 0 | 0 | 0 | 0 | 0 | 1.0234 |  | 2023 | 160 | 23 | 2.3338 | 0.12955 | 0 | 2.4634 | 0 | 2.4634 | 2023 | 103 | 15 | 1.4794 | 0.082313 | 0 | 1.5617 | 0 | 1.5617 | 2023 | 442 | 63 | 6.0391 | 0.32955 | 0 | 6.3686 | 0 | 6.3686
2024 | 0 | 0 | 0 | 0 | 0 | 1.0234 |  | 2024 | 237 | 34 | 3.5389 | 0.19408 | 0 | 3.733 | 0 | 3.733 | 2024 | 161 | 23 | 2.3972 | 0.1318 | 0 | 2.529 | 0 | 2.529 | 2024 | 663 | 94 | 9.4993 | 0.50415 | 0 | 10.0035 | 0 | 10.0035
2025 | 0 | 0 | 0 | 0 | 0 | 1.0234 |  | 2025 | 244 | 35 | 3.6494 | 0.19687 | 0 | 3.8463 | 0 | 3.8463 | 2025 | 159 | 23 | 2.3666 | 0.12867 | 0 | 2.4953 | 0 | 2.4953 | 2025 | 726 | 103 | 10.5011 | 0.55155 | 0 | 11.0526 | 0 | 11.0526
2026 | 0 | 0 | 0 | 0 | 0 | 1.0234 |  | 2026 | 321 | 45 | 5.0889 | 0.27307 | 0 | 5.3619 | 0 | 5.3619 | 2026 | 178 | 25 | 2.7768 | 0.15039 | 0 | 2.9272 | 0 | 2.9272 | 2026 | 927 | 131 | 13.4255 | 0.70226 | 0 | 14.1277 | 0 | 14.1277
2027 | 0 | 0 | 0 | 0 | 0 | 1.0234 |  | 2027 | 387 | 56 | 5.7023 | 0.30627 | 0 | 6.0086 | 0 | 6.0086 | 2027 | 171 | 24 | 2.4545 | 0.13367 | 0 | 2.5881 | 0 | 2.5881 | 2027 | 1107 | 156 | 14.122 | 0.74249 | 0 | 14.8645 | 0 | 14.8645
2028 | 0 | 0 | 0 | 0 | 0 | 1.0234 |  | 2028 | 435 | 62 | 6.5319 | 0.35015 | 0 | 6.8821 | 0 | 6.8821 | 2028 | 176 | 25 | 2.5851 | 0.14084 | 0 | 2.726 | 0 | 2.726 | 2028 | 1207 | 170 | 15.4252 | 0.80763 | 0 | 16.2328 | 0 | 16.2328
Total | 300 | 19.1 | 1.0034 | 0.020067 | 16.3852 | 16.3852 |  | Total | 1948 | 279 | 29.1273 | 1.5778 | 0 | 30.7051 | 97.4126 | 97.4126 |  | 1081 | 155 | 15.9115 | 0.87146 | 0 | 16.783 | 43.9829 | 43.9829 |  | 5343 | 756 | 72.5227 | 3.8344 | 0 | 76.357 | 241.3625 | 241.3625
High Cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 21.6922 |  | NPV | [7 empty] | 64.9227 | NPV | [7 empty] | 31.6143 | NPV | [7 empty] | 160.7972
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 8.32 | 0.57023 | 0.011405 | 7.424 | 0.58163 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 25.8864 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 11.688 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 64.1396 | 0.79408
2022 | 200 | 16.51 | 1.1315 | 0.022631 | 15.0522 | 1.7358 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 52.8984 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 23.8843 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 131.0682 | 2.9131
2023 | 0 | 0 | 0 | 0 | 0 | 1.7358 |  | 2023 | 160 | 23 | 2.3338 | 0.12955 | 0 | 2.4634 | 0 | 2.4634 | 2023 | 103 | 15 | 1.4794 | 0.082313 | 0 | 1.5617 | 0 | 1.5617 | 2023 | 442 | 63 | 6.0391 | 0.32955 | 0 | 6.3686 | 0 | 6.3686
2024 | 0 | 0 | 0 | 0 | 0 | 1.7358 |  | 2024 | 237 | 34 | 3.5389 | 0.19408 | 0 | 3.733 | 0 | 3.733 | 2024 | 161 | 23 | 2.3972 | 0.1318 | 0 | 2.529 | 0 | 2.529 | 2024 | 663 | 94 | 9.4993 | 0.50415 | 0 | 10.0035 | 0 | 10.0035
2025 | 0 | 0 | 0 | 0 | 0 | 1.7358 |  | 2025 | 244 | 35 | 3.6494 | 0.19687 | 0 | 3.8463 | 0 | 3.8463 | 2025 | 159 | 23 | 2.3666 | 0.12867 | 0 | 2.4953 | 0 | 2.4953 | 2025 | 726 | 103 | 10.5011 | 0.55155 | 0 | 11.0526 | 0 | 11.0526
2026 | 0 | 0 | 0 | 0 | 0 | 1.7358 |  | 2026 | 321 | 45 | 5.0889 | 0.27307 | 0 | 5.3619 | 0 | 5.3619 | 2026 | 178 | 25 | 2.7768 | 0.15039 | 0 | 2.9272 | 0 | 2.9272 | 2026 | 927 | 131 | 13.4255 | 0.70226 | 0 | 14.1277 | 0 | 14.1277
2027 | 0 | 0 | 0 | 0 | 0 | 1.7358 |  | 2027 | 387 | 56 | 5.7023 | 0.30627 | 0 | 6.0086 | 0 | 6.0086 | 2027 | 171 | 24 | 2.4545 | 0.13367 | 0 | 2.5881 | 0 | 2.5881 | 2027 | 1107 | 156 | 14.122 | 0.74249 | 0 | 14.8645 | 0 | 14.8645
2028 | 0 | 0 | 0 | 0 | 0 | 1.7358 |  | 2028 | 435 | 62 | 6.5319 | 0.35015 | 0 | 6.8821 | 0 | 6.8821 | 2028 | 176 | 25 | 2.5851 | 0.14084 | 0 | 2.726 | 0 | 2.726 | 2028 | 1207 | 170 | 15.4252 | 0.80763 | 0 | 16.2328 | 0 | 16.2328
Total | 300 | 24.83 | 1.7018 | 0.034035 | 22.4762 | 22.4762 |  | Total | 1948 | 279 | 29.1273 | 1.5778 | 0 | 30.7051 | 78.7849 | 78.7849 |  | 1081 | 155 | 15.9115 | 0.87146 | 0 | 16.783 | 35.5723 | 35.5723 |  | 5343 | 756 | 72.5227 | 3.8344 | 0 | 76.357 | 195.2078 | 195.2078
Low cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 11.6804 |  | NPV | [7 empty] | 64.9227 | NPV | [7 empty] | 31.6143 | NPV | [7 empty] | 160.7972
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 4.48 | 0.30704 | 0.0061409 | 3.9975 | 0.31319 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 25.8864 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 11.688 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 64.1396 | 0.79408
2022 | 200 | 8.89 | 0.60929 | 0.012186 | 8.105 | 0.93466 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 52.8984 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 23.8843 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 131.0682 | 2.9131
2023 | 0 | 0 | 0 | 0 | 0 | 0.93466 |  | 2023 | 160 | 23 | 2.3338 | 0.12955 | 0 | 2.4634 | 0 | 2.4634 | 2023 | 103 | 15 | 1.4794 | 0.082313 | 0 | 1.5617 | 0 | 1.5617 | 2023 | 442 | 63 | 6.0391 | 0.32955 | 0 | 6.3686 | 0 | 6.3686
2024 | 0 | 0 | 0 | 0 | 0 | 0.93466 |  | 2024 | 237 | 34 | 3.5389 | 0.19408 | 0 | 3.733 | 0 | 3.733 | 2024 | 161 | 23 | 2.3972 | 0.1318 | 0 | 2.529 | 0 | 2.529 | 2024 | 663 | 94 | 9.4993 | 0.50415 | 0 | 10.0035 | 0 | 10.0035
2025 | 0 | 0 | 0 | 0 | 0 | 0.93466 |  | 2025 | 244 | 35 | 3.6494 | 0.19687 | 0 | 3.8463 | 0 | 3.8463 | 2025 | 159 | 23 | 2.3666 | 0.12867 | 0 | 2.4953 | 0 | 2.4953 | 2025 | 726 | 103 | 10.5011 | 0.55155 | 0 | 11.0526 | 0 | 11.0526
2026 | 0 | 0 | 0 | 0 | 0 | 0.93466 |  | 2026 | 321 | 45 | 5.0889 | 0.27307 | 0 | 5.3619 | 0 | 5.3619 | 2026 | 178 | 25 | 2.7768 | 0.15039 | 0 | 2.9272 | 0 | 2.9272 | 2026 | 927 | 131 | 13.4255 | 0.70226 | 0 | 14.1277 | 0 | 14.1277
2027 | 0 | 0 | 0 | 0 | 0 | 0.93466 |  | 2027 | 387 | 56 | 5.7023 | 0.30627 | 0 | 6.0086 | 0 | 6.0086 | 2027 | 171 | 24 | 2.4545 | 0.13367 | 0 | 2.5881 | 0 | 2.5881 | 2027 | 1107 | 156 | 14.122 | 0.74249 | 0 | 14.8645 | 0 | 14.8645
2028 | 0 | 0 | 0 | 0 | 0 | 0.93466 |  | 2028 | 435 | 62 | 6.5319 | 0.35015 | 0 | 6.8821 | 0 | 6.8821 | 2028 | 176 | 25 | 2.5851 | 0.14084 | 0 | 2.726 | 0 | 2.726 | 2028 | 1207 | 170 | 15.4252 | 0.80763 | 0 | 16.2328 | 0 | 16.2328
Total | 300 | 13.37 | 0.91634 | 0.018327 | 12.1026 | 12.1026 |  | Total | 1948 | 279 | 29.1273 | 1.5778 | 0 | 30.7051 | 78.7849 | 78.7849 |  | 1081 | 155 | 15.9115 | 0.87146 | 0 | 16.783 | 35.5723 | 35.5723 |  | 5343 | 756 | 72.5227 | 3.8344 | 0 | 76.357 | 195.2078 | 195.2078

## Option 1B
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Neutral | Fast | Slow | Weighting_Base | Weighting_Fast | Weighting_Slow
Base | 6% | 100% | 25.4 | 21.4709 | 53.0492 | 15.098 | 165.4284 | 71.6562 | 62.1684 | 99.751
High Discount rate | 8.5% | 100% | 25.4 | 19.9297 | 33.6496 | 6.8495 | 114.4881 | 47.1592 | 40.4592 | 67.3689
Low Discount rate | 3.5% | 100% | 25.4 | 23.1816 | 84.9022 | 28.9634 | 247.7443 | 111.628 | 97.6433 | 152.3385
High Cost | 6% | 130% | 25.4 | 27.9122 | 46.6079 | 8.6567 | 158.9871 | 65.2149 | 55.7271 | 93.3097
Low Cost | 6% | 70% | 25.4 | 15.0296 | 59.4904 | 21.5392 | 171.8697 | 78.0975 | 68.6097 | 106.1923
Base
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 21.4709 |  | NPV | [7 empty] | 74.5201 | NPV | [7 empty] | 36.5689 | NPV | [7 empty] | 186.8993
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.43863 | 0.0087727 | 5.7107 | 0.44741 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 22.3629 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 10.1947 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 55.8255 | 0.79408
2022 | 100 | 6.4 | 0.43863 | 0.0087727 | 5.8349 | 0.89482 |  | 2022 | 106 | 15 | 1.2316 | 0.069034 | 0 | 1.3006 | 22.8491 | 1.3006 | 2022 | 73 | 10 | 0.99001 | 0.055498 | 0 | 1.0455 | 10.4163 | 1.0455 | 2022 | 170 | 25 | 2.2029 | 0.12333 | 0 | 2.3263 | 57.0392 | 2.3263
2023 | 200 | 12.6 | 0.86356 | 0.017271 | 11.7181 | 1.7756 |  | 2023 | 160 | 23 | 2.5368 | 0.14067 | 0 | 2.6775 | 46.6156 | 2.6775 | 2023 | 114 | 17 | 1.6461 | 0.091499 | 0 | 1.7376 | 21.2508 | 1.7376 | 2023 | 502 | 71 | 6.8466 | 0.37352 | 0 | 7.2201 | 116.3685 | 7.2201
2024 | 0 | 0 | 0 | 0 | 0 | 1.7756 |  | 2024 | 237 | 34 | 3.894 | 0.21347 | 0 | 4.1074 | 0 | 4.1074 | 2024 | 181 | 25 | 2.6869 | 0.14773 | 0 | 2.8347 | 0 | 2.8347 | 2024 | 762 | 108 | 10.9107 | 0.58014 | 0 | 11.4909 | 0 | 11.4909
2025 | 0 | 0 | 0 | 0 | 0 | 1.7756 |  | 2025 | 244 | 35 | 4.0872 | 0.22047 | 0 | 4.3076 | 0 | 4.3076 | 2025 | 191 | 26 | 2.8358 | 0.14875 | 0 | 2.9845 | 0 | 2.9845 | 2025 | 844 | 120 | 12.1951 | 0.64197 | 0 | 12.8371 | 0 | 12.8371
2026 | 0 | 0 | 0 | 0 | 0 | 1.7756 |  | 2026 | 321 | 45 | 5.7652 | 0.30945 | 0 | 6.0747 | 0 | 6.0747 | 2026 | 206 | 30 | 3.2255 | 0.1747 | 0 | 3.4002 | 0 | 3.4002 | 2026 | 1080 | 153 | 15.6452 | 0.81995 | 0 | 16.4652 | 0 | 16.4652
2027 | 0 | 0 | 0 | 0 | 0 | 1.7756 |  | 2027 | 387 | 56 | 6.5766 | 0.35351 | 0 | 6.9301 | 0 | 6.9301 | 2027 | 200 | 29 | 2.866 | 0.15613 | 0 | 3.0222 | 0 | 3.0222 | 2027 | 1282 | 181 | 16.3681 | 0.86152 | 0 | 17.2296 | 0 | 17.2296
2028 | 0 | 0 | 0 | 0 | 0 | 1.7756 |  | 2028 | 435 | 62 | 7.6112 | 0.40826 | 0 | 8.0195 | 0 | 8.0195 | 2028 | 205 | 29 | 2.9989 | 0.16308 | 0 | 3.162 | 0 | 3.162 | 2028 | 1396 | 197 | 17.8529 | 0.93601 | 0 | 18.7889 | 0 | 18.7889
Total | 400 | 25.4 | 1.7408 | 0.034817 | 23.2637 | 23.2637 |  | Total | 1948 | 279 | 32.5434 | 1.7621 | 0 | 34.3055 | 91.8277 | 91.8277 |  | 1221 | 174 | 17.9813 | 0.97848 | 0 | 18.9598 | 41.8618 | 41.8618 |  | 6095 | 863 | 82.773 | 4.3791 | 0 | 87.1521 | 229.2332 | 229.2332
High Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 19.9297 |  | NPV | [7 empty] | 53.5794 | NPV | [7 empty] | 26.7793 | NPV | [7 empty] | 134.4179
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.54887 | 0.010977 | 5.9588 | 0.55985 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 18.6479 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 8.5011 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 46.5514 | 0.79408
2022 | 100 | 6.4 | 0.54887 | 0.010977 | 6.0518 | 1.1197 |  | 2022 | 106 | 15 | 1.2316 | 0.069034 | 0 | 1.3006 | 18.939 | 1.3006 | 2022 | 73 | 10 | 0.99001 | 0.055498 | 0 | 1.0455 | 8.6338 | 1.0455 | 2022 | 170 | 25 | 2.2029 | 0.12333 | 0 | 2.3263 | 47.2782 | 2.3263
2023 | 200 | 12.6 | 1.0806 | 0.021612 | 12.0833 | 2.2219 |  | 2023 | 160 | 23 | 2.5368 | 0.14067 | 0 | 2.6775 | 38.4146 | 2.6775 | 2023 | 114 | 17 | 1.6461 | 0.091499 | 0 | 1.7376 | 17.5122 | 1.7376 | 2023 | 502 | 71 | 6.8466 | 0.37352 | 0 | 7.2201 | 95.896 | 7.2201
2024 | 0 | 0 | 0 | 0 | 0 | 2.2219 |  | 2024 | 237 | 34 | 3.894 | 0.21347 | 0 | 4.1074 | 0 | 4.1074 | 2024 | 181 | 25 | 2.6869 | 0.14773 | 0 | 2.8347 | 0 | 2.8347 | 2024 | 762 | 108 | 10.9107 | 0.58014 | 0 | 11.4909 | 0 | 11.4909
2025 | 0 | 0 | 0 | 0 | 0 | 2.2219 |  | 2025 | 244 | 35 | 4.0872 | 0.22047 | 0 | 4.3076 | 0 | 4.3076 | 2025 | 191 | 26 | 2.8358 | 0.14875 | 0 | 2.9845 | 0 | 2.9845 | 2025 | 844 | 120 | 12.1951 | 0.64197 | 0 | 12.8371 | 0 | 12.8371
2026 | 0 | 0 | 0 | 0 | 0 | 2.2219 |  | 2026 | 321 | 45 | 5.7652 | 0.30945 | 0 | 6.0747 | 0 | 6.0747 | 2026 | 206 | 30 | 3.2255 | 0.1747 | 0 | 3.4002 | 0 | 3.4002 | 2026 | 1080 | 153 | 15.6452 | 0.81995 | 0 | 16.4652 | 0 | 16.4652
2027 | 0 | 0 | 0 | 0 | 0 | 2.2219 |  | 2027 | 387 | 56 | 6.5766 | 0.35351 | 0 | 6.9301 | 0 | 6.9301 | 2027 | 200 | 29 | 2.866 | 0.15613 | 0 | 3.0222 | 0 | 3.0222 | 2027 | 1282 | 181 | 16.3681 | 0.86152 | 0 | 17.2296 | 0 | 17.2296
2028 | 0 | 0 | 0 | 0 | 0 | 2.2219 |  | 2028 | 435 | 62 | 7.6112 | 0.40826 | 0 | 8.0195 | 0 | 8.0195 | 2028 | 205 | 29 | 2.9989 | 0.16308 | 0 | 3.162 | 0 | 3.162 | 2028 | 1396 | 197 | 17.8529 | 0.93601 | 0 | 18.7889 | 0 | 18.7889
Total | 400 | 25.4 | 2.1783 | 0.043567 | 24.094 | 24.094 |  | Total | 1948 | 279 | 32.5434 | 1.7621 | 0 | 34.3055 | 76.0015 | 76.0015 |  | 1221 | 174 | 17.9813 | 0.97848 | 0 | 18.9598 | 34.647 | 34.647 |  | 6095 | 863 | 82.773 | 4.3791 | 0 | 87.1521 | 189.7257 | 189.7257
Low Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 23.1816 |  | NPV | [7 empty] | 108.0838 | NPV | [7 empty] | 52.145 | NPV | [7 empty] | 270.9259
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.33621 | 0.0067242 | 5.3834 | 0.34293 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 27.5032 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 12.538 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 68.6573 | 0.79408
2022 | 100 | 6.4 | 0.33621 | 0.0067242 | 5.5442 | 0.68587 |  | 2022 | 106 | 15 | 1.2316 | 0.069034 | 0 | 1.3006 | 28.3252 | 1.3006 | 2022 | 73 | 10 | 0.99001 | 0.055498 | 0 | 1.0455 | 12.9127 | 1.0455 | 2022 | 170 | 25 | 2.2029 | 0.12333 | 0 | 2.3263 | 70.7092 | 2.3263
2023 | 200 | 12.6 | 0.66191 | 0.013238 | 11.2213 | 1.361 |  | 2023 | 160 | 23 | 2.5368 | 0.14067 | 0 | 2.6775 | 58.2386 | 2.6775 | 2023 | 114 | 17 | 1.6461 | 0.091499 | 0 | 1.7376 | 26.5494 | 1.7376 | 2023 | 502 | 71 | 6.8466 | 0.37352 | 0 | 7.2201 | 145.3835 | 7.2201
2024 | 0 | 0 | 0 | 0 | 0 | 1.361 |  | 2024 | 237 | 34 | 3.894 | 0.21347 | 0 | 4.1074 | 0 | 4.1074 | 2024 | 181 | 25 | 2.6869 | 0.14773 | 0 | 2.8347 | 0 | 2.8347 | 2024 | 762 | 108 | 10.9107 | 0.58014 | 0 | 11.4909 | 0 | 11.4909
2025 | 0 | 0 | 0 | 0 | 0 | 1.361 |  | 2025 | 244 | 35 | 4.0872 | 0.22047 | 0 | 4.3076 | 0 | 4.3076 | 2025 | 191 | 26 | 2.8358 | 0.14875 | 0 | 2.9845 | 0 | 2.9845 | 2025 | 844 | 120 | 12.1951 | 0.64197 | 0 | 12.8371 | 0 | 12.8371
2026 | 0 | 0 | 0 | 0 | 0 | 1.361 |  | 2026 | 321 | 45 | 5.7652 | 0.30945 | 0 | 6.0747 | 0 | 6.0747 | 2026 | 206 | 30 | 3.2255 | 0.1747 | 0 | 3.4002 | 0 | 3.4002 | 2026 | 1080 | 153 | 15.6452 | 0.81995 | 0 | 16.4652 | 0 | 16.4652
2027 | 0 | 0 | 0 | 0 | 0 | 1.361 |  | 2027 | 387 | 56 | 6.5766 | 0.35351 | 0 | 6.9301 | 0 | 6.9301 | 2027 | 200 | 29 | 2.866 | 0.15613 | 0 | 3.0222 | 0 | 3.0222 | 2027 | 1282 | 181 | 16.3681 | 0.86152 | 0 | 17.2296 | 0 | 17.2296
2028 | 0 | 0 | 0 | 0 | 0 | 1.361 |  | 2028 | 435 | 62 | 7.6112 | 0.40826 | 0 | 8.0195 | 0 | 8.0195 | 2028 | 205 | 29 | 2.9989 | 0.16308 | 0 | 3.162 | 0 | 3.162 | 2028 | 1396 | 197 | 17.8529 | 0.93601 | 0 | 18.7889 | 0 | 18.7889
Total | 400 | 25.4 | 1.3343 | 0.026687 | 22.1489 | 22.1489 |  | Total | 1948 | 279 | 32.5434 | 1.7621 | 0 | 34.3055 | 114.067 | 114.067 |  | 1221 | 174 | 17.9813 | 0.97848 | 0 | 18.9598 | 52 | 52 |  | 6095 | 863 | 82.773 | 4.3791 | 0 | 87.1521 | 284.7501 | 284.7501
High Cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 27.9122 |  | NPV | [7 empty] | 74.5201 | NPV | [7 empty] | 36.5689 | NPV | [7 empty] | 186.8993
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 8.32 | 0.57023 | 0.011405 | 7.424 | 0.58163 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 22.3629 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 10.1947 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 55.8255 | 0.79408
2022 | 100 | 8.32 | 0.57023 | 0.011405 | 7.5854 | 1.1633 |  | 2022 | 106 | 15 | 1.2316 | 0.069034 | 0 | 1.3006 | 22.8491 | 1.3006 | 2022 | 73 | 10 | 0.99001 | 0.055498 | 0 | 1.0455 | 10.4163 | 1.0455 | 2022 | 170 | 25 | 2.2029 | 0.12333 | 0 | 2.3263 | 57.0392 | 2.3263
2023 | 200 | 16.38 | 1.1226 | 0.022453 | 15.2335 | 2.3083 |  | 2023 | 160 | 23 | 2.5368 | 0.14067 | 0 | 2.6775 | 46.6156 | 2.6775 | 2023 | 114 | 17 | 1.6461 | 0.091499 | 0 | 1.7376 | 21.2508 | 1.7376 | 2023 | 502 | 71 | 6.8466 | 0.37352 | 0 | 7.2201 | 116.3685 | 7.2201
2024 | 0 | 0 | 0 | 0 | 0 | 2.3083 |  | 2024 | 237 | 34 | 3.894 | 0.21347 | 0 | 4.1074 | 0 | 4.1074 | 2024 | 181 | 25 | 2.6869 | 0.14773 | 0 | 2.8347 | 0 | 2.8347 | 2024 | 762 | 108 | 10.9107 | 0.58014 | 0 | 11.4909 | 0 | 11.4909
2025 | 0 | 0 | 0 | 0 | 0 | 2.3083 |  | 2025 | 244 | 35 | 4.0872 | 0.22047 | 0 | 4.3076 | 0 | 4.3076 | 2025 | 191 | 26 | 2.8358 | 0.14875 | 0 | 2.9845 | 0 | 2.9845 | 2025 | 844 | 120 | 12.1951 | 0.64197 | 0 | 12.8371 | 0 | 12.8371
2026 | 0 | 0 | 0 | 0 | 0 | 2.3083 |  | 2026 | 321 | 45 | 5.7652 | 0.30945 | 0 | 6.0747 | 0 | 6.0747 | 2026 | 206 | 30 | 3.2255 | 0.1747 | 0 | 3.4002 | 0 | 3.4002 | 2026 | 1080 | 153 | 15.6452 | 0.81995 | 0 | 16.4652 | 0 | 16.4652
2027 | 0 | 0 | 0 | 0 | 0 | 2.3083 |  | 2027 | 387 | 56 | 6.5766 | 0.35351 | 0 | 6.9301 | 0 | 6.9301 | 2027 | 200 | 29 | 2.866 | 0.15613 | 0 | 3.0222 | 0 | 3.0222 | 2027 | 1282 | 181 | 16.3681 | 0.86152 | 0 | 17.2296 | 0 | 17.2296
2028 | 0 | 0 | 0 | 0 | 0 | 2.3083 |  | 2028 | 435 | 62 | 7.6112 | 0.40826 | 0 | 8.0195 | 0 | 8.0195 | 2028 | 205 | 29 | 2.9989 | 0.16308 | 0 | 3.162 | 0 | 3.162 | 2028 | 1396 | 197 | 17.8529 | 0.93601 | 0 | 18.7889 | 0 | 18.7889
Total | 400 | 33.02 | 2.2631 | 0.045262 | 30.2428 | 30.2428 |  | Total | 1948 | 279 | 32.5434 | 1.7621 | 0 | 34.3055 | 91.8277 | 91.8277 |  | 1221 | 174 | 17.9813 | 0.97848 | 0 | 18.9598 | 41.8618 | 41.8618 |  | 6095 | 863 | 82.773 | 4.3791 | 0 | 87.1521 | 229.2332 | 229.2332
Low cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 15.0296 |  | NPV | [7 empty] | 74.5201 | NPV | [7 empty] | 36.5689 | NPV | [7 empty] | 186.8993
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 4.48 | 0.30704 | 0.0061409 | 3.9975 | 0.31319 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 22.3629 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 10.1947 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 55.8255 | 0.79408
2022 | 100 | 4.48 | 0.30704 | 0.0061409 | 4.0844 | 0.62637 |  | 2022 | 106 | 15 | 1.2316 | 0.069034 | 0 | 1.3006 | 22.8491 | 1.3006 | 2022 | 73 | 10 | 0.99001 | 0.055498 | 0 | 1.0455 | 10.4163 | 1.0455 | 2022 | 170 | 25 | 2.2029 | 0.12333 | 0 | 2.3263 | 57.0392 | 2.3263
2023 | 200 | 8.82 | 0.60449 | 0.01209 | 8.2026 | 1.243 |  | 2023 | 160 | 23 | 2.5368 | 0.14067 | 0 | 2.6775 | 46.6156 | 2.6775 | 2023 | 114 | 17 | 1.6461 | 0.091499 | 0 | 1.7376 | 21.2508 | 1.7376 | 2023 | 502 | 71 | 6.8466 | 0.37352 | 0 | 7.2201 | 116.3685 | 7.2201
2024 | 0 | 0 | 0 | 0 | 0 | 1.243 |  | 2024 | 237 | 34 | 3.894 | 0.21347 | 0 | 4.1074 | 0 | 4.1074 | 2024 | 181 | 25 | 2.6869 | 0.14773 | 0 | 2.8347 | 0 | 2.8347 | 2024 | 762 | 108 | 10.9107 | 0.58014 | 0 | 11.4909 | 0 | 11.4909
2025 | 0 | 0 | 0 | 0 | 0 | 1.243 |  | 2025 | 244 | 35 | 4.0872 | 0.22047 | 0 | 4.3076 | 0 | 4.3076 | 2025 | 191 | 26 | 2.8358 | 0.14875 | 0 | 2.9845 | 0 | 2.9845 | 2025 | 844 | 120 | 12.1951 | 0.64197 | 0 | 12.8371 | 0 | 12.8371
2026 | 0 | 0 | 0 | 0 | 0 | 1.243 |  | 2026 | 321 | 45 | 5.7652 | 0.30945 | 0 | 6.0747 | 0 | 6.0747 | 2026 | 206 | 30 | 3.2255 | 0.1747 | 0 | 3.4002 | 0 | 3.4002 | 2026 | 1080 | 153 | 15.6452 | 0.81995 | 0 | 16.4652 | 0 | 16.4652
2027 | 0 | 0 | 0 | 0 | 0 | 1.243 |  | 2027 | 387 | 56 | 6.5766 | 0.35351 | 0 | 6.9301 | 0 | 6.9301 | 2027 | 200 | 29 | 2.866 | 0.15613 | 0 | 3.0222 | 0 | 3.0222 | 2027 | 1282 | 181 | 16.3681 | 0.86152 | 0 | 17.2296 | 0 | 17.2296
2028 | 0 | 0 | 0 | 0 | 0 | 1.243 |  | 2028 | 435 | 62 | 7.6112 | 0.40826 | 0 | 8.0195 | 0 | 8.0195 | 2028 | 205 | 29 | 2.9989 | 0.16308 | 0 | 3.162 | 0 | 3.162 | 2028 | 1396 | 197 | 17.8529 | 0.93601 | 0 | 18.7889 | 0 | 18.7889
Total | 400 | 17.78 | 1.2186 | 0.024372 | 16.2846 | 16.2846 |  | Total | 1948 | 279 | 32.5434 | 1.7621 | 0 | 34.3055 | 91.8277 | 91.8277 |  | 1221 | 174 | 17.9813 | 0.97848 | 0 | 18.9598 | 41.8618 | 41.8618 |  | 6095 | 863 | 82.773 | 4.3791 | 0 | 87.1521 | 229.2332 | 229.2332

## Option 1C
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Neutral | Fast | Slow | Weighting_Base | Weighting_Fast | Weighting_Slow
Base | 6% | 100% | 31.7 | 26.8663 | 53.5098 | 13.8093 | 178.9044 | 74.9333 | 65.0082 | 106.282
High Discount rate | 8.5% | 100% | 31.7 | 24.9607 | 32.777 | 4.7914 | 123.0565 | 48.3505 | 41.3541 | 70.9204
Low Discount rate | 3.5% | 100% | 31.7 | 28.9775 | 87.6812 | 29.0789 | 269.2165 | 118.4145 | 103.7639 | 163.7983
High Cost | 6% | 130% | 31.7 | 34.9262 | 45.4499 | 5.7494 | 170.8445 | 66.8734 | 56.9483 | 98.2221
Low Cost | 6% | 70% | 31.7 | 18.8064 | 61.5697 | 21.8692 | 186.9643 | 82.9932 | 73.0681 | 114.3419
Base
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 26.8663 |  | NPV | [7 empty] | 80.3762 | NPV | [7 empty] | 40.6756 | NPV | [7 empty] | 205.7707
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.43863 | 0.0087727 | 5.7107 | 0.44741 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 19.3973 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 9.1306 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 49.22 | 0.79408
2022 | 200 | 12.7 | 0.87042 | 0.017408 | 11.5786 | 1.3352 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 39.638 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 18.6583 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 100.5801 | 2.9131
2023 | 200 | 12.6 | 0.86356 | 0.017271 | 11.7181 | 2.2161 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 40.4337 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 19.0328 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 102.5991 | 7.7544
2024 | 0 | 0 | 0 | 0 | 0 | 2.2161 |  | 2024 | 269 | 39 | 4.0258 | 0.22066 | 0 | 4.2464 | 0 | 4.2464 | 2024 | 200 | 29 | 2.958 | 0.16263 | 0 | 3.1207 | 0 | 3.1207 | 2024 | 840 | 119 | 12.0167 | 0.63984 | 0 | 12.6565 | 0 | 12.6565
2025 | 0 | 0 | 0 | 0 | 0 | 2.2161 |  | 2025 | 287 | 41 | 4.3053 | 0.23232 | 0 | 4.5376 | 0 | 4.5376 | 2025 | 205 | 30 | 3.0464 | 0.16569 | 0 | 3.2121 | 0 | 3.2121 | 2025 | 919 | 131 | 13.272 | 0.69963 | 0 | 13.9716 | 0 | 13.9716
2026 | 0 | 0 | 0 | 0 | 0 | 2.2161 |  | 2026 | 389 | 55 | 6.1603 | 0.33075 | 0 | 6.4911 | 0 | 6.4911 | 2026 | 232 | 33 | 3.616 | 0.19589 | 0 | 3.8119 | 0 | 3.8119 | 2026 | 1185 | 168 | 17.1496 | 0.90031 | 0 | 18.0499 | 0 | 18.0499
2027 | 0 | 0 | 0 | 0 | 0 | 2.2161 |  | 2027 | 486 | 70 | 7.1431 | 0.38409 | 0 | 7.5272 | 0 | 7.5272 | 2027 | 225 | 32 | 3.2225 | 0.17558 | 0 | 3.3981 | 0 | 3.3981 | 2027 | 1411 | 199 | 18.0089 | 0.94925 | 0 | 18.9582 | 0 | 18.9582
2028 | 0 | 0 | 0 | 0 | 0 | 2.2161 |  | 2028 | 555 | 80 | 8.3299 | 0.447 | 0 | 8.7769 | 0 | 8.7769 | 2028 | 228 | 32 | 3.3381 | 0.18194 | 0 | 3.5201 | 0 | 3.5201 | 2028 | 1549 | 219 | 19.7942 | 1.0397 | 0 | 20.8339 | 0 | 20.8339
Total | 500 | 31.7 | 2.1726 | 0.043452 | 29.0074 | 29.0074 |  | Total | 2327 | 334 | 34.8283 | 1.8858 | 0 | 36.7141 | 99.4689 | 99.4689 |  | 1348 | 194 | 19.8301 | 1.0854 | 0 | 20.9155 | 46.8218 | 46.8218 |  | 6714 | 951 | 91.1049 | 4.8268 | 0 | 95.9317 | 252.3992 | 252.3992
High Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 24.9607 |  | NPV | [7 empty] | 57.7377 | NPV | [7 empty] | 29.7521 | NPV | [7 empty] | 148.0172
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.54887 | 0.010977 | 5.9588 | 0.55985 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 16.1749 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 7.6138 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 41.0432 | 0.79408
2022 | 200 | 12.7 | 1.0892 | 0.021783 | 12.0091 | 1.6708 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 32.8548 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 15.4653 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 83.368 | 2.9131
2023 | 200 | 12.6 | 1.0806 | 0.021612 | 12.0833 | 2.773 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 33.3202 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 15.6844 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 84.5491 | 7.7544
2024 | 0 | 0 | 0 | 0 | 0 | 2.773 |  | 2024 | 269 | 39 | 4.0258 | 0.22066 | 0 | 4.2464 | 0 | 4.2464 | 2024 | 200 | 29 | 2.958 | 0.16263 | 0 | 3.1207 | 0 | 3.1207 | 2024 | 840 | 119 | 12.0167 | 0.63984 | 0 | 12.6565 | 0 | 12.6565
2025 | 0 | 0 | 0 | 0 | 0 | 2.773 |  | 2025 | 287 | 41 | 4.3053 | 0.23232 | 0 | 4.5376 | 0 | 4.5376 | 2025 | 205 | 30 | 3.0464 | 0.16569 | 0 | 3.2121 | 0 | 3.2121 | 2025 | 919 | 131 | 13.272 | 0.69963 | 0 | 13.9716 | 0 | 13.9716
2026 | 0 | 0 | 0 | 0 | 0 | 2.773 |  | 2026 | 389 | 55 | 6.1603 | 0.33075 | 0 | 6.4911 | 0 | 6.4911 | 2026 | 232 | 33 | 3.616 | 0.19589 | 0 | 3.8119 | 0 | 3.8119 | 2026 | 1185 | 168 | 17.1496 | 0.90031 | 0 | 18.0499 | 0 | 18.0499
2027 | 0 | 0 | 0 | 0 | 0 | 2.773 |  | 2027 | 486 | 70 | 7.1431 | 0.38409 | 0 | 7.5272 | 0 | 7.5272 | 2027 | 225 | 32 | 3.2225 | 0.17558 | 0 | 3.3981 | 0 | 3.3981 | 2027 | 1411 | 199 | 18.0089 | 0.94925 | 0 | 18.9582 | 0 | 18.9582
2028 | 0 | 0 | 0 | 0 | 0 | 2.773 |  | 2028 | 555 | 80 | 8.3299 | 0.447 | 0 | 8.7769 | 0 | 8.7769 | 2028 | 228 | 32 | 3.3381 | 0.18194 | 0 | 3.5201 | 0 | 3.5201 | 2028 | 1549 | 219 | 19.7942 | 1.0397 | 0 | 20.8339 | 0 | 20.8339
Total | 500 | 31.7 | 2.7186 | 0.054372 | 30.0513 | 30.0513 |  | Total | 2327 | 334 | 34.8283 | 1.8858 | 0 | 36.7141 | 82.3499 | 82.3499 |  | 1348 | 194 | 19.8301 | 1.0854 | 0 | 20.9155 | 38.7636 | 38.7636 |  | 6714 | 951 | 91.1049 | 4.8268 | 0 | 95.9317 | 208.9603 | 208.9603
Low Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 28.9775 |  | NPV | [7 empty] | 116.6587 | NPV | [7 empty] | 58.0564 | NPV | [7 empty] | 298.194
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.33621 | 0.0067242 | 5.3834 | 0.34293 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 23.8558 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 11.2294 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 60.5334 | 0.79408
2022 | 200 | 12.7 | 0.66717 | 0.013343 | 11.0019 | 1.0234 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 49.1376 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 23.1299 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 124.6851 | 2.9131
2023 | 200 | 12.6 | 0.66191 | 0.013238 | 11.2213 | 1.6986 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 50.5153 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 23.7784 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 128.181 | 7.7544
2024 | 0 | 0 | 0 | 0 | 0 | 1.6986 |  | 2024 | 269 | 39 | 4.0258 | 0.22066 | 0 | 4.2464 | 0 | 4.2464 | 2024 | 200 | 29 | 2.958 | 0.16263 | 0 | 3.1207 | 0 | 3.1207 | 2024 | 840 | 119 | 12.0167 | 0.63984 | 0 | 12.6565 | 0 | 12.6565
2025 | 0 | 0 | 0 | 0 | 0 | 1.6986 |  | 2025 | 287 | 41 | 4.3053 | 0.23232 | 0 | 4.5376 | 0 | 4.5376 | 2025 | 205 | 30 | 3.0464 | 0.16569 | 0 | 3.2121 | 0 | 3.2121 | 2025 | 919 | 131 | 13.272 | 0.69963 | 0 | 13.9716 | 0 | 13.9716
2026 | 0 | 0 | 0 | 0 | 0 | 1.6986 |  | 2026 | 389 | 55 | 6.1603 | 0.33075 | 0 | 6.4911 | 0 | 6.4911 | 2026 | 232 | 33 | 3.616 | 0.19589 | 0 | 3.8119 | 0 | 3.8119 | 2026 | 1185 | 168 | 17.1496 | 0.90031 | 0 | 18.0499 | 0 | 18.0499
2027 | 0 | 0 | 0 | 0 | 0 | 1.6986 |  | 2027 | 486 | 70 | 7.1431 | 0.38409 | 0 | 7.5272 | 0 | 7.5272 | 2027 | 225 | 32 | 3.2225 | 0.17558 | 0 | 3.3981 | 0 | 3.3981 | 2027 | 1411 | 199 | 18.0089 | 0.94925 | 0 | 18.9582 | 0 | 18.9582
2028 | 0 | 0 | 0 | 0 | 0 | 1.6986 |  | 2028 | 555 | 80 | 8.3299 | 0.447 | 0 | 8.7769 | 0 | 8.7769 | 2028 | 228 | 32 | 3.3381 | 0.18194 | 0 | 3.5201 | 0 | 3.5201 | 2028 | 1549 | 219 | 19.7942 | 1.0397 | 0 | 20.8339 | 0 | 20.8339
Total | 500 | 31.7 | 1.6653 | 0.033306 | 27.6065 | 27.6065 |  | Total | 2327 | 334 | 34.8283 | 1.8858 | 0 | 36.7141 | 123.5087 | 123.5087 |  | 1348 | 194 | 19.8301 | 1.0854 | 0 | 20.9155 | 58.1377 | 58.1377 |  | 6714 | 951 | 91.1049 | 4.8268 | 0 | 95.9317 | 313.3995 | 313.3995
High Cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 34.9262 |  | NPV | [7 empty] | 80.3762 | NPV | [7 empty] | 40.6756 | NPV | [7 empty] | 205.7707
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 8.32 | 0.57023 | 0.011405 | 7.424 | 0.58163 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 19.3973 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 9.1306 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 49.22 | 0.79408
2022 | 200 | 16.51 | 1.1315 | 0.022631 | 15.0522 | 1.7358 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 39.638 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 18.6583 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 100.5801 | 2.9131
2023 | 200 | 16.38 | 1.1226 | 0.022453 | 15.2335 | 2.8809 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 40.4337 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 19.0328 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 102.5991 | 7.7544
2024 | 0 | 0 | 0 | 0 | 0 | 2.8809 |  | 2024 | 269 | 39 | 4.0258 | 0.22066 | 0 | 4.2464 | 0 | 4.2464 | 2024 | 200 | 29 | 2.958 | 0.16263 | 0 | 3.1207 | 0 | 3.1207 | 2024 | 840 | 119 | 12.0167 | 0.63984 | 0 | 12.6565 | 0 | 12.6565
2025 | 0 | 0 | 0 | 0 | 0 | 2.8809 |  | 2025 | 287 | 41 | 4.3053 | 0.23232 | 0 | 4.5376 | 0 | 4.5376 | 2025 | 205 | 30 | 3.0464 | 0.16569 | 0 | 3.2121 | 0 | 3.2121 | 2025 | 919 | 131 | 13.272 | 0.69963 | 0 | 13.9716 | 0 | 13.9716
2026 | 0 | 0 | 0 | 0 | 0 | 2.8809 |  | 2026 | 389 | 55 | 6.1603 | 0.33075 | 0 | 6.4911 | 0 | 6.4911 | 2026 | 232 | 33 | 3.616 | 0.19589 | 0 | 3.8119 | 0 | 3.8119 | 2026 | 1185 | 168 | 17.1496 | 0.90031 | 0 | 18.0499 | 0 | 18.0499
2027 | 0 | 0 | 0 | 0 | 0 | 2.8809 |  | 2027 | 486 | 70 | 7.1431 | 0.38409 | 0 | 7.5272 | 0 | 7.5272 | 2027 | 225 | 32 | 3.2225 | 0.17558 | 0 | 3.3981 | 0 | 3.3981 | 2027 | 1411 | 199 | 18.0089 | 0.94925 | 0 | 18.9582 | 0 | 18.9582
2028 | 0 | 0 | 0 | 0 | 0 | 2.8809 |  | 2028 | 555 | 80 | 8.3299 | 0.447 | 0 | 8.7769 | 0 | 8.7769 | 2028 | 228 | 32 | 3.3381 | 0.18194 | 0 | 3.5201 | 0 | 3.5201 | 2028 | 1549 | 219 | 19.7942 | 1.0397 | 0 | 20.8339 | 0 | 20.8339
Total | 500 | 41.21 | 2.8244 | 0.056488 | 37.7097 | 37.7097 |  | Total | 2327 | 334 | 34.8283 | 1.8858 | 0 | 36.7141 | 99.4689 | 99.4689 |  | 1348 | 194 | 19.8301 | 1.0854 | 0 | 20.9155 | 46.8218 | 46.8218 |  | 6714 | 951 | 91.1049 | 4.8268 | 0 | 95.9317 | 252.3992 | 252.3992
Low cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 18.8064 |  | NPV | [7 empty] | 80.3762 | NPV | [7 empty] | 40.6756 | NPV | [7 empty] | 205.7707
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 4.48 | 0.30704 | 0.0061409 | 3.9975 | 0.31319 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 19.3973 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 9.1306 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 49.22 | 0.79408
2022 | 200 | 8.89 | 0.60929 | 0.012186 | 8.105 | 0.93466 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 39.638 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 18.6583 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 100.5801 | 2.9131
2023 | 200 | 8.82 | 0.60449 | 0.01209 | 8.2026 | 1.5512 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 40.4337 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 19.0328 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 102.5991 | 7.7544
2024 | 0 | 0 | 0 | 0 | 0 | 1.5512 |  | 2024 | 269 | 39 | 4.0258 | 0.22066 | 0 | 4.2464 | 0 | 4.2464 | 2024 | 200 | 29 | 2.958 | 0.16263 | 0 | 3.1207 | 0 | 3.1207 | 2024 | 840 | 119 | 12.0167 | 0.63984 | 0 | 12.6565 | 0 | 12.6565
2025 | 0 | 0 | 0 | 0 | 0 | 1.5512 |  | 2025 | 287 | 41 | 4.3053 | 0.23232 | 0 | 4.5376 | 0 | 4.5376 | 2025 | 205 | 30 | 3.0464 | 0.16569 | 0 | 3.2121 | 0 | 3.2121 | 2025 | 919 | 131 | 13.272 | 0.69963 | 0 | 13.9716 | 0 | 13.9716
2026 | 0 | 0 | 0 | 0 | 0 | 1.5512 |  | 2026 | 389 | 55 | 6.1603 | 0.33075 | 0 | 6.4911 | 0 | 6.4911 | 2026 | 232 | 33 | 3.616 | 0.19589 | 0 | 3.8119 | 0 | 3.8119 | 2026 | 1185 | 168 | 17.1496 | 0.90031 | 0 | 18.0499 | 0 | 18.0499
2027 | 0 | 0 | 0 | 0 | 0 | 1.5512 |  | 2027 | 486 | 70 | 7.1431 | 0.38409 | 0 | 7.5272 | 0 | 7.5272 | 2027 | 225 | 32 | 3.2225 | 0.17558 | 0 | 3.3981 | 0 | 3.3981 | 2027 | 1411 | 199 | 18.0089 | 0.94925 | 0 | 18.9582 | 0 | 18.9582
2028 | 0 | 0 | 0 | 0 | 0 | 1.5512 |  | 2028 | 555 | 80 | 8.3299 | 0.447 | 0 | 8.7769 | 0 | 8.7769 | 2028 | 228 | 32 | 3.3381 | 0.18194 | 0 | 3.5201 | 0 | 3.5201 | 2028 | 1549 | 219 | 19.7942 | 1.0397 | 0 | 20.8339 | 0 | 20.8339
Total | 500 | 22.19 | 1.5208 | 0.030417 | 20.3052 | 20.3052 |  | Total | 2327 | 334 | 34.8283 | 1.8858 | 0 | 36.7141 | 99.4689 | 99.4689 |  | 1348 | 194 | 19.8301 | 1.0854 | 0 | 20.9155 | 46.8218 | 46.8218 |  | 6714 | 951 | 91.1049 | 4.8268 | 0 | 95.9317 | 252.3992 | 252.3992

## Option 1D
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Neutral | Fast | Slow | Weighting_Base | Weighting_Fast | Weighting_Slow
Base | 6% | 100% | 38.8 | 32.278 | 51.3734 | 10.7997 | 185.2226 | 74.6923 | 64.5489 | 108.1546
High Discount rate | 8.5% | 100% | 38.8 | 29.777 | 30.1602 | 1.6461 | 126.3363 | 47.0757 | 39.9472 | 71.1197
Low Discount rate | 3.5% | 100% | 38.8 | 35.0751 | 86.7179 | 26.613 | 280.9958 | 120.2611 | 105.2349 | 168.8306
High Cost | 6% | 130% | 38.8 | 41.9613 | 41.69 | 1.1163 | 175.5392 | 65.0089 | 54.8655 | 98.4712
Low Cost | 6% | 70% | 38.8 | 22.5946 | 61.0568 | 20.4831 | 194.906 | 84.3757 | 74.2323 | 117.838
Base
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 32.278 |  | NPV | [7 empty] | 83.6514 | NPV | [7 empty] | 43.0777 | NPV | [7 empty] | 217.5006
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.43863 | 0.0087727 | 5.7107 | 0.44741 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 16.8253 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 8.0689 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 43.2962 | 0.79408
2022 | 200 | 12.7 | 0.87042 | 0.017408 | 11.5786 | 1.3352 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 34.3821 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 16.4887 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 88.4749 | 2.9131
2023 | 200 | 12.6 | 0.86356 | 0.017271 | 11.7181 | 2.2161 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 35.0723 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 16.8197 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 90.251 | 7.7544
2024 | 100 | 7.1 | 0.48661 | 0.0097322 | 6.7256 | 2.7124 |  | 2024 | 272 | 39 | 4.0674 | 0.22294 | 0 | 4.2903 | 17.8617 | 4.2903 | 2024 | 210 | 30 | 3.1112 | 0.17107 | 0 | 3.2822 | 8.566 | 3.2822 | 2024 | 887 | 126 | 12.6872 | 0.67614 | 0 | 13.3634 | 45.9633 | 13.3634
2025 | 0 | 0 | 0 | 0 | 0 | 2.7124 |  | 2025 | 292 | 42 | 4.3789 | 0.23632 | 0 | 4.6152 | 0 | 4.6152 | 2025 | 217 | 31 | 3.2212 | 0.17521 | 0 | 3.3964 | 0 | 3.3964 | 2025 | 965 | 137 | 13.9362 | 0.73508 | 0 | 14.6712 | 0 | 14.6712
2026 | 0 | 0 | 0 | 0 | 0 | 2.7124 |  | 2026 | 401 | 57 | 6.3548 | 0.34116 | 0 | 6.696 | 0 | 6.696 | 2026 | 246 | 35 | 3.8377 | 0.2079 | 0 | 4.0456 | 0 | 4.0456 | 2026 | 1243 | 176 | 17.9914 | 0.94525 | 0 | 18.9366 | 0 | 18.9366
2027 | 0 | 0 | 0 | 0 | 0 | 2.7124 |  | 2027 | 507 | 73 | 7.4606 | 0.40126 | 0 | 7.8619 | 0 | 7.8619 | 2027 | 238 | 34 | 3.4162 | 0.18613 | 0 | 3.6024 | 0 | 3.6024 | 2027 | 1491 | 210 | 19.0152 | 1.0033 | 0 | 20.0185 | 0 | 20.0185
2028 | 0 | 0 | 0 | 0 | 0 | 2.7124 |  | 2028 | 580 | 83 | 8.7021 | 0.46712 | 0 | 9.1692 | 0 | 9.1692 | 2028 | 242 | 34 | 3.538 | 0.19284 | 0 | 3.7309 | 0 | 3.7309 | 2028 | 1643 | 232 | 20.9974 | 1.104 | 0 | 22.1014 | 0 | 22.1014
Total | 600 | 38.8 | 2.6592 | 0.053184 | 35.7331 | 35.7331 |  | Total | 2393 | 343 | 35.8279 | 1.9398 | 0 | 37.7677 | 104.1415 | 104.1415 |  | 1411 | 202 | 20.7733 | 1.1368 | 0 | 21.9101 | 49.9433 | 49.9433 |  | 7039 | 996 | 95.4909 | 5.0619 | 0 | 100.5528 | 267.9853 | 267.9853
High Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 29.777 |  | NPV | [7 empty] | 59.9372 | NPV | [7 empty] | 31.4231 | NPV | [7 empty] | 156.1133
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.54887 | 0.010977 | 5.9588 | 0.55985 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 14.0302 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 6.7285 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 36.1035 | 0.79408
2022 | 200 | 12.7 | 1.0892 | 0.021783 | 12.0091 | 1.6708 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 28.4984 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 13.667 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 73.3344 | 2.9131
2023 | 200 | 12.6 | 1.0806 | 0.021612 | 12.0833 | 2.773 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 28.9021 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 13.8607 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 74.3733 | 7.7544
2024 | 100 | 7.1 | 0.6089 | 0.012178 | 6.8965 | 3.3941 |  | 2024 | 272 | 39 | 4.0674 | 0.22294 | 0 | 4.2903 | 14.6371 | 4.2903 | 2024 | 210 | 30 | 3.1112 | 0.17107 | 0 | 3.2822 | 7.0196 | 3.2822 | 2024 | 887 | 126 | 12.6872 | 0.67614 | 0 | 13.3634 | 37.6655 | 13.3634
2025 | 0 | 0 | 0 | 0 | 0 | 3.3941 |  | 2025 | 292 | 42 | 4.3789 | 0.23632 | 0 | 4.6152 | 0 | 4.6152 | 2025 | 217 | 31 | 3.2212 | 0.17521 | 0 | 3.3964 | 0 | 3.3964 | 2025 | 965 | 137 | 13.9362 | 0.73508 | 0 | 14.6712 | 0 | 14.6712
2026 | 0 | 0 | 0 | 0 | 0 | 3.3941 |  | 2026 | 401 | 57 | 6.3548 | 0.34116 | 0 | 6.696 | 0 | 6.696 | 2026 | 246 | 35 | 3.8377 | 0.2079 | 0 | 4.0456 | 0 | 4.0456 | 2026 | 1243 | 176 | 17.9914 | 0.94525 | 0 | 18.9366 | 0 | 18.9366
2027 | 0 | 0 | 0 | 0 | 0 | 3.3941 |  | 2027 | 507 | 73 | 7.4606 | 0.40126 | 0 | 7.8619 | 0 | 7.8619 | 2027 | 238 | 34 | 3.4162 | 0.18613 | 0 | 3.6024 | 0 | 3.6024 | 2027 | 1491 | 210 | 19.0152 | 1.0033 | 0 | 20.0185 | 0 | 20.0185
2028 | 0 | 0 | 0 | 0 | 0 | 3.3941 |  | 2028 | 580 | 83 | 8.7021 | 0.46712 | 0 | 9.1692 | 0 | 9.1692 | 2028 | 242 | 34 | 3.538 | 0.19284 | 0 | 3.7309 | 0 | 3.7309 | 2028 | 1643 | 232 | 20.9974 | 1.104 | 0 | 22.1014 | 0 | 22.1014
Total | 600 | 38.8 | 3.3275 | 0.06655 | 36.9478 | 36.9478 |  | Total | 2393 | 343 | 35.8279 | 1.9398 | 0 | 37.7677 | 86.0678 | 86.0678 |  | 1411 | 202 | 20.7733 | 1.1368 | 0 | 21.9101 | 41.2757 | 41.2757 |  | 7039 | 996 | 95.4909 | 5.0619 | 0 | 100.5528 | 221.4767 | 221.4767
Low Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 35.0751 |  | NPV | [7 empty] | 121.7929 | NPV | [7 empty] | 61.688 | NPV | [7 empty] | 316.0709
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.33621 | 0.0067242 | 5.3834 | 0.34293 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 20.6927 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 9.9236 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 53.248 | 0.79408
2022 | 200 | 12.7 | 0.66717 | 0.013343 | 11.0019 | 1.0234 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 42.6222 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 20.4404 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 109.6788 | 2.9131
2023 | 200 | 12.6 | 0.66191 | 0.013238 | 11.2213 | 1.6986 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 43.8172 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 21.0135 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 112.7539 | 7.7544
2024 | 100 | 7.1 | 0.37298 | 0.0074596 | 6.4897 | 2.079 |  | 2024 | 272 | 39 | 4.0674 | 0.22294 | 0 | 4.2903 | 22.4859 | 4.2903 | 2024 | 210 | 30 | 3.1112 | 0.17107 | 0 | 3.2822 | 10.7836 | 3.2822 | 2024 | 887 | 126 | 12.6872 | 0.67614 | 0 | 13.3634 | 57.8625 | 13.3634
2025 | 0 | 0 | 0 | 0 | 0 | 2.079 |  | 2025 | 292 | 42 | 4.3789 | 0.23632 | 0 | 4.6152 | 0 | 4.6152 | 2025 | 217 | 31 | 3.2212 | 0.17521 | 0 | 3.3964 | 0 | 3.3964 | 2025 | 965 | 137 | 13.9362 | 0.73508 | 0 | 14.6712 | 0 | 14.6712
2026 | 0 | 0 | 0 | 0 | 0 | 2.079 |  | 2026 | 401 | 57 | 6.3548 | 0.34116 | 0 | 6.696 | 0 | 6.696 | 2026 | 246 | 35 | 3.8377 | 0.2079 | 0 | 4.0456 | 0 | 4.0456 | 2026 | 1243 | 176 | 17.9914 | 0.94525 | 0 | 18.9366 | 0 | 18.9366
2027 | 0 | 0 | 0 | 0 | 0 | 2.079 |  | 2027 | 507 | 73 | 7.4606 | 0.40126 | 0 | 7.8619 | 0 | 7.8619 | 2027 | 238 | 34 | 3.4162 | 0.18613 | 0 | 3.6024 | 0 | 3.6024 | 2027 | 1491 | 210 | 19.0152 | 1.0033 | 0 | 20.0185 | 0 | 20.0185
2028 | 0 | 0 | 0 | 0 | 0 | 2.079 |  | 2028 | 580 | 83 | 8.7021 | 0.46712 | 0 | 9.1692 | 0 | 9.1692 | 2028 | 242 | 34 | 3.538 | 0.19284 | 0 | 3.7309 | 0 | 3.7309 | 2028 | 1643 | 232 | 20.9974 | 1.104 | 0 | 22.1014 | 0 | 22.1014
Total | 600 | 38.8 | 2.0383 | 0.040765 | 34.0962 | 34.0962 |  | Total | 2393 | 343 | 35.8279 | 1.9398 | 0 | 37.7677 | 129.6179 | 129.6179 |  | 1411 | 202 | 20.7733 | 1.1368 | 0 | 21.9101 | 62.1611 | 62.1611 |  | 7039 | 996 | 95.4909 | 5.0619 | 0 | 100.5528 | 333.5433 | 333.5433
High Cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 41.9613 |  | NPV | [7 empty] | 83.6514 | NPV | [7 empty] | 43.0777 | NPV | [7 empty] | 217.5006
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 8.32 | 0.57023 | 0.011405 | 7.424 | 0.58163 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 16.8253 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 8.0689 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 43.2962 | 0.79408
2022 | 200 | 16.51 | 1.1315 | 0.022631 | 15.0522 | 1.7358 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 34.3821 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 16.4887 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 88.4749 | 2.9131
2023 | 200 | 16.38 | 1.1226 | 0.022453 | 15.2335 | 2.8809 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 35.0723 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 16.8197 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 90.251 | 7.7544
2024 | 100 | 9.23 | 0.63259 | 0.012652 | 8.7433 | 3.5261 |  | 2024 | 272 | 39 | 4.0674 | 0.22294 | 0 | 4.2903 | 17.8617 | 4.2903 | 2024 | 210 | 30 | 3.1112 | 0.17107 | 0 | 3.2822 | 8.566 | 3.2822 | 2024 | 887 | 126 | 12.6872 | 0.67614 | 0 | 13.3634 | 45.9633 | 13.3634
2025 | 0 | 0 | 0 | 0 | 0 | 3.5261 |  | 2025 | 292 | 42 | 4.3789 | 0.23632 | 0 | 4.6152 | 0 | 4.6152 | 2025 | 217 | 31 | 3.2212 | 0.17521 | 0 | 3.3964 | 0 | 3.3964 | 2025 | 965 | 137 | 13.9362 | 0.73508 | 0 | 14.6712 | 0 | 14.6712
2026 | 0 | 0 | 0 | 0 | 0 | 3.5261 |  | 2026 | 401 | 57 | 6.3548 | 0.34116 | 0 | 6.696 | 0 | 6.696 | 2026 | 246 | 35 | 3.8377 | 0.2079 | 0 | 4.0456 | 0 | 4.0456 | 2026 | 1243 | 176 | 17.9914 | 0.94525 | 0 | 18.9366 | 0 | 18.9366
2027 | 0 | 0 | 0 | 0 | 0 | 3.5261 |  | 2027 | 507 | 73 | 7.4606 | 0.40126 | 0 | 7.8619 | 0 | 7.8619 | 2027 | 238 | 34 | 3.4162 | 0.18613 | 0 | 3.6024 | 0 | 3.6024 | 2027 | 1491 | 210 | 19.0152 | 1.0033 | 0 | 20.0185 | 0 | 20.0185
2028 | 0 | 0 | 0 | 0 | 0 | 3.5261 |  | 2028 | 580 | 83 | 8.7021 | 0.46712 | 0 | 9.1692 | 0 | 9.1692 | 2028 | 242 | 34 | 3.538 | 0.19284 | 0 | 3.7309 | 0 | 3.7309 | 2028 | 1643 | 232 | 20.9974 | 1.104 | 0 | 22.1014 | 0 | 22.1014
Total | 600 | 50.44 | 3.457 | 0.06914 | 46.453 | 46.453 |  | Total | 2393 | 343 | 35.8279 | 1.9398 | 0 | 37.7677 | 104.1415 | 104.1415 |  | 1411 | 202 | 20.7733 | 1.1368 | 0 | 21.9101 | 49.9433 | 49.9433 |  | 7039 | 996 | 95.4909 | 5.0619 | 0 | 100.5528 | 267.9853 | 267.9853
Low cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 22.5946 |  | NPV | [7 empty] | 83.6514 | NPV | [7 empty] | 43.0777 | NPV | [7 empty] | 217.5006
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 4.48 | 0.30704 | 0.0061409 | 3.9975 | 0.31319 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 16.8253 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 8.0689 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 43.2962 | 0.79408
2022 | 200 | 8.89 | 0.60929 | 0.012186 | 8.105 | 0.93466 |  | 2022 | 106 | 15 | 1.4412 | 0.080576 | 0 | 1.5218 | 34.3821 | 1.5218 | 2022 | 82 | 12 | 1.1199 | 0.062699 | 0 | 1.1826 | 16.4887 | 1.1826 | 2022 | 212 | 31 | 2.7591 | 0.15406 | 0 | 2.9131 | 88.4749 | 2.9131
2023 | 200 | 8.82 | 0.60449 | 0.01209 | 8.2026 | 1.5512 |  | 2023 | 177 | 25 | 2.582 | 0.14316 | 0 | 2.7252 | 35.0723 | 2.7252 | 2023 | 125 | 18 | 1.797 | 0.099881 | 0 | 1.8969 | 16.8197 | 1.8969 | 2023 | 539 | 76 | 7.353 | 0.40136 | 0 | 7.7544 | 90.251 | 7.7544
2024 | 100 | 4.97 | 0.34063 | 0.0068125 | 4.7079 | 1.8987 |  | 2024 | 272 | 39 | 4.0674 | 0.22294 | 0 | 4.2903 | 17.8617 | 4.2903 | 2024 | 210 | 30 | 3.1112 | 0.17107 | 0 | 3.2822 | 8.566 | 3.2822 | 2024 | 887 | 126 | 12.6872 | 0.67614 | 0 | 13.3634 | 45.9633 | 13.3634
2025 | 0 | 0 | 0 | 0 | 0 | 1.8987 |  | 2025 | 292 | 42 | 4.3789 | 0.23632 | 0 | 4.6152 | 0 | 4.6152 | 2025 | 217 | 31 | 3.2212 | 0.17521 | 0 | 3.3964 | 0 | 3.3964 | 2025 | 965 | 137 | 13.9362 | 0.73508 | 0 | 14.6712 | 0 | 14.6712
2026 | 0 | 0 | 0 | 0 | 0 | 1.8987 |  | 2026 | 401 | 57 | 6.3548 | 0.34116 | 0 | 6.696 | 0 | 6.696 | 2026 | 246 | 35 | 3.8377 | 0.2079 | 0 | 4.0456 | 0 | 4.0456 | 2026 | 1243 | 176 | 17.9914 | 0.94525 | 0 | 18.9366 | 0 | 18.9366
2027 | 0 | 0 | 0 | 0 | 0 | 1.8987 |  | 2027 | 507 | 73 | 7.4606 | 0.40126 | 0 | 7.8619 | 0 | 7.8619 | 2027 | 238 | 34 | 3.4162 | 0.18613 | 0 | 3.6024 | 0 | 3.6024 | 2027 | 1491 | 210 | 19.0152 | 1.0033 | 0 | 20.0185 | 0 | 20.0185
2028 | 0 | 0 | 0 | 0 | 0 | 1.8987 |  | 2028 | 580 | 83 | 8.7021 | 0.46712 | 0 | 9.1692 | 0 | 9.1692 | 2028 | 242 | 34 | 3.538 | 0.19284 | 0 | 3.7309 | 0 | 3.7309 | 2028 | 1643 | 232 | 20.9974 | 1.104 | 0 | 22.1014 | 0 | 22.1014
Total | 600 | 27.16 | 1.8615 | 0.037229 | 25.0131 | 25.0131 |  | Total | 2393 | 343 | 35.8279 | 1.9398 | 0 | 37.7677 | 104.1415 | 104.1415 |  | 1411 | 202 | 20.7733 | 1.1368 | 0 | 21.9101 | 49.9433 | 49.9433 |  | 7039 | 996 | 95.4909 | 5.0619 | 0 | 100.5528 | 267.9853 | 267.9853

## Option 2
|  |  | Cost $M (2019-2020) | NPV Cost $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M | Net Benefits NPV $M
Sensitivity | Discount rate | Cost | Capital Cost | Capital + O&M + Outage | Neutral | Fast | Slow | Weighting_Base | Weighting_Fast | Weighting_Slow
Base | 6% | 100% | 84.7 | 72.2561 | 64.9033 | 18.4927 | 208.6975 | 89.2492 | 77.6465 | 125.1978
High Discount rate | 8.5% | 100% | 84.7 | 67.2847 | 32.9347 | -0.20351 | 137.0376 | 50.6759 | 42.3913 | 76.7016
Low Discount rate | 3.5% | 100% | 84.7 | 77.7365 | 118.2689 | 50.5302 | 325.3518 | 153.105 | 136.1703 | 204.8757
High Cost | 6% | 130% | 84.7 | 93.933 | 43.2264 | -3.1842 | 187.0207 | 67.5723 | 55.9697 | 103.5209
Low Cost | 6% | 70% | 84.7 | 50.5793 | 86.5801 | 40.1695 | 230.3744 | 110.926 | 99.3234 | 146.8746
Base
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 72.2561 |  | NPV | [7 empty] | 137.1594 | NPV | [7 empty] | 90.7488 | NPV | [7 empty] | 280.9537
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.43863 | 0.0087727 | 5.7107 | 0.44741 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 31.0105 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 19.5362 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 64.3943 | 0.79408
2022 | 200 | 65.7 | 4.5029 | 0.090057 | 59.8989 | 5.0403 |  | 2022 | 194 | 26 | 2.8513 | 0.14355 | 4.2381 | 7.233 | 63.3693 | 7.233 | 2022 | 211 | 28 | 3.1593 | 0.15615 | 3.835 | 7.1504 | 39.9218 | 7.1504 | 2022 | 296 | 41 | 4.199 | 0.21303 | 5.0562 | 9.4683 | 131.5885 | 9.4683
2023 | 200 | 12.6 | 0.86356 | 0.017271 | 11.7181 | 5.9212 |  | 2023 | 282 | 39 | 4.229 | 0.21866 | 5.3476 | 9.7953 | 64.6414 | 9.7953 | 2023 | 241 | 33 | 3.6633 | 0.18582 | 0.95014 | 4.7992 | 40.7232 | 4.7992 | 2023 | 688 | 94 | 9.7696 | 0.50078 | 3.7069 | 13.9773 | 134.2301 | 13.9773
2024 | 0 | 0 | 0 | 0 | 0 | 5.9212 |  | 2024 | 404 | 57 | 6.1558 | 0.31791 | -1.0685 | 5.4052 | 0 | 5.4052 | 2024 | 356 | 47 | 5.4451 | 0.27608 | 0.011741 | 5.733 | 0 | 5.733 | 2024 | 1023 | 139 | 15.0178 | 0.75415 | 3.8975 | 19.6695 | 0 | 19.6695
2025 | 0 | 0 | 0 | 0 | 0 | 5.9212 |  | 2025 | 524 | 70 | 8.0339 | 0.39303 | 1.3679 | 9.7948 | 0 | 9.7948 | 2025 | 492 | 63 | 7.5812 | 0.36112 | -0.029215 | 7.9131 | 0 | 7.9131 | 2025 | 1220 | 162 | 18.1286 | 0.87846 | 1.8745 | 20.8816 | 0 | 20.8816
2026 | 0 | 0 | 0 | 0 | 0 | 5.9212 |  | 2026 | 626 | 84 | 9.8845 | 0.49017 | 0.49165 | 10.8663 | 0 | 10.8663 | 2026 | 498 | 67 | 7.8273 | 0.3824 | -0.056586 | 8.1531 | 0 | 8.1531 | 2026 | 1484 | 198 | 22.0112 | 1.0723 | 1.4559 | 24.5394 | 0 | 24.5394
2027 | 0 | 0 | 0 | 0 | 0 | 5.9212 |  | 2027 | 719 | 98 | 10.854 | 0.54184 | 0.75079 | 12.1466 | 0 | 12.1466 | 2027 | 465 | 63 | 7.0433 | 0.3484 | 0.12707 | 7.5188 | 0 | 7.5188 | 2027 | 1699 | 228 | 22.9501 | 1.125 | -0.67469 | 23.4004 | 0 | 23.4004
2028 | 0 | 0 | 0 | 0 | 0 | 5.9212 |  | 2028 | 839 | 113 | 12.8443 | 0.63258 | -0.047026 | 13.4298 | 0 | 13.4298 | 2028 | 533 | 71 | 8.175 | 0.39541 | -1.2839 | 7.2864 | 0 | 7.2864 | 2028 | 1885 | 250 | 25.5568 | 1.2316 | 0.94619 | 27.7346 | 0 | 27.7346
Total | 500 | 84.7 | 5.8051 | 0.1161 | 77.3277 | 77.3277 |  | Total | 3646 | 496 | 55.6934 | 2.785 | 11.0806 | 69.559 | 159.0212 | 159.0212 |  | 2847 | 380 | 43.6265 | 2.1465 | 3.5542 | 49.3272 | 100.1813 | 100.1813 |  | 8354 | 1120 | 118.3845 | 5.818 | 16.2625 | 140.4651 | 330.2129 | 330.2129
High Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 67.2847 |  | NPV | [7 empty] | 100.2194 | NPV | [7 empty] | 67.0812 | NPV | [7 empty] | 204.3223
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.54887 | 0.010977 | 5.9588 | 0.55985 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 25.8588 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 16.2907 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 53.6967 | 0.79408
2022 | 200 | 65.7 | 5.6345 | 0.11269 | 62.1259 | 6.307 |  | 2022 | 194 | 26 | 2.8513 | 0.14355 | 4.2381 | 7.233 | 52.525 | 7.233 | 2022 | 211 | 28 | 3.1593 | 0.15615 | 3.835 | 7.1504 | 33.0901 | 7.1504 | 2022 | 296 | 41 | 4.199 | 0.21303 | 5.0562 | 9.4683 | 109.07 | 9.4683
2023 | 200 | 12.6 | 1.0806 | 0.021612 | 12.0833 | 7.4092 |  | 2023 | 282 | 39 | 4.229 | 0.21866 | 5.3476 | 9.7953 | 53.2692 | 9.7953 | 2023 | 241 | 33 | 3.6633 | 0.18582 | 0.95014 | 4.7992 | 33.5589 | 4.7992 | 2023 | 688 | 94 | 9.7696 | 0.50078 | 3.7069 | 13.9773 | 110.6153 | 13.9773
2024 | 0 | 0 | 0 | 0 | 0 | 7.4092 |  | 2024 | 404 | 57 | 6.1558 | 0.31791 | -1.0685 | 5.4052 | 0 | 5.4052 | 2024 | 356 | 47 | 5.4451 | 0.27608 | 0.011741 | 5.733 | 0 | 5.733 | 2024 | 1023 | 139 | 15.0178 | 0.75415 | 3.8975 | 19.6695 | 0 | 19.6695
2025 | 0 | 0 | 0 | 0 | 0 | 7.4092 |  | 2025 | 524 | 70 | 8.0339 | 0.39303 | 1.3679 | 9.7948 | 0 | 9.7948 | 2025 | 492 | 63 | 7.5812 | 0.36112 | -0.029215 | 7.9131 | 0 | 7.9131 | 2025 | 1220 | 162 | 18.1286 | 0.87846 | 1.8745 | 20.8816 | 0 | 20.8816
2026 | 0 | 0 | 0 | 0 | 0 | 7.4092 |  | 2026 | 626 | 84 | 9.8845 | 0.49017 | 0.49165 | 10.8663 | 0 | 10.8663 | 2026 | 498 | 67 | 7.8273 | 0.3824 | -0.056586 | 8.1531 | 0 | 8.1531 | 2026 | 1484 | 198 | 22.0112 | 1.0723 | 1.4559 | 24.5394 | 0 | 24.5394
2027 | 0 | 0 | 0 | 0 | 0 | 7.4092 |  | 2027 | 719 | 98 | 10.854 | 0.54184 | 0.75079 | 12.1466 | 0 | 12.1466 | 2027 | 465 | 63 | 7.0433 | 0.3484 | 0.12707 | 7.5188 | 0 | 7.5188 | 2027 | 1699 | 228 | 22.9501 | 1.125 | -0.67469 | 23.4004 | 0 | 23.4004
2028 | 0 | 0 | 0 | 0 | 0 | 7.4092 |  | 2028 | 839 | 113 | 12.8443 | 0.63258 | -0.047026 | 13.4298 | 0 | 13.4298 | 2028 | 533 | 71 | 8.175 | 0.39541 | -1.2839 | 7.2864 | 0 | 7.2864 | 2028 | 1885 | 250 | 25.5568 | 1.2316 | 0.94619 | 27.7346 | 0 | 27.7346
Total | 500 | 84.7 | 7.2639 | 0.14528 | 80.168 | 80.168 |  | Total | 3646 | 496 | 55.6934 | 2.785 | 11.0806 | 69.559 | 131.653 | 131.653 |  | 2847 | 380 | 43.6265 | 2.1465 | 3.5542 | 49.3272 | 82.9397 | 82.9397 |  | 8354 | 1120 | 118.3845 | 5.818 | 16.2625 | 140.4651 | 273.3819 | 273.3819
Low Discount rate
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 77.7365 |  | NPV | [7 empty] | 196.0054 | NPV | [7 empty] | 128.2668 | NPV | [7 empty] | 403.0883
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 6.4 | 0.33621 | 0.0067242 | 5.3834 | 0.34293 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 38.1384 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 24.0267 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 79.1957 | 0.79408
2022 | 200 | 65.7 | 3.4514 | 0.069028 | 56.9152 | 3.8634 |  | 2022 | 194 | 26 | 2.8513 | 0.14355 | 4.2381 | 7.233 | 78.5564 | 7.233 | 2022 | 211 | 28 | 3.1593 | 0.15615 | 3.835 | 7.1504 | 49.4895 | 7.1504 | 2022 | 296 | 41 | 4.199 | 0.21303 | 5.0562 | 9.4683 | 163.125 | 9.4683
2023 | 200 | 12.6 | 0.66191 | 0.013238 | 11.2213 | 4.5385 |  | 2023 | 282 | 39 | 4.229 | 0.21866 | 5.3476 | 9.7953 | 80.7589 | 9.7953 | 2023 | 241 | 33 | 3.6633 | 0.18582 | 0.95014 | 4.7992 | 50.8771 | 4.7992 | 2023 | 688 | 94 | 9.7696 | 0.50078 | 3.7069 | 13.9773 | 167.6986 | 13.9773
2024 | 0 | 0 | 0 | 0 | 0 | 4.5385 |  | 2024 | 404 | 57 | 6.1558 | 0.31791 | -1.0685 | 5.4052 | 0 | 5.4052 | 2024 | 356 | 47 | 5.4451 | 0.27608 | 0.011741 | 5.733 | 0 | 5.733 | 2024 | 1023 | 139 | 15.0178 | 0.75415 | 3.8975 | 19.6695 | 0 | 19.6695
2025 | 0 | 0 | 0 | 0 | 0 | 4.5385 |  | 2025 | 524 | 70 | 8.0339 | 0.39303 | 1.3679 | 9.7948 | 0 | 9.7948 | 2025 | 492 | 63 | 7.5812 | 0.36112 | -0.029215 | 7.9131 | 0 | 7.9131 | 2025 | 1220 | 162 | 18.1286 | 0.87846 | 1.8745 | 20.8816 | 0 | 20.8816
2026 | 0 | 0 | 0 | 0 | 0 | 4.5385 |  | 2026 | 626 | 84 | 9.8845 | 0.49017 | 0.49165 | 10.8663 | 0 | 10.8663 | 2026 | 498 | 67 | 7.8273 | 0.3824 | -0.056586 | 8.1531 | 0 | 8.1531 | 2026 | 1484 | 198 | 22.0112 | 1.0723 | 1.4559 | 24.5394 | 0 | 24.5394
2027 | 0 | 0 | 0 | 0 | 0 | 4.5385 |  | 2027 | 719 | 98 | 10.854 | 0.54184 | 0.75079 | 12.1466 | 0 | 12.1466 | 2027 | 465 | 63 | 7.0433 | 0.3484 | 0.12707 | 7.5188 | 0 | 7.5188 | 2027 | 1699 | 228 | 22.9501 | 1.125 | -0.67469 | 23.4004 | 0 | 23.4004
2028 | 0 | 0 | 0 | 0 | 0 | 4.5385 |  | 2028 | 839 | 113 | 12.8443 | 0.63258 | -0.047026 | 13.4298 | 0 | 13.4298 | 2028 | 533 | 71 | 8.175 | 0.39541 | -1.2839 | 7.2864 | 0 | 7.2864 | 2028 | 1885 | 250 | 25.5568 | 1.2316 | 0.94619 | 27.7346 | 0 | 27.7346
Total | 500 | 84.7 | 4.4495 | 0.08899 | 73.5198 | 73.5198 |  | Total | 3646 | 496 | 55.6934 | 2.785 | 11.0806 | 69.559 | 197.4537 | 197.4537 |  | 2847 | 380 | 43.6265 | 2.1465 | 3.5542 | 49.3272 | 124.3933 | 124.3933 |  | 8354 | 1120 | 118.3845 | 5.818 | 16.2625 | 140.4651 | 410.0193 | 410.0193
High Cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 93.933 |  | NPV | [7 empty] | 137.1594 | NPV | [7 empty] | 90.7488 | NPV | [7 empty] | 280.9537
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 8.32 | 0.57023 | 0.011405 | 7.424 | 0.58163 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 31.0105 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 19.5362 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 64.3943 | 0.79408
2022 | 200 | 85.41 | 5.8537 | 0.11707 | 77.8686 | 6.5524 |  | 2022 | 194 | 26 | 2.8513 | 0.14355 | 4.2381 | 7.233 | 63.3693 | 7.233 | 2022 | 211 | 28 | 3.1593 | 0.15615 | 3.835 | 7.1504 | 39.9218 | 7.1504 | 2022 | 296 | 41 | 4.199 | 0.21303 | 5.0562 | 9.4683 | 131.5885 | 9.4683
2023 | 200 | 16.38 | 1.1226 | 0.022453 | 15.2335 | 7.6975 |  | 2023 | 282 | 39 | 4.229 | 0.21866 | 5.3476 | 9.7953 | 64.6414 | 9.7953 | 2023 | 241 | 33 | 3.6633 | 0.18582 | 0.95014 | 4.7992 | 40.7232 | 4.7992 | 2023 | 688 | 94 | 9.7696 | 0.50078 | 3.7069 | 13.9773 | 134.2301 | 13.9773
2024 | 0 | 0 | 0 | 0 | 0 | 7.6975 |  | 2024 | 404 | 57 | 6.1558 | 0.31791 | -1.0685 | 5.4052 | 0 | 5.4052 | 2024 | 356 | 47 | 5.4451 | 0.27608 | 0.011741 | 5.733 | 0 | 5.733 | 2024 | 1023 | 139 | 15.0178 | 0.75415 | 3.8975 | 19.6695 | 0 | 19.6695
2025 | 0 | 0 | 0 | 0 | 0 | 7.6975 |  | 2025 | 524 | 70 | 8.0339 | 0.39303 | 1.3679 | 9.7948 | 0 | 9.7948 | 2025 | 492 | 63 | 7.5812 | 0.36112 | -0.029215 | 7.9131 | 0 | 7.9131 | 2025 | 1220 | 162 | 18.1286 | 0.87846 | 1.8745 | 20.8816 | 0 | 20.8816
2026 | 0 | 0 | 0 | 0 | 0 | 7.6975 |  | 2026 | 626 | 84 | 9.8845 | 0.49017 | 0.49165 | 10.8663 | 0 | 10.8663 | 2026 | 498 | 67 | 7.8273 | 0.3824 | -0.056586 | 8.1531 | 0 | 8.1531 | 2026 | 1484 | 198 | 22.0112 | 1.0723 | 1.4559 | 24.5394 | 0 | 24.5394
2027 | 0 | 0 | 0 | 0 | 0 | 7.6975 |  | 2027 | 719 | 98 | 10.854 | 0.54184 | 0.75079 | 12.1466 | 0 | 12.1466 | 2027 | 465 | 63 | 7.0433 | 0.3484 | 0.12707 | 7.5188 | 0 | 7.5188 | 2027 | 1699 | 228 | 22.9501 | 1.125 | -0.67469 | 23.4004 | 0 | 23.4004
2028 | 0 | 0 | 0 | 0 | 0 | 7.6975 |  | 2028 | 839 | 113 | 12.8443 | 0.63258 | -0.047026 | 13.4298 | 0 | 13.4298 | 2028 | 533 | 71 | 8.175 | 0.39541 | -1.2839 | 7.2864 | 0 | 7.2864 | 2028 | 1885 | 250 | 25.5568 | 1.2316 | 0.94619 | 27.7346 | 0 | 27.7346
Total | 500 | 110.11 | 7.5466 | 0.15093 | 100.5261 | 100.5261 |  | Total | 3646 | 496 | 55.6934 | 2.785 | 11.0806 | 69.559 | 159.0212 | 159.0212 |  | 2847 | 380 | 43.6265 | 2.1465 | 3.5542 | 49.3272 | 100.1813 | 100.1813 |  | 8354 | 1120 | 118.3845 | 5.818 | 16.2625 | 140.4651 | 330.2129 | 330.2129
Low cost
[8 empty] | Benefits | Neutral | [7 empty] | Benefits | Fast Change | [7 empty] | Benefits | Slow Change
Costs | Capacity MVAr | Capital Cost $M | Annualised Cost $M | O&M $M | Residual $M | Total Cost $M |  | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M) | Benefits | Reduction in Intervention hours | Reduction in Start-ups | Reduction in dispatch cost ($M) | Reduction in start-up cost ($M) | Reduction in dispatch cost - export ($M) | Gross Market Benefits ($M) | Terminal Value ($M) | Total Gross Market Benefits ($M)
NPV | [5 empty] | 50.5793 |  | NPV | [7 empty] | 137.1594 | NPV | [7 empty] | 90.7488 | NPV | [7 empty] | 280.9537
2020 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 100 | 4.48 | 0.30704 | 0.0061409 | 3.9975 | 0.31319 |  | 2021 | 58 | 9 | 0.84079 | 0.047246 | 0 | 0.88803 | 31.0105 | 0.88803 | 2021 | 51 | 8 | 0.73205 | 0.041081 | 0 | 0.77313 | 19.5362 | 0.77313 | 2021 | 59 | 8 | 0.75139 | 0.042688 | 0 | 0.79408 | 64.3943 | 0.79408
2022 | 200 | 45.99 | 3.152 | 0.06304 | 41.9293 | 3.5282 |  | 2022 | 194 | 26 | 2.8513 | 0.14355 | 4.2381 | 7.233 | 63.3693 | 7.233 | 2022 | 211 | 28 | 3.1593 | 0.15615 | 3.835 | 7.1504 | 39.9218 | 7.1504 | 2022 | 296 | 41 | 4.199 | 0.21303 | 5.0562 | 9.4683 | 131.5885 | 9.4683
2023 | 200 | 8.82 | 0.60449 | 0.01209 | 8.2026 | 4.1448 |  | 2023 | 282 | 39 | 4.229 | 0.21866 | 5.3476 | 9.7953 | 64.6414 | 9.7953 | 2023 | 241 | 33 | 3.6633 | 0.18582 | 0.95014 | 4.7992 | 40.7232 | 4.7992 | 2023 | 688 | 94 | 9.7696 | 0.50078 | 3.7069 | 13.9773 | 134.2301 | 13.9773
2024 | 0 | 0 | 0 | 0 | 0 | 4.1448 |  | 2024 | 404 | 57 | 6.1558 | 0.31791 | -1.0685 | 5.4052 | 0 | 5.4052 | 2024 | 356 | 47 | 5.4451 | 0.27608 | 0.011741 | 5.733 | 0 | 5.733 | 2024 | 1023 | 139 | 15.0178 | 0.75415 | 3.8975 | 19.6695 | 0 | 19.6695
2025 | 0 | 0 | 0 | 0 | 0 | 4.1448 |  | 2025 | 524 | 70 | 8.0339 | 0.39303 | 1.3679 | 9.7948 | 0 | 9.7948 | 2025 | 492 | 63 | 7.5812 | 0.36112 | -0.029215 | 7.9131 | 0 | 7.9131 | 2025 | 1220 | 162 | 18.1286 | 0.87846 | 1.8745 | 20.8816 | 0 | 20.8816
2026 | 0 | 0 | 0 | 0 | 0 | 4.1448 |  | 2026 | 626 | 84 | 9.8845 | 0.49017 | 0.49165 | 10.8663 | 0 | 10.8663 | 2026 | 498 | 67 | 7.8273 | 0.3824 | -0.056586 | 8.1531 | 0 | 8.1531 | 2026 | 1484 | 198 | 22.0112 | 1.0723 | 1.4559 | 24.5394 | 0 | 24.5394
2027 | 0 | 0 | 0 | 0 | 0 | 4.1448 |  | 2027 | 719 | 98 | 10.854 | 0.54184 | 0.75079 | 12.1466 | 0 | 12.1466 | 2027 | 465 | 63 | 7.0433 | 0.3484 | 0.12707 | 7.5188 | 0 | 7.5188 | 2027 | 1699 | 228 | 22.9501 | 1.125 | -0.67469 | 23.4004 | 0 | 23.4004
2028 | 0 | 0 | 0 | 0 | 0 | 4.1448 |  | 2028 | 839 | 113 | 12.8443 | 0.63258 | -0.047026 | 13.4298 | 0 | 13.4298 | 2028 | 533 | 71 | 8.175 | 0.39541 | -1.2839 | 7.2864 | 0 | 7.2864 | 2028 | 1885 | 250 | 25.5568 | 1.2316 | 0.94619 | 27.7346 | 0 | 27.7346
Total | 500 | 59.29 | 4.0635 | 0.081271 | 54.1294 | 54.1294 |  | Total | 3646 | 496 | 55.6934 | 2.785 | 11.0806 | 69.559 | 159.0212 | 159.0212 |  | 2847 | 380 | 43.6265 | 2.1465 | 3.5542 | 49.3272 | 100.1813 | 100.1813 |  | 8354 | 1120 | 118.3845 | 5.818 | 16.2625 | 140.4651 | 330.2129 | 330.2129