{"text_format":"1","workbook":"xlsx","n_sheets":18,"sheets":["Disclaimer","Readme","Main","S-6","S-7","S-8.1","S-9.1","S-9.2","S-10.1","S-11.2","S-11.3","S-12.1","S-12.2","S-12.3","S-13","S-16.1","S-16.2","S-16.4"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":46,"comments":6,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Disclaimer","index":0,"n_rows":12,"n_cols":3,"rows_kept":12,"cut":false,"hidden":false,"merged":[[3,1,3,2],[11,1,11,2],[1,1,1,2]]}
[]
[null,"DISCLAIMER"]
[]
[null,"This document is made available to you on the following basis: "]
[]
[null,"(a)","Purpose - This document is provided to you for information purposes only. You are not permitted to commercialise it or any information contained in it."]
[null,"(b)","Reliance - This document may be subsequently amended.  Any reliance on this document is at your own risk."]
[null,"(c)","Intellectual Property – AEMO is the owner of the copyright in this document. All rights are reserved. All material is subject to copyright under the Copyright Act 1968 (Commonwealth) and permission to copy it, or any parts of it, must be obtained in writing from AEMO. AEMO is the owner of all other intellectual property rights in this document and the information contained in it. You must not in any way, or by any means, store, reproduce or modify it without AEMO's express written consent."]
[null,"(d)","No Warranty - Neither AEMO, nor any of AEMO’s advisers, consultants or other contributors to this document (or their respective associated companies, businesses, partners, directors, officers or employees) make any representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of this document, or the information contained in it."]
[null,"(e)","No Liability - To the maximum extent permitted by law, neither AEMO, nor any of its advisers, consultants or other contributors to this document (or their respective associated companies, businesses, partners, directors, officers or employees) shall have any liability (whether arising from negligence or otherwise) in respect of your use of the information (including any reliance on its currency, accuracy, reliability or completeness) contained in this document."]
[]
[null,"© 2013 - AEMO Limited is the owner of the copyright in this document. All rights reserved."]

{"sheet":"Readme","index":1,"n_rows":23,"n_cols":2,"rows_kept":23,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Schedule 4.2 SRAS Generator Modelling Data"]
[null,"for System Restart Anicillary Services Studies"]
[]
[]
[]
[null,"Prepared by: AEMO - Network Models"]
[]
[null,"2014-06-27"]
[]
[]
[null,"Usage Note:"]
[]
[1,"This spreadsheet has been designed to assist applicants in preparing the model and data that need to be submitted in order for AEMO to conduct power system modelling and studies for verification of system restart ancillary services."]
[3,"The \"Main\" sheet contains a list of all the data sheets. Some typical data sheet \"packages\" for generating systems have been provided for reference. The applicant should only select the relevant ones based on the actual arrangement of the generating plant."]
[4,"Each data sheet listed in the \"Main\" sheet contains a hyperlink which points to the corresponding tab."]
[6,"The \"value\" cells are only for information in the specified units. Other information should be entered into the remark field. One typical use is the name of additional reference material."]
[7,"Additional sheets may be inserted but the plant item(s) should be listed under the \"Proposed Plant\" column in the \"Main\" sheet."]
[8,"This spreadsheet is a testing version and is subject to change with no further notice."]
[9,"Users are encouraged to provide feedback on improvement of this spreadsheet."]
[]
[]
[null,"START - GO TO MAIN sheet"]

{"sheet":"Main","index":2,"n_rows":23,"n_cols":7,"rows_kept":23,"cut":false,"hidden":false,"merged":[[1,5,1,6],[1,3,2,3],[1,1,2,1],[1,2,2,2]]}
[]
[null,"Section","Data Sheet","Proposed Plant",null,"Examples"]
[null,null,null,null,"Thermal","Hydro","Gas Turbine"]
[null,6,"Generating system (Power Station)",null,"a","a","a"]
[null,7,"Individual Generating Unit Data",null,"a","a","a"]
[null,8,"Transformer (generating unit and generating system)",null,"aa","aa","aa"]
[null,9,"Electrical Machine "]
[null,9.1,"Synchronous Generator",null,"a","a","a"]
[null,9.1999999999999993,"Asynchronous Motor (generator auxilaries)",null,"a","(a)","(a)"]
[null,10,"Primary control systems"]
[null,10.1,"Synchronous Machine Excitation System",null,"a","a","a"]
[null,11,"Secondary Electrical Control systems"]
[null,11.2,"Other Generating unit control systems",null,"aa","aa","aa"]
[null,11.3,"Generating System Control systems (coordinated control of generating system plant)",null,"aa","aa","aa"]
[null,12,"Prime Mover and Primary Mechanical Control systems"]
[null,12.1,"Steam turbine and turbine governor",null,"a"]
[null,12.2,"Hydro turbine and turbine governor",null,null,"a"]
[null,12.3,"Gas turbine and turbine governor",null,null,null,"a"]
[null,13,"Secondary Mechanical Control systems",null,"aa","aa","aa"]
[null,16,"Protection systems"]
[null,16.100000000000001,"Synchronous machine protection systems (backups for excitation limiters)",null,"aa","aa","aa"]
[null,16.2,"Asynchronous motor protection systems"]
[null,16.399999999999999,"Other protection systems",null,"aa","aa","aa"]

{"sheet":"S-6","index":3,"n_rows":51,"n_cols":10,"rows_kept":51,"cut":false,"hidden":false,"merged":[[42,5,42,8],[49,5,49,8],[50,5,50,8],[43,5,43,8],[44,5,44,8],[47,5,47,8],[48,5,48,8],[37,5,37,8],[38,5,38,8],[39,5,39,8],[40,5,40,8],[41,5,41,8],[31,5,32,8],[31,9,32,9],[33,5,34,8],[33,9,34,9],[35,5,36,8],[35,9,36,9],[2,5,2,8],[27,9,28,9],[29,5,30,8],[29,9,30,9],[3,5,3,8],[5,5,5,8],[6,5,6,8],[7,5,7,8],[8,5,8,8],[17,5,17,8],[27,5,28,8],[21,9,22,9],[23,5,24,8],[23,9,24,9],[25,5,26,8],[25,9,26,9],[35,2,36,2],[35,4,36,4],[31,2,32,2],[31,4,32,4],[33,2,34,2],[33,4,34,4],[27,2,28,2],[27,4,28,4],[29,2,30,2],[29,4,30,4],[23,2,24,2],[23,4,24,4],[25,2,26,2],[25,4,26,4],[4,5,4,8],[8,2,16,2],[8,4,16,4],[21,2,22,2],[21,4,22,4],[10,3,16,3],[18,5,18,8],[19,5,19,8],[20,5,20,8],[21,5,22,8]]}
["Return to Main"]
[null,null,"6.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value",null,null,null,"Remarks"]
[null,null,null,"Connection point to network ","Text"]
[null,null,"VCON","Nominal voltage at connection to network","kV"]
[null,null,"NMC","Total station net maximum capacity (NMC)","MW (sent out)"]
[null,null,null,"Single line diagram of the power station showing primary plant configuration, switching arrangements, earthing arrangements for plant. On the single line diagram or separate diagram, show branch and earthing impedances.","Diagram"]
[null,null,null,"Diagram showing the various control systems for the generating unit and generating system together with their inputs and outputs and how they link with each other","Diagram"]
[null,null,null,"Three phase short circuit infeed at the connection point, for the following faults: "]
[null,null,null,"·          Balanced (3 phase)",null,"max",null,"min"]
[null,null,null,"·          Unbalanced (each phase)",null,null,"Ia","Ib","Ic"]
[null,null,null,null,null,"line-line, max"]
[null,null,null,null,null,"line-line, min"]
[null,null,null,null,null,"line-line-ground, max"]
[null,null,null,null,null,"line-line-ground, min"]
[null,null,null,null,null,"line-ground, max"]
[null,null,null,null,null,"line-ground, min"]
[null,null,"UH","·          Highest Voltage of a system (as per AS 1824.1)","kV"]
[null,null,"ZS1","·          Supplying Network Positive-sequence short-circuit impedance as viewed from the connection point","(a + jb) % on 100 MVA base and VCON"]
[null,null,"ZS2","·          Supplying Network Negative-sequence short-circuit impedance as viewed from the connection point","(a + jb) % on 100 MVA base and VCON"]
[null,null,"ZS0","·          Supplying Network Zero-sequence short-circuit impedance as viewed from the connection point","(a + jb) % on 100 MVA base and VCON"]
[null,null,"IKDDO","·          initial symmetrical short-circuit current with generating system disconnected","kA (RMS)"]
[null,null,null,"(peak RMS short circuit current, assuming non-meshed calculation approach for a radial connection)"]
[null,null,"IKDD","·          initial symmetrical short-circuit current","kA (RMS)"]
[null,null,null,"(peak RMS short circuit current, assuming non-meshed calculation approach for a radial connection)"]
[null,null,"IP","·          peak short-circuit current","kA (peak)"]
[null,null,null,"(maximum possible instantaneous value of the prospective (available) short-circuit current)"]
[null,null,"TMIN","·          minimum time delay","s"]
[null,null,null,"(the minimum time from fault inception to the instant of contact separation of the first pole to open of a switching device at or near the connection point – the time as agreed with the network service provider or 60 milliseconds)"]
[null,null,"IB","·          symmetrical short-circuit breaking current","kA (RMS)"]
[null,null,null,"(RMS value of an integral cycle of the symmetrical AC component of the prospective short circuit current at TMIN.)"]
[null,null,"IK","·          steady-state short-circuit current","kA (RMS)"]
[null,null,null,"(RMS value of the short-circuit current which remains after the decay of the transient phenomena)"]
[null,null,"IDC","·          decaying DC component of short-circuit current","kA"]
[null,null,null,"(mean value between the top and bottom envelope of a short-circuit current decaying from an initial value to zero)"]
[null,null,"TDC","·          decay time for DC component of short-circuit current","s"]
[null,null,null,"(the time taken for DC current component to fall to 1/2.718 of IDC)"]
[null,null,"ZGS1MIN","Minimum positive sequence impedance of Generating System","% on 100 MVA base and VCON"]
[null,null,"ZGS2MIN","Minimum negative sequence impedance of Generating System","% on 100 MVA base and VCON"]
[null,null,"ZGS0MIN","Minimum zero sequence impedance of Generating System","% on 100 MVA base and VCON"]
[null,null,null,"Description of the assumptions used in the derivation of the above quantities.","Text "]
[null,null,null,"Single phase to ground fault at the connection point ","3 phase current waveform vs time"]
[null,null,null,"Two Phase to ground fault at the connection point","3 phase current waveform vs time"]
[null,null,null,"Three phase fault at the connection point","3 phase current waveform vs time"]
[null,null,null,"Description of the assumptions used in the derivation of the above quantities.","Text "]
[]
[null,null,"6.1.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value",null,null,null,"Remarks"]
[null,null,null,"Operational arrangements for the generating system or within the generating system where this may affect switching configuration or plant operational limits. ","Text "]
[null,null,null,"Connection point over-voltage and under-voltage trip settings and times (if applicable)","kV and seconds"]
[null,null,null,"Model documentation (in accordance with Rule s5.2.4 (b)), as specified in the Generating System Model Guidelines."]

{"sheet":"S-7","index":4,"n_rows":30,"n_cols":7,"rows_kept":30,"cut":false,"hidden":false,"merged":[[14,2,16,2],[12,5,13,5],[12,6,13,6],[12,2,13,2],[12,4,13,4]]}
["Return to Main"]
[null,null,7,"Individual Generating Unit Data"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"NGU","Number of identical generating units and identification names or numbers","Text"]
[null,null,null,"Type of generating unit (technology), manufacturer and manufacturer’s type designation or product name.","Text"]
[null,null,null,"List or table of plant, control systems and protection systems, applicable to this generating unit, for which data has been provided in the Data Sheets.","Text"]
[]
[null,null,"7.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"MBASE","Rated MVA ","MVA"]
[null,null,"PSO","Rated MW (Sent Out)","MW (sent out)"]
[null,null,"PMAX","Nameplate Rating (Generated) ","MW (Gen)"]
[null,null,"PDMAX","Maximum capacity MW (Generated)"]
[null,null,null,"(e.g. short term rating or maximum dispatchable MW)"]
[null,null,null,"·          generated MW value(s)","MW"]
[null,null,null,"·          time(s) that the generated MW applies; and","minutes"]
[null,null,null,"·          conditions for which the generated MW applies.","Text                      (or chart and text)"]
[null,null,null,"Maximum ambient operating temperature (if applicable)","degrees C"]
[null,null,"VT","Nominal terminal voltage","kV"]
[null,null,"PAUX","Auxiliary load at PMAX","MW"]
[null,null,"Qmax","Rated reactive power output at PMAX","MVAr (sent out)"]
[null,null,"PMIN","Minimum Load (ML)","MW (sent out)"]
[null,null,"GCD","Capability chart","Graphical data"]
[null,null,"ZGU1MIN","Minimum positive sequence impedance ","% on 100 MVA base and VT"]
[null,null,"ZGU2MIN","Minimum zero sequence impedance ","% on 100 MVA base and VT"]
[null,null,"ZGU0MIN","Minimum negative sequence impedance ","% on 100 MVA base and VT"]
[]
[null,null,"7.1.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Operational arrangements for the generating system or within the generating system where this may affect switching configuration or plant operational limits. ","Text "]

{"sheet":"S-8.1","index":5,"n_rows":36,"n_cols":7,"rows_kept":36,"cut":false,"hidden":false,"merged":[[13,5,14,5],[13,6,14,6],[34,2,35,2],[34,3,35,3],[13,2,14,2],[13,4,14,4]]}
["Return to Main"]
[null,null,8.1,"Transformer (generating unit and generating system)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Transformer identification number","Text"]
[null,null,null,"If this is a generating unit transformer, the list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"8.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"GTW","Number of windings"]
[null,null,"GTVG","Vector group","Text"]
[null,null,"GTRn","Rated MVA of each winding","MVA"]
[null,null,"GTTRn","Principal tap rated voltages","kV/kV"]
[null,null,"GTZ1n","Positive sequence impedance of each winding","(a + jb) % on 100 MVA base and VCON"]
[null,null,null,"(negative sequence impedance [GTZ2n] is expected to be identical to GTZ1n)"]
[null,null,"GTZOn","Zero sequence impedance of each winding","(a + jb) % on 100 MVA base and VCON"]
[null,null,null,"Earthing arrangement","Text, diagram"]
[null,null,null,"No load losses","%"]
[null,null,null,"Copper losses","%"]
[null,null,null,"Saturation curve","Diagram"]
[null,null,null,"Tap changer type, on/off load","On/Off"]
[null,null,null,"Tapped winding","Text, diagram"]
[null,null,"GTAPR","Tap change range","kV – kV"]
[null,null,"GTAPS","Tap change step size","%"]
[null,null,null,"OLTC details of control loop described in block diagram or schematic form showing functions of individual elements, measurement units and measurement location.","Diagram"]
[]
[null,null,"8.1.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"VREFMAX","Upper voltage reference","V"]
[null,null,"VREFMIN","Lower voltage reference","V"]
[null,null,"GTAPV","Tap change voltage setting range and setpoint (if any)","kV – kV"]
[null,null,"GTAPD","Tap change voltage deadband","kV"]
[null,null,"GTAPVL","Tap change high and low voltage interlocks (monitoring non-tapped side voltage or other control signal (specify))","kV, kV"]
[null,null,"GTAPT","Tap change cycle time(s)","s, text"]
[null,null,"RL and XL","Line Drop Compensation or reactive power droop settings ","pu , pu   ","RL:"]
[null,null,null,null,"(per unit base on GTRn and nominal voltage of winding where the measurement is taken.) ","XL:"]

{"sheet":"S-9.1","index":6,"n_rows":48,"n_cols":7,"rows_kept":48,"cut":false,"hidden":false,"merged":[[24,2,25,2],[26,2,27,2],[30,5,31,5],[30,6,31,6],[30,2,31,2],[30,4,31,4]]}
["Return to Main"]
[null,null,9.1,"Synchronous Generator"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"9.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"VTGEN","Nominal terminal voltage","kV"]
[null,null,"MBASEGEN","Synchronous machine nameplate rating (MVA)","MVA"]
[null,null,"GCD","Capability chart","Graphical data"]
[null,null,"Q+PMAX","Maximum lagging Reactive power at PMAX","MVAr export"]
[null,null,"Q+PMIN","Maximum lagging Reactive power at PMIN","MVAr export"]
[null,null,"Q-PMAX","Maximum leading Reactive power at PMAX","MVAr import"]
[null,null,"Q-PMIN","Maximum leading Reactive power at PMIN","MVAr import"]
[null,null,"Q+OEX","Maximum lagging short term Reactive power capability at PMAX, VTGEN and rated speed (before over-excitation limiter action)","MVAr export"]
[null,null,"Hgen","Synchronous machine inertia constant (excluding prime mover inertia)","MWs/MBASE"]
[null,null,"NP","Number of poles","Text"]
[null,null,"GSCR","Short circuit ratio"]
[null,null,"ISTATOR","Rated stator current","A"]
[null,null,"IROTOR","Rated rotor current at rated MVA and power factor, rated terminal voltage and rated speed","A"]
[null,null,"VROTOR","Rotor voltage at which IROTOR is achieved","V"]
[null,null,"VF","DC field voltage at VTGEN and rated speed with unit unsynchronised","V"]
[null,null,"IF","DC field current at VTGEN and rated speed with unit unsynchronised","A"]
[null,null,"RA ","Stator resistance","% on MBASE and VTGEN"]
[null,null,null,"(at normal or typical operating temperature – specify temperature)","(temperature in °C)"]
[null,null,"RF ","Rotor resistance","% on MBASE and VTGEN"]
[null,null,null,"(at normal or typical operating temperature – specify temperature)","(temperature in °C)"]
[null,null,"XL","Stator leakage reactance","% on MBASE and VTGEN"]
[null,null,"X2","Negative sequence reactance","% on MBASE and VTGEN"]
[null,null,"Z0","Zero sequence impedance","(a+jb) % on MBASE and VTGEN"]
[null,null,null,"(including any neutral earthing impedance)"]
[null,null,"XD","Direct axis unsaturated synchronous reactance","% on MBASE and VTGEN"]
[null,null,"XDD","Direct axis unsaturated transient reactance","% on MBASE and VTGEN"]
[null,null,"XDDD","Direct axis unsaturated sub-transient reactance","% on MBASE and VTGEN"]
[null,null,"XQ","Quadrature axis unsaturated synchronous reactance","% on MBASE and VTGEN"]
[null,null,"XQQ","Quadrature axis unsaturated transient reactance","% on MBASE and VTGEN"]
[null,null,"XQQQ","Quadrature axis unsaturated sub-transient reactance","% on MBASE and VTGEN"]
[null,null,"TD0","Direct axis open circuit transient time constant","s"]
[null,null,"TDD0","Direct axis open circuit sub-transient time constant","s"]
[null,null,"TKD","Direct axis damper leakage time constant","s"]
[null,null,"TQ0","Quadrature axis open circuit transient time constant","s"]
[null,null,"TQQ0","Quadrature axis open circuit sub-transient time constant","s"]
[null,null,"GOCC","Open circuit characteristic","Graphical data"]
[null,null,"S10","Saturation Parameter at 1.0pu terminal voltage on GOCC (the ratio between measured voltage and the air-gap line)."]
[null,null,"S12","Saturation Parameter 1.2pu terminal voltage on GOCC(the ratio between measured voltage and the air-gap line)."]
[null,null,"GSCC","Short circuit characteristic","Graphical data"]
[null,null,"GZPC","Zero power factor curve","Graphical data"]

{"sheet":"S-9.2","index":7,"n_rows":36,"n_cols":7,"rows_kept":36,"cut":false,"hidden":false,"merged":[[10,5,11,5],[10,6,11,6],[16,2,17,2],[10,2,11,2],[10,3,11,3],[18,4,20,4],[26,2,28,2],[26,4,28,4],[22,2,24,2],[22,4,24,4],[18,2,20,2]]}
["Return to Main"]
[null,null,9.1999999999999993,"Asynchronous Motor (generator auxilaries)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"9.2.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"VTGEN","Nominal terminal voltage","kV"]
[null,null,"MBASEGEN","Asynchronous machine nameplate rating (MVA)","MVA"]
[null,null,"QN","Reactive power  consumption over range of asynchronous machine output (0 to PMAX) at VTGEN","Chart"]
[null,null,null,null,"(MVAr vs. MW)"]
[null,null,"Hgen","Asynchronous machine and gearbox inertia constant (excluding prime mover inertia)","MWs/MBASE"]
[null,null,"NP","Number of poles"]
[null,null,"SLIP","Rated slip"]
[null,null,null,"Stator/rotor turn ratio"]
[null,null,"RS","Stator resistance","% on MBASE and VTGEN"]
[null,null,null,"(at normal or typical operating temperature – specify temperature)","(temperature in °C)"]
[null,null,"XS","Stator leakage reactance ","% on MBASE and VTGEN"]
[null,null,null,"·          unsaturated and "]
[null,null,null,"·          at VTGEN"]
[null,null,"RM ","Iron loss resistance, referred to the stator","% on MBASE and VTGEN"]
[null,null,"XM","Magnetizing reactance, referred to the stator ","% on MBASE and VTGEN"]
[null,null,null,"·          unsaturated and "]
[null,null,null,"·          at VTGEN"]
[null,null,"RR","Rotor resistance at rated slip, referred to the stator","% on MBASE and VTGEN"]
[null,null,"XR","Rotor leakage reactance, referred to the stator ","% on MBASE and VTGEN"]
[null,null,null,"·          unsaturated and "]
[null,null,null,"·          at VTGEN"]
[null,null,"R0","Zero sequence resistance","% on MBASE and VTGEN"]
[null,null,"X0","Zero sequence reactance ","% on MBASE and VTGEN"]
[null,null,"R2","Negative sequence resistance","% on MBASE and VTGEN"]
[null,null,"X2","Negative sequence reactance ","% on MBASE and VTGEN"]
[null,null,null,"Magnetising curve (voltage versus current)","Chart"]
[null,null,null,"Speed (slip) vs torque (power) curve(s)","Chart"]
[null,null,null,"Equivalent circuit noting location of equivalent impedances","Chart"]

{"sheet":"S-10.1","index":8,"n_rows":42,"n_cols":7,"rows_kept":42,"cut":false,"hidden":false,"merged":[[18,6,19,6],[14,2,25,2],[14,4,25,4],[18,5,19,5]]}
["Return to Main"]
[null,null,10.1,"Synchronous Machine Excitation System"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"10.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"VCEIL","Rotor voltage capable of being supplied for 5s at rated voltage (VTGEN) and rated speed","V"]
[null,null,"VFMIN","Minimum field voltage","V"]
[null,null,null,"Maximum rate of change of field voltage","Rising V/s"]
[null,null,null,"Maximum rate of change of field voltage","Falling V/s"]
[null,null,null,"Exciter description including type, ratings, connection schematic, source of any external supplies, etc.","Text"]
[null,null,null,"If applicable, exciter saturation curve over 50%-120% of rated voltage. ","Diagram"]
[null,null,null,"Details of the excitation control system described in functional block diagram form showing:","Functional block diagram"]
[null,null,null,"·          voltage control systems (AVR);"]
[null,null,null,"·          power system stabiliser (PSS);"]
[null,null,null,"·          exciter;"]
[null,null,null,"·          reactive current or reactive power compensation (if fitted)"]
[null,null,null,"(e.g. Load drop compensation/VAr sharing, also referred to as line drop compensation or reactive power droop);"]
[null,null,null,"·          over-excitation limiter;"]
[null,null,null,"·          under-excitation limiter;"]
[null,null,null,"·          stator current limiter (if fitted);"]
[null,null,null,"·          flux (V/f) limiter (if fitted); "]
[null,null,null,"·          manual restrictive limiter (if fitted); and"]
[null,null,null,"·          any other limiters that may restrict excitation system operation."]
[null,null,null,"Details of excitation control system components failover (e.g. for multiple AVR channels, or AVR to manual control) or generator trip, describing conditions that cause the failover or trip.","Text"]
[]
[null,null,"10.1.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"DC gain of excitation control loop","V/V"]
[null,null,null,"Active power operating range of the generating unit when the PSS is in operation. "]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, etc.) for:"]
[null,null,null,"·          voltage control systems (AVR);"]
[null,null,null,"·          power system stabiliser;"]
[null,null,null,"·          exciter;"]
[null,null,null,"·          reactive current or reactive power compensation;"]
[null,null,null,"·          over-excitation limiter;"]
[null,null,null,"·          under-excitation limiter;"]
[null,null,null,"·          stator current limiter;"]
[null,null,null,"·          flux (V/f) limiter; and"]
[null,null,null,"·          any other limiters that may restrict excitation control system operation."]

{"sheet":"S-11.2","index":9,"n_rows":15,"n_cols":7,"rows_kept":15,"cut":false,"hidden":false,"merged":[[31,2,32,2],[31,4,32,4],[25,2,26,2],[27,2,28,2]]}
["Return to Main"]
[null,null,11.2,"Other Generating unit control systems"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"11.2.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Details of the control system showing principles of operation, trigger levels, etc.","Text / Diagram"]
[null,null,null,"Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b).","Functional block diagram"]
[null,null,null,"Details of how this controller interfaces with other control systems or directly to generating system plant (if applicable), or how this controller effects its control action.","Text / Diagram"]
[]
[null,null,"11.2.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.)."]

{"sheet":"S-11.3","index":10,"n_rows":15,"n_cols":7,"rows_kept":15,"cut":false,"hidden":false,"merged":[[31,2,32,2],[31,4,32,4],[25,2,26,2],[27,2,28,2]]}
["Return to Main"]
[null,null,11.3,"Generating System Control systems (coordinated control of generating system plant)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies. ","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"11.3.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Details of the control system showing principles of operation, trigger levels, etc.","Text / Diagram"]
[null,null,null,"Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b).","Functional block diagram"]
[null,null,null,"Details of how this controller interfaces with other control systems or directly to generating system plant (if applicable), or how this controller effects its control action.","Text / Diagram"]
[]
[null,null,"11.3.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.)."]

{"sheet":"S-12.1","index":11,"n_rows":58,"n_cols":7,"rows_kept":58,"cut":false,"hidden":false,"merged":[[43,5,44,5],[43,6,44,6],[45,5,46,5],[45,6,46,6],[33,5,34,5],[33,6,34,6],[35,5,36,5],[35,6,36,6],[41,5,42,5],[41,6,42,6],[41,2,42,2],[41,4,42,4],[28,4,29,4],[20,5,21,5],[20,6,21,6],[26,5,27,5],[26,6,27,6],[28,5,29,5],[28,6,29,6],[55,2,57,2],[43,2,44,2],[43,4,44,4],[45,2,46,2],[45,4,46,4],[12,2,12,4],[23,2,23,4],[35,2,36,2],[20,2,21,2],[20,4,21,4],[33,2,34,2],[33,4,34,4],[26,4,27,4],[26,2,27,2],[28,2,29,2],[35,4,36,4]]}
["Return to Main"]
[null,null,12.1,"Steam turbine and turbine governor"]
[null,null,"Note 1:","(when applicable the information provided must include operation with both droop and isochronous modes of operation)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[null,null,null,"If this is the steam cycle part of a combined cycle gas turbine, list the generating unit(s) that forms the gas cycle part of the generating system and describe the power output relationship between the cycles.  ","Text / Chart"]
[]
[null,null,"12.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Description of steam turbine configuration (e.g. cross compound, single reheat) ","Text"]
[null,null,null,"Functional block diagram for turbine governor and turbine model, in accordance with Rule s5.2.4 (b).","Diagram"]
[null,null,"Power fractions and rated power(s) (whichever apply):"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"FVHP","Very high pressure turbine power fraction","Per-unit of PMAX"]
[null,null,"FHP","High pressure turbine power fraction","Per-unit of PMAX "]
[null,null,"FIP","Intermediate pressure turbine power fraction","Per-unit of PMAX "]
[null,null,"FLP1","Low pressure turbine 1 power fraction","Per-unit of PMAX "]
[null,null,"FLP2","Low pressure turbine 2 power fraction","Per-unit of PMAX"]
[null,null,"PM1","Rated mechanical power, shaft 1","MW"]
[null,null,"PM2","Rated mechanical power, shaft 2","MW"]
[null,null,null,"(if applicable)"]
[null,null,"HT1, HT2","Summated turbine inertias (excluding electrical generator), as seen on each generator shaft.","MWs/MBASE"]
[null,null,"Turbine time constants (whichever apply) :"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"TCH","Steam chest time constant (control valves to HP or VHP) Exhaust","s"]
[null,null,"TVHP","Very high pressure turbine time constant","s"]
[null,null,null,"(possible alternative to TCH)"]
[null,null,"THP","High pressure turbine","s"]
[null,null,null,"(possible alternative to TCH)"]
[null,null,"TRH1","Boiler reheat #1 time constant","s"]
[null,null,"TRH2","Boiler reheat #2 time constant","s"]
[null,null,"TCO ","Crossover time constant (IP exhaust to LP exhaust)","s"]
[null,null,"TLP1","Low pressure turbine 1 time constant","s"]
[null,null,null,"(possible alternative to TCO)"]
[null,null,"TLP2","Low pressure turbine 2 time constant","s"]
[null,null,null,"(possible alternative to TCO)"]
[]
[null,null,"12.1.2","Setting Data Sheet"]
[null,null,"Turbine governor"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"RMAX","Maximum Droop","% "]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,"RNORM","Normal Droop","% "]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,"RMIN","Minimum Droop","% "]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,null,"Sustained response to frequency change","MW/Hz"]
[null,null,null,"Non-sustained response to frequency change","MW/Hz"]
[null,null,"PLR","Load Rejection Capability","MW"]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.)."]
[null,null,"FDBMAX","Maximum Frequency Dead band","Hz"]
[null,null,"FDBN","Normal Frequency Deadband","Hz"]
[null,null,"FDBMIN","Minimum Frequency Deadband","Hz"]
[null,null,"PDB","MW Deadband","MW"]
[null,null,null,"Governor/servomotor rate limits"]
[null,null,null,"·          raise MW output","MW/s"]
[null,null,null,"·          lower MW output","MW/s"]

{"sheet":"S-12.2","index":12,"n_rows":45,"n_cols":7,"rows_kept":45,"cut":false,"hidden":false,"merged":[[37,5,38,5],[37,6,38,6],[37,2,38,2],[37,4,38,4],[7,2,11,2],[7,4,11,4],[16,3,17,3],[16,4,17,4],[22,2,24,2],[33,6,34,6],[33,4,34,4],[31,2,32,2],[31,4,32,4],[29,2,30,2],[29,4,30,4],[33,2,34,2],[29,5,30,5],[29,6,30,6],[31,5,32,5],[31,6,32,6],[33,5,34,5]]}
["Return to Main"]
[null,null,12.2,"Hydro turbine and turbine governor"]
[null,null,"Note 1:","(when applicable the information provided must include operation with both droop and isochronous modes of operation)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[null,null,null,"Description of hydro-turbine type (e.g. Francis turbine, Pelton wheel, etc.) ","Text"]
[null,null,null,"Functional block diagram, in accordance with Rule s5.2.4 (b), for turbine governor and turbine model showing: ","Diagram"]
[null,null,null,"·          functional structure;"]
[null,null,null,"·          mathematical model details within each block (gains, time constants and non-linear elements);"]
[null,null,null,"·          input and output quantities for each function block; and"]
[null,null,null,"·          units for functional block diagram input and output quantities (if per-unit, specify base)."]
[]
[null,null,"12.2.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"PM1","Rated mechanical power","MW"]
[null,null,"PTMAX","Power limits imposed by valve or gate travel","MW"]
[null,null,"PTMIN"]
[null,null,"TW","Water starting time","s"]
[null,null,"TG","Gate servomotor time constant","s"]
[null,null,"TP","Pilot valve time constant","s"]
[null,null,"TR","Dashpot time constant","s"]
[null,null,null,"Governor/gate rate limits"]
[null,null,null,"·          raise MW output","MW/s"]
[null,null,null,"·          lower MW output","MW/s"]
[null,null,"HT","Turbine inertia (excluding electrical generator)","MWs/MBASE"]
[]
[null,null,"12.2.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"RMAX","Maximum Droop","% "]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,"RNORM","Normal Droop","% "]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,"RMIN","Minimum Droop","% "]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,null,"Sustained response to frequency change","MW/Hz"]
[null,null,null,"Non-sustained response to frequency change","MW/Hz"]
[null,null,null,"Governor control system time constant(s)","s"]
[null,null,null,"(specify)"]
[null,null,"PLR","Load Rejection Capability","MW"]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.)."]
[null,null,"FDBMAX","Maximum Frequency Dead band","Hz"]
[null,null,"FDBN","Normal Frequency Deadband","Hz"]
[null,null,"FDBMIN","Minimum Frequency Deadband","Hz"]
[null,null,"PDB","MW Deadband","MW"]

{"sheet":"S-12.3","index":13,"n_rows":62,"n_cols":7,"rows_kept":62,"cut":false,"hidden":false,"merged":[[39,6,41,6],[50,5,51,5],[50,6,51,6],[46,5,47,5],[46,6,47,6],[48,5,49,5],[48,6,49,6],[54,2,55,2],[54,4,55,4],[54,5,55,5],[54,6,55,6],[8,5,12,5],[8,6,12,6],[18,5,20,5],[18,6,20,6],[24,5,26,5],[48,2,49,2],[24,6,26,6],[27,5,29,5],[27,6,29,6],[37,5,38,5],[37,6,38,6],[39,5,41,5],[48,4,49,4],[50,2,51,2],[50,4,51,4],[37,2,38,2],[37,4,38,4],[46,2,47,2],[46,4,47,4],[27,2,29,2],[27,4,29,4],[30,4,32,4],[39,2,41,2],[39,4,41,4],[33,4,35,4],[24,2,26,2],[24,4,26,4],[8,2,12,2],[8,4,12,4],[18,2,20,2],[18,4,20,4]]}
["Return to Main"]
[null,null,12.3,"Gas turbine and turbine governor"]
[null,null,"Note 1:","(when applicable the information provided must include operation with both droop and isochronous modes of operation)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[null,null,null,"Description of gas turbine type (e.g. combined cycle, open cycle, etc.)","Text"]
[null,null,null,"Fuel capability (gas, distillate, other)","Text"]
[null,null,null,"Functional block diagram for turbine governor and turbine model, in accordance with Rule s5.2.4 (b), showing: ","Diagram"]
[null,null,null,"·          functional structure;"]
[null,null,null,"·          mathematical model details within each block (gains, time constants and non-linear elements);"]
[null,null,null,"·          input and output quantities for each function block; and"]
[null,null,null,"·          units for functional block diagram input and output quantities (if per-unit, specify base)."]
[null,null,null,"Details of the temperature control system and its impact on sustainable generating unit output (e.g. characteristic of output power versus frequency).","Diagram"]
[]
[null,null,"12.3.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"PM1","Rated mechanical power","MW"]
[null,null,"KFC","Fuel control system gain","pu/pu"]
[null,null,null,"(per unit valve position / per unit governor output)"]
[null,null,null,"(specify per unit bases)"]
[null,null,"TFC","Fuel control system time delay","s"]
[null,null,"TVP","Valve positioner time constant","s"]
[null,null,"TFS","Fuel system time constant","s"]
[null,null,"KVP","Valve positioner forward gain","pu/pu"]
[null,null,null,"(per unit fuel flow / per unit valve position)"]
[null,null,null,"(specify per unit bases)"]
[null,null,"KVPF","Valve positioner feedback gain","pu/pu"]
[null,null,null,"(per unit valve position / per unit fuel flow)"]
[null,null,null,"(specify per unit bases)"]
[null,null,"VPMAX","Valve positioner range limits ","pu","max:"]
[null,null,"VPMIN","(maximum and minimum)",null,"min:"]
[null,null,null,"(specify per unit bases)",null,"p.u. base:"]
[null,null,"VPMAXR","Valve positioner rate or change limits","pu/s","max raise rate:"]
[null,null,"VPMAXL","(maximum raise and lower rates)",null,"max lower rate:"]
[null,null,null,"(specify per unit bases)",null,"p.u. base:"]
[null,null,"TC","Combustor time delay","s"]
[null,null,"TCD","Gas turbine output time constant","s"]
[null,null,null,"(compressor discharge time constant)"]
[null,null,null,"Output power characteristic / torque function","Graph"]
[null,null,null,"(per unit output power versus per unit fuel flow and speed, excluding limiting effects of temperature controller)"]
[null,null,null,"(specify per unit bases)"]
[null,null,"HT","Turbine and compressor inertia (excluding electrical generator), as measured on generator shaft.","MWs/MBASE"]
[]
[null,null,"12.3.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,"RMAX","Maximum Droop","%"]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,"RNORM","Normal Droop","%"]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,"RMIN","Minimum Droop","%"]
[null,null,null,"(% change in frequency / per-unit change in generating unit output)"]
[null,null,null,"Sustained response to frequency change","MW/Hz"]
[null,null,null,"Non-sustained response to frequency change","MW/Hz"]
[null,null,null,"Governor control system time constant(s)","s"]
[null,null,null,"(specify)"]
[null,null,null,"Load Rejection Capability","MW"]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.)."]
[null,null,"FDBMAX","Maximum Frequency Dead band","Hz"]
[null,null,"FDBN","Normal Frequency Deadband","Hz"]
[null,null,"FDBMIN","Minimum Frequency Deadband","Hz"]
[null,null,"PDB","MW Deadband","MW"]

{"sheet":"S-13","index":14,"n_rows":16,"n_cols":7,"rows_kept":16,"cut":false,"hidden":false,"merged":[[31,2,32,2],[31,4,32,4],[25,2,26,2],[27,2,28,2]]}
["Return to Main"]
[null,null,13,"Secondary Mechanical Control systems"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[null,null,null,"Description of controller type (e.g. over-speed controller, etc.) and a description of its purpose. ","Text"]
[]
[null,null,"13.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Details of the control system showing principles of operation, trigger levels, etc.","Text / Diagram"]
[null,null,null,"Details of the control system described in functional block diagram form, in accordance with Rule s5.2.4 (b).","Functional block diagram"]
[null,null,null,"Details of how this controller interfaces with the primary mechanical control systems (if applicable), or how this controller effects its control action.","Text / Diagram"]
[]
[null,null,"13.1.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"All functional block diagram parameters, in accordance with Rule s5.2.4 (b), (gains, time constants, mathematical functions, non-linear characteristics, limits, set-points, etc.)."]

{"sheet":"S-16.1","index":15,"n_rows":26,"n_cols":7,"rows_kept":26,"cut":false,"hidden":false,"merged":[[10,2,15,2],[20,2,25,2]]}
["Return to Main"]
[null,null,16.100000000000001,"Synchronous machine protection systems (backups for excitation limiters)"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"16.1.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Details of the protection system showing principles of operation, trigger levels, switching times, etc. for the following protective functions:","Text / Diagram"]
[null,null,null,"Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, turbine trip, etc.) for the following protective functions:","Text / Diagram"]
[null,null,null,"·          over-excitation protection;"]
[null,null,null,"·          under-excitation protection;"]
[null,null,null,"·          stator current protection (if fitted);"]
[null,null,null,"·          flux (V/f) protection ; "]
[null,null,null,"·          loss of field protection; and"]
[null,null,null,"·          pole-slip (out-of-step) protection. "]
[]
[null,null,"16.1.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Protection trigger levels and timings for the following protective functions:"]
[null,null,null,"·          over-excitation protection;"]
[null,null,null,"·          under-excitation protection;"]
[null,null,null,"·          stator current protection (if fitted);"]
[null,null,null,"·          flux (V/f) protection ; "]
[null,null,null,"·          loss of field protection; and"]
[null,null,null,"·          pole-slip (out-of-step) protection. "]

{"sheet":"S-16.2","index":16,"n_rows":14,"n_cols":7,"rows_kept":14,"cut":false,"hidden":false,"merged":[]}
["Return to Main"]
[null,null,16.2,"Asynchronous motor protection systems "]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"16.2.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Details of the protection system showing principles of operation, trigger levels, switching times, etc.","Text / Diagram"]
[null,null,null,"Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, etc.).","Text / Diagram"]
[]
[null,null,"16.2.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Protection trigger levels and timings."]

{"sheet":"S-16.4","index":17,"n_rows":30,"n_cols":7,"rows_kept":30,"cut":false,"hidden":false,"merged":[[10,2,17,2],[22,2,29,2]]}
["Return to Main"]
[null,null,16.399999999999999,"Other protection systems"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"The list of generating units to which this information applies.","Text "]
[null,null,null,"Manufacturer and manufacturer’s type designation or product name.","Text"]
[]
[null,null,"16.4.1","Design Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Details of the protection system showing principles of operation, trigger levels, switching times, etc., and conditions for discharging active power to the power system for the following protective functions:","Text / Diagram"]
[null,null,null,"Details of how this protection system effects its protection action (e.g. trips the generating unit at the generating unit circuit breaker, turbine trip, etc.) for the following protective functions:","Text / Diagram"]
[null,null,null,"·          over-speed or high or low frequencies;"]
[null,null,null,"·          high frequency rates of change;"]
[null,null,null,"·          high or low voltages;"]
[null,null,null,"·          excessive negative phase sequence current; "]
[null,null,null,"·          sustained voltage fluctuations or harmonic distortion;"]
[null,null,null,"·          differential; "]
[null,null,null,"·          anti-islanding; and"]
[null,null,null,"·          synchrocheck (if fitted); "]
[]
[null,null,"16.4.2","Setting Data Sheet"]
[null,null,"Symbol","Data Description","Units","Value","Remarks"]
[null,null,null,"Protection trigger levels and timings for the following protective functions:"]
[null,null,null,"·          over-speed or high or low frequencies;"]
[null,null,null,"·          high frequency rates of change;"]
[null,null,null,"·          high or low voltages;"]
[null,null,null,"·          excessive negative phase sequence current; "]
[null,null,null,"·          sustained voltage fluctuations or harmonic distortion; "]
[null,null,null,"·          differential;"]
[null,null,null,"·          anti-islanding; and"]
[null,null,null,"·          synchrocheck (if fitted); "]