## Index
The National Electricity Market Constraint Report 2018
Electronic Material
This spreadsheet provides (for each calendar year):
* Constraint equation changes year on year comparison
* Binding constraint equations (energy and FCAS separately)
* Binding Impact of constraint equations
* Summary of binding/binding impact constraint equations by region
* Summary of binding/binding impact constraint equations for System Normal vs Outages
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time
* Network and generation augmentations
Important Notice
This document is subject to an important disclaimer that limits or excludes AEMO’s liability for reliance on the information in it. Please read this on the disclaimer page (see link below) before you read the rest of this document.
Go to Disclaimer page
Binding constraints:
A constraint equation is a linear equation, with a left hand side (LHS) and a right hand side (RHS). A constraint is binding when LHS=RHS, which means it has reached its upper limit.
In some cases, the binding results for several constraint equation IDs have been combined. This is due to some limits being represented by several constraint equations, to either:
• Move each generator from a maximum calculation onto the LHS of separate constraint equations (such as the New South Wales to Queensland voltage stability limit).
• Manage the same limit under different network configurations (such as Yallourn W1 switched into 500 kV or 220 kV mode).
• Combine different values of network support for the same generator(s).
Binding Impact:
Binding Impact is used to distinguish between the severities of different binding constraint equations. It represents the financial pain associated with that binding constraint equation and can be a good way of picking up congestion issues. It is a relative term, not an absolute term.

## Constraint Changes
Constraint changes by region and year
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Ad-Hoc | 1 | 0 | 0 | 0 | 1 | 1
Constraint Automation - Real Time | 24316 | 24110 | 11484 | 22603 | 29805 | 37744
Constraint Automation | 139 | 166 | 98 | 64 | 20 | 48
DATASNAP | 92 | 87 | 105 | 115 | 44 | 92
FCAS | 295 | 255 | 543 | 257 | 267 | 486
NSW | 2345 | 5272 | 6332 | 1973 | 2455 | 8206
Negative Residue | 0 | 0 | 0 | 0 | 0 | 0
Non-Conformance | 6 | 3 | 5 | 5 | 52 | 35
Other | 2 | 0 | 2 | 0 | 0 | 3
Outage Ramping | 22066 | 19888 | 21056 | 20484 | 16928 | 19368
PASA | 3 | 12 | 0 | 0 | 0 | 0
Qld | 330 | 270 | 118 | 206 | 246 | 1716
Quick | 84 | 93 | 101 | 359 | 386 | 1032
SA | 1101 | 600 | 1001 | 3197 | 1775 | 3239
Tas | 1114 | 726 | 121 | 1050 | 134 | 193
Vic | 359 | 637 | 3541 | 3251 | 1376 | 6280
Total constraint eqns | 9935 | 10303 | 11231 | 11660 | 11578 | 11467
Total changes without outage ramping and CA-RT | 5871 | 8121 | 11967 | 10477 | 6756 | 21331
Total number of constraints
| 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Constraint Equations | 7746 | 7697 | 8275 | 8902 | 9523 | 9745 | 9935 | 10303 | 11231 | 11660 | 11578 | 11467
Constraint Sets | 3366 | 3369 | 3431 | 3559 | 3657 | 3597 | 3410 | 3424 | 3630 | 3778 | 3917 | 4036
Constraint Functions |  |  | 347 | 382 | 390 | 401 | 366 | 359 | 364 | 373 | 387 | 505
Increase in Constraint Equations |  |  | 578 | 627 | 621 | 222 | 190 | 368 | 928 | 429 | -82 | -111

## Binding
Constraint Equation ID | 2018 Hours | 2017 Hours | Description | Type | Region
#HAYMSF1_E | 2144.5 | 0 | QCCK2H.ENERGY * 1 <= 25 (Wt = 360) | Other | Quick
#BNGSF2_E | 1691.5833 | 0 | SBEM2B.ENERGY * 1 <= 20 (Wt = 360) | Other | Quick
#WHITSF1_E | 1129.8333 | 0 | QSLS1W.ENERGY * 1 <= 38 (Wt = 360) | Other | Quick
N^^V_NIL_1 | 1117.8333 | 1806.4167 | Out = Nil, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | NIL | NSW
#DAYDSF1_E | 1111.25 | 0 | QCCK1D.ENERGY * 1 <= 140 (Wt = 360) | Other | Quick
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 1063.0833 | 390.4167 | Upper limit (1460 to 1295 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | NIL | SA
#HAMISF1_E | 831.1667 | 0 | QSLD1H.ENERGY * 1 <= 38 (Wt = 360) | Other | Quick
#PPCCGT_P_E | 774.5833 | 77 | SPPT.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA1_P_E | 774.5833 | 26.8333 | STSA1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA1_O_E | 773 | 22.5 | STSA1.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
#PPCCGT_O_E | 762.9167 | 81.3333 | SPPT.ENERGY * 1 >= 175 (Wt = 65) | Other | Direction
#DDSF1_E | 725.9167 | 0 | QBRS1D.ENERGY * 1 <= 87 (Wt = 360) | Other | Quick
#BANN1_E | 674.8333 | 0 | VWES1B.ENERGY * 1 <= 32 (Wt = 360) | Other | Quick
#CLARESF1_E | 671.0833 | 0 | QCLA1C.ENERGY * 1 <= 66 (Wt = 360) | Other | Quick
#TORRA3_P_E | 536.5 | 0 | STSA3.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA3_O_E | 535.75 | 0 | STSA3.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
#TORRA4_P_E | 512.25 | 23.1667 | STSA4.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA4_O_E | 512.0833 | 21.5833 | STSA4.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
VSML_ZERO | 490.3333 | 20.75 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
N^N-LS_SVC | 488 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | NSW
#TORRB2_P_E | 370.3333 | 174.5 | STSB2.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#OSB-AG_P_E | 353.5833 | 205.5 | SNBN1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#OSB-AG_O_E | 353.3333 | 205.4167 | SNBN1.ENERGY * 1 >= 145 (Wt = 65) | Other | Direction
S>V_NIL_NIL_RBNW | 338.75 | 282.4167 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL | SA
N_X_MBTE2_A & N_X_MBTE2_B | 300.6667 | 1203.3333 | Out= two Directlink cables, NSW to Qld limit | Outage | NSW
SVML_ZERO | 289.6667 | 83.5833 | SA to Vic on ML upper transfer limit of 0 MW | Outage | SA
#TORRB1_P_E | 275.5833 | 0 | STSB1.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#MEWF1_E | 271.1667 | 0 | QWKM1M.ENERGY * 1 <= 135 (Wt = 360) | Other | Quick
V::N_NIL_xxx | 269.6667 | 624.5 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Vic
#SMCSF1_E | 260.75 | 0 | QTZS1S.ENERGY * 1 <= 61 (Wt = 360) | Other | Quick
N_X_MBTE_3A & N_X_MBTE_3B | 253.75 | 224 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | NSW
#GANNSF1_E | 252.6667 | 0 | VKGS1G.ENERGY * 1 <= 45 (Wt = 360) | Other | Quick
#TORRB3_P_E | 240.5 | 22.75 | STSB3.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA2_P_E | 229.0833 | 26.1667 | STSA2.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#TORRA2_O_E | 228.5833 | 21.9167 | STSA2.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 208.25 | 311.9167 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Vic
#TORRB2_O_E | 195.9167 | 103 | STSB2.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
#KARSF1_E | 189.25 | 0 | VRCS1K.ENERGY * 1 <= 90 (Wt = 360) | Other | Quick
#TORRB1_O_E | 176.0833 | 0 | STSB1.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
NSA_S_PORxxx | 173.6667 | 30.0833 | Port Lincoln >= 15 MW for Network Support Agreement | Outage | SA
V::S_SETB_TBSE_2 | 169.4167 | 45.3333 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
#BNGSF1_E | 165.0833 | 0 | SBEM1B.ENERGY * 1 <= 105 (Wt = 360) | Other | Quick
#EMERASF1_E | 155.5833 | 0 | QLIS1E.ENERGY * 1 <= 4 (Wt = 360) | Other | Quick
#STWF1_E | 153.3333 | 0 | NBKW1S.ENERGY * 1 <= 131 (Wt = 360) | Other | Quick
T>T_NIL_110_1 | 150.9167 | 188.0833 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Tas
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 144.9167 | 517.1667 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
#TORRB3_O_E | 138.25 | 19.0833 | STSB3.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
N_MBTE1_B | 130.3333 | 206.4167 | Out= one Directlink cable, Qld to NSW limit | Outage | NSW
T>T_LIPM_110_2B | 129.0833 | 2.1667 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
#TORRB4_P_E | 123.25 | 40.8333 | STSB4.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
S:V_500_HY_TEST_DYN | 122.5833 | 208 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
S_SNOW_N+S_190 | 121.0833 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 190 MW | Outage | SA
S::V_TBSE_TBSE_2 | 119.75 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
N_SILVERWF_MAX | 119.6667 | 0 | Limit MW output of Silverton wind farm to not exceed 45 MW with Broken Hill solar generating | Outage | NSW
V_T_NIL_FCSPS | 114.5833 | 194.75 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Vic
I_CTRL_ISSUE_TE | 113.25 | 311.4167 | DC Link Control Issue Constraint for Terranora | Outage | Other
V::S_SETB_MAXG_2 | 112.0833 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with both Black Range series capacitors O/S). | Outage | SA
#WEMENSF1_E | 108.5 | 0 | VWES2W.ENERGY * 1 <= 43 (Wt = 360) | Other | Quick
Q>NIL_BI_xxx | 91.25 | 139.5 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact between T022 Callide A and H015 Lilyvale. | NIL | Qld
#SNOWTWN1_E | 86.9167 | 6.25 | SNWF1T.ENERGY * 1 <= 5 (Wt = 360) | Other | Quick
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 82 | 148.25 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | NSW
N>N-NIL_DC | 81.1667 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | NSW
#SAPHWF1_E | 80.9167 | 0 | NSAP1S.ENERGY * 1 <= 170 (Wt = 360) | Other | Quick
#N-Q-MNSP1_I_E | 79.3333 | 44.0833 | N-Q-MNSP1.ENERGY * -1 = 65 (Wt = 0.0005) | Other | Quick
#TORRB4_O_E | 77.1667 | 24.25 | STSB4.ENERGY * 1 >= 40 (Wt = 65) | Other | Direction
V:S_600_HY_TEST_DYN | 77 | 288.5 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
V^^N_NIL_1 | 74.8333 | 0 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Vic
#CSPVPS1_E | 74.5833 | 0 | QCOS1C.ENERGY * 1 <= 30 (Wt = 360) | Other | Quick
#BODWF1_E | 74.4167 | 0 | NBOD1B.ENERGY * 1 <= 76 (Wt = 360) | Other | Quick
NQTE_ROC | 74.25 | 19.5 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | NSW
#KSP1_E | 71.5833 | 111.6667 | QROG1K.ENERGY * 1 <= 32.5 (Wt = 360) | Other | Quick
QNTE_ROC | 71.1667 | 16.8333 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
#QPS5_P_E | 70.75 | 1.4167 | SQPS5Q.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
#QPS5_O_E | 70.5833 | 1.4167 | SQPS5Q.ENERGY * 1 >= 74 (Wt = 65) | Other | Direction
T^V_NIL_11 | 70.1667 | 21.5 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
N^^Q_LS_VC_B1 | 69.8333 | 0.83333 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
S_LB_1+2+3_190 | 67 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms<= 190 MW | Outage | SA
V::N_SETB_xxx | 67 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S>SE6161_SETX2_SGBL | 66.9167 | 0 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | SA
#TARONG#3_E | 65.3333 | 0 | QTRN3.ENERGY * 1 <= 245 (Wt = 360) | Other | Quick
NQTE_BLOCK_ECS | 65 | 0 | Minimum of 29MW on Directlink QLD to NSW to ensure that Directlink ECS will not operate when Directlink support is required | Outage | NSW
#STAN-4_E | 63.75 | 0 | QSTN4.ENERGY * 1 <= 365 (Wt = 360) | Other | Quick
T_TAMARCCGT_GCS | 61.3333 | 65.4167 | Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) constraint to manage effective size of generation contingency for loss of Tamar CCGT. Limit output of Tamar CCGT based on load available and/or armed for shedding by Tamar GCS. | NIL | Tas
#PARSF1_E | 60.1667 | 0 | NPG11P.ENERGY * 1 <= 35 (Wt = 360) | Other | Quick
V^SML_NSWRB_2 | 58.5 | 53.1667 | Out = NSW Murraylink runback scheme, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | NIL | Vic
#OAKLAND1_E | 58.4167 | 31.25 | VTGT3A.ENERGY * 1 <= 39 (Wt = 35) | Other | Quick
T^V_NIL_9 | 57.6667 | 1.1667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
T>T_NIL_BL_IMP_7CC | 51.9167 | 14.8333 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
#WRWF1_E | 50.5 | 184.9167 | NWRK1W.ENERGY * 1 <= 35 (Wt = 360) | Other | Quick
SVML_ROC_80 | 49.9167 | 21.6667 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
V>SMLARHO1 | 49 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
Q>N-MUTE_758 | 47.8333 | 68.9167 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
N_STWF1_ZERO | 45.5833 | 0 | Silverton wind farm upper limit of 0 MW | Outage | NSW
VSML_ROC_80 | 43.1667 | 20.5 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
T^V_NIL_8 | 43 | 2.25 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
T>T_HAPM_2A | 42.5 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
#NPS_P_E | 42.3333 | 0 | VNPS.ENERGY * 1 <= 0 (Wt = 29) | Other | Direction
V>>V_ROTS_TX_2A_R | 38.5 | 2.25 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
S>>PATW_BWPA_TPRS | 35.3333 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>RBTX2_RBTX1_WEMWP4 | 33.8333 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage | SA
Q>NIL_BI_CAGS_CALV_O | 33.6667 | 0 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104/7105 (T022 Callide A to T152 Gladstone South) 132 kV lines closed with 132 kV split between T022 Callide A and H015 Lilyvale. | NIL | Qld
V^^S_SETB_TBSE_2 | 32.8333 | 2.0833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
NSA_Q_BARCALDN | 32.4167 | 4.9167 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Qld
#SALTCRK1_E | 32.25 | 0 | VTG61S.ENERGY * 1 <= 54 (Wt = 360) | Other | Quick
S_HPRG1_E | 31.1667 | 2.5 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
#MANSLR1_E | 29.5833 | 0 | NMLS1M.ENERGY * 1 <= 35.85 (Wt = 360) | Other | Quick
S:VS_650_HY_TEST_DYN | 27.6667 | 28.75 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
S_DVRB2_270 | 27.5833 | 30.75 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
N^^V_NIL_MAXG_PP_N-2 | 27.3333 | 0 | Out = Nil, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit + Pelican Point when they declared as single credible contingency | NIL | NSW
T>T_PMSH_IMP_4C | 27.0833 | 4 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V:S_600_HY_TEST | 27.0833 | 75.4167 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
T>T_NIL_BL_110_18_1 | 26.6667 | 33.1667 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
S>>PARB_RBTU_WEWT | 26.25 | 0.75 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
V_OWF_TGTSNRBHTN_30 | 26.0833 | 17.8333 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
S:V_500_HY_TEST | 25.6667 | 48.3333 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
T_ROCOF_1 | 25.3333 | 49.25 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
VSML_220 | 25 | 22.4167 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Vic
V_T_NIL_BL1 | 24.4167 | 145.8333 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Vic
#TORRB3_C_E | 24.0833 | 23.5833 | STSB3.ENERGY * 1 <= 55 (Wt = 27) | Other | Quick
V>>N-NIL_HA | 21.9167 | 12.1667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Vic
#WRSF1_E | 21.8333 | 0 | NWRK2W.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
N>>V-NIL_O | 21.75 | 0 | Out = Nil, avoid overloading Upper Tumut to Murray (65) using 15 mins rating line on trip of Lower Tumut to Wagga (051) + 970,990,99M (out of Yass) line, Feedback | NIL | NSW
T^V_HA_GT_220_1 | 21.75 | 0 | Out= one George Town to Hadspen 220kV line, limit post-contingency loading on Palmerston to Sheffield 220kV line (flow to north) to avoid voltage collapse on trip of the remaining Hadspen to George Town 220kV line. | Outage | Tas
V_OAKHILL_TFB_42 | 20.6667 | 0 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Vic
N^N_KKLS_1 | 20.1667 | 233.8333 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | NSW
T_T_BA_JB_RC2_250 | 20 | 0.58333 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
T:T_LIPM_1 | 19.6667 | 63.1667 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 19.3333 | 40 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Qld
#SA1_E_20180723 | 19.1667 | 0 | Multiple SA1 LHS <= 100 (Wt = 35) | Other | Quick
#NPS_O_E | 19.0833 | 0 | VNPS.ENERGY * 1 = 100 (Wt = 755) | Other | Direction
VS_350 | 18.8333 | 0 | Victoria to SA on VicSA upper transfer limit of 350 MW | Outage | Vic
#TORRB2_C_E | 18.5 | 12.5833 | STSB2.ENERGY * 1 <= 55 (Wt = 27) | Other | Quick
T^V_HAPM_220_1 | 18.5 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage | Tas
V::N_WBHO_xxx | 17.8333 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
Q:N_1078 | 17.6667 | 0 | QNI oscillatory stability limit of 1078 MW | Outage | Qld
V>>V_ROTS_TX_2B_R | 17.5 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
V::S_BLKRG_MAXG_2 | 17.0833 | 0 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
V^SML_HORC_3 | 17 | 0.33333 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
S_WATERLWF_RB | 16.8333 | 27.4167 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
V_BANNERTON_ZERO | 16.3333 | 0 | Bannerton Solar Farm upper limit of 0 MW | Outage | Vic
#SA1_E_20180514 | 16.0833 | 0 | Multiple SA1 LHS <= 0 (Wt = 360) | Other | Quick
N>>N-NIL__3_OPENED & CLOSED | 15.9167 | 21.25 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
T>T_FASH_1_2_C1 | 15.8333 | 0 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, West Coast 220/110 kV parallel closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
#SA1_E_20180721 | 15.6667 | 0 | Multiple SA1 LHS <= 270 (Wt = 35) | Other | Quick
V::S_NIL_MAXG_xxx | 15.6667 | 3.75 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
S_PW-CB6156_LG1 | 15.4167 | 0 | Out=Penola West 132kV CB 6156 O/S (Note: with Penola West 132kV CB 6158 CLOSED), Oscillatory stability limit Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
T>T_PMSH_IMP_4D | 15 | 0.5 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_NIL_BL_5C | 14.8333 | 1.8333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
S>NIL_NIL_NWMH2 | 14.6667 | 37 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
Q::N_ARSVC_AR_2L-G | 14.5833 | 0 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
T>T_X_BWLF_PMWA110_4 | 14.5833 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana AND Palmerston to Waddamana 110kV lines, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Tas
S_SNOWNTH1_ZERO | 14.25 | 0 | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW | Outage | SA
S_SNOWSTH1_ZERO | 14.25 | 0 | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW | Outage | SA
S>>MKRB_CNRB_WEMWP4 | 14.1667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | SA
T::T_NIL_4 | 14.1667 | 15.5833 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
V::N_HWSM_xxx | 14 | 52.8333 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
#MPP_2_E | 13.25 | 0 | QBCK2.ENERGY * 1 <= 250 (Wt = 360) | Other | Quick
S_PPT+TIPSB_800 | 13.0833 | 0 | Heywood IC (VIC-SA) <= 800- (Pelican Pt GT11) -Max(TIPS B units, TIPS A units, Osbourne, QPS5, Snowthown North+South, Mintaro, Pelican) - South East generation + South East Load; NOTE: Pelican PT output restricted to 400MW | NIL | SA
S_HALWF2_0 | 13 | 18.3333 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
S>X_RBPA+CB_01 | 12.8333 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
N>LSDU_LSDU | 12.6667 | 33 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
N_NIL_TE_B | 12.5 | 23.4167 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
T_FASH_MAXGEN_1 | 12.25 | 15.5 | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
V>>V_NIL_8 | 12 | 0.83333 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
T>T_NIL_BL_IMP_7C | 11.9167 | 0 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Tas
N^^V_CNCW_1 | 11.5833 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
NC_N_VP5 | 11.4167 | 6.5 | Non Conformance Constraint for Vales Point VP5 Power Station | Other | Non-Conformance
N^N-89_LSTX_SVC | 11.4167 | 0 | Out= Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage | NSW
S>NIL_SGBN_SGSE-T2 | 11.4167 | 54.0833 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
V>>V_NIL_6A_R | 11 | 0 | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL | Vic
T>T_FASH_1_N-2 | 10.9167 | 2.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
#BALBG1_E | 9.5 | 0 | VBA21B.ENERGY * 1 <= 10 (Wt = 360) | Other | Quick
S^NIL_PL_MAX | 9.4167 | 0.5 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
T>>T_PMSH_EXP_3C | 9.4167 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
V^^S_NIL_MAXG_xxx | 9.4167 | 0.41667 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
T::T_HA_GT_PM_4 | 9.1667 | 2.3333 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
V>>V_NIL_1A | 9.1667 | 0.33333 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
S>>PARB_RBTU_WTTP | 8.9167 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
S_PPT400 | 8.9167 | 0 | SA Pelican Point gen <= 400MW | NIL | SA
T>T_PMSH_IMP_4E | 8.9167 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V_BALDHILL_ZERO | 8.9167 | 0 | Bald Hill Windfarm upper limit of 0 MW | Outage | Vic
T^^V_GTSH_1 | 8.8333 | 0.083333 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
S>>X_RBPA+CB_03 | 8.6667 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
N_BODWF1_ZERO | 8.5833 | 0 | Bodangora wind farm upper limit of 0 MW | Outage | NSW
S:VS_650_HY_TEST | 8.4167 | 5.4167 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
#TORRB1_C_E | 8.1667 | 14.1667 | STSB1.ENERGY * 1 <= 40 (Wt = 27) | Other | Quick
S>BRDV_BWPA_RHBR | 8.1667 | 1.5833 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T_T_JB_RC1+2_TI_250 | 8.0833 | 0 | Discretionary 250 MW upper limit on John Butters, Reece 1+2 and Tribute | Outage | Tas
T>T_PMSH_IMP_4F | 8 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
NRM_SA1_VIC1 | 7.6667 | 1.25 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
N>>N-NIL__G_15M | 7.5833 | 0 | Out= Nil, avoid O/L Upper Tumut to Yass (2) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
VTBL_ROC | 7.5833 | 12.5833 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Vic
Q:NIL_CS | 7.5 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Qld
T>T_PMSH_2B | 7.5 | 0.41667 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
N_COLEASF1_ZERO | 7.4167 | 0 | Coleambally solar farm upper limit of 0 MW | Outage | NSW
TVBL_ROC | 7.4167 | 12.75 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Tas
V>>N-NIL_HG | 7.25 | 0.66667 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
VS_050 | 7.1667 | 59.25 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Vic
V>>V_DDSM_1 | 7.0833 | 0.16667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Vic
N^^Q_NIL_A | 7 | 11.25 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
#NPS_D_E | 6.8333 | 0 | VNPS.ENERGY * 1 = 100 (Wt = 755) | Other | Quick
T_T_FASH_3_N-2 | 6.75 | 0.16667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain Reece Unit 1 to 0 MW as per TAS Networks advice | Outage | Tas
T_T_FASH_1_N-2 | 6.6667 | 7.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
S-HDWF2_0 | 6.4167 | 2.1667 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | SA
S_HDWF1_0 | 6.4167 | 1.8333 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
S_HDWF3_0 | 6.4167 | 1.25 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | SA
V::N_EPMB_xxx | 6.3333 | 0.66667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_HYSE_xxx | 6.3333 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
N^^V_DDSM1 | 6.25 | 12.5 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | NSW
S_SNOW_N+S_210 | 6.1667 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 210 MW | Outage | SA
#N-Q-MNSP1_E_E | 6.0833 | 0 | N-Q-MNSP1.ENERGY * 1 = -40 (Wt = 0.0001) | Other | Quick
N>LSDU9U6_LSDU9U7 | 6.0833 | 0 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
#SA1_E_20180724 | 6 | 0 | Multiple SA1 LHS <= 200 (Wt = 35) | Other | Quick
T>T_PM_TX_1A | 6 | 0 | Out= Palmerston 220/110kV transformer, prevent overload of either Palmerston to Hadspen 110kV line (flow to North) for trip of the parallel Palmerston to Hadspen 110 kV line, feedback | Outage | Tas
#MINTARO_E | 5.9167 | 0 | SMPS.ENERGY * 1 <= 90 (Wt = 360) | Other | Direction
T>T_HA_TX | 5.75 | 0 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 220 kV to 110 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Tas
V::N_HORC_xxx | 5.75 | 0.58333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S>NIL_NIL_SETX12 | 5.6667 | 3.3333 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
VS_250 | 5.5 | 0 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Vic
V^SML_BUDP_3 | 5.5 | 0 | Out = Buronga to Balranald to Darlington Pt (X5) 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
T>T_NIL_BL_3C | 5.4167 | 0.16667 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
Q_CS_1750 | 5.3333 | 0 | Qld Central to Qld South upper transfer limit of 1750MW (discretionary) | Outage | Qld
V>>V-MSUT_1 | 5.1667 | 0 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage | Vic
T_V_NIL_BL1 | 5 | 4.8333 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Tas
N>N-NIL_LSDU | 4.9167 | 7.9167 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
Q>>GGWU_GGCP2_GGCP1 | 4.9167 | 0 | Out= Gin Gin to Wurdong (819), avoid O/L Gin Gin to Calliope River (813) on trip of Gin Gin to Calliope River (814) line, Feedback | Outage | Qld
QNTE_OSCILLATE | 4.8333 | 10.6667 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
V_OWF_NRB_0 | 4.8333 | 6.6667 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
S::V_TBSE_TBSE_1 | 4.75 | 2.1667 | Out = one Tailembend-South East 275kV line (NOTE: with both Black Range series capacitors I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines | Outage | SA
S>NIL_WERB_WEWT | 4.75 | 104.25 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
NC_N_VP6 | 4.6667 | 4.75 | Non Conformance Constraint for Vales Point VP6 Power Station | Other | Non-Conformance
S_LB_1+2+3_210 | 4.6667 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=210 MW | Outage | SA
#NSW1-QLD1_RAMP_I_F | 4.4167 | 11.5833 | NSW1-QLD1 >= MIN(-400, InitialFlow + 200) (Wt=35) | Other | Quick
S_HPRL1_E | 4.3333 | 1.3333 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | SA
NSA_V_BDL0xxx | 4.25 | 6 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Vic
VSML_VFRB_OFF | 4.25 | 0.083333 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Vic
S>>BG6246_BGPR_HUWT | 4.1667 | 0 | Out= Bungama 132kV CB6246, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Port Pirie 132kV line (this offloads Snowtown-Bungama 132kV line), Feedback | Outage | SA
S_SECB_LG-1 | 4.0833 | 0.25 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
T^^V_PMSH_1 | 4.0833 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of either one Sheffield to Georgetown 220kV line or one Hadspen to Georgetown 220kV line. | Outage | Tas
T_MRWF_QLIM_xx | 4.0833 | 118.8333 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Tas
S_BRBG_CMWF_0 | 3.9167 | 1.6667 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | SA
S_PW-CB6156_LG3 | 3.9167 | 0 | Out=Penola West 132kV CB 6156 O/S (Note: with with Penola West 132kV CB 6158 CLOSED), Oscillatory stability limit max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
N>>N-964__3_OPENED & CLOSED | 3.8333 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | Outage | NSW
T_GO_300 | 3.75 | 0 | Discretionary 300 MW upper limit on total Gordon generation | Outage | Tas
N^^V_DDWG | 3.6667 | 14.75 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V_ARARAT_ZERO | 3.6667 | 0.5 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
S-BUPV1_0 | 3.6667 | 0 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | SA
VSML_000 | 3.4167 | 0 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
VS_300 | 3.4167 | 0 | Victoria to SA on VicSA upper transfer limit of 300 MW | Outage | Vic
T^T_LIPM_1 | 3.3333 | 0 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Tas
T>T_GTHA_IMP_4O | 3.25 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Sheffield) for trip of remaining Hadspen to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_GTSH_IMP_4K | 3.25 | 3.6667 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
#MORTLK12_D_E | 3.1667 | 0 | VM0P2O.ENERGY * 1 = 20 (Wt = 755) | Other | Quick
N^N_CHLS_1 | 3.1667 | 0 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage | NSW
S>>RBTX2_RBTX1_WEWT | 3.1667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage | SA
V::N_JNWO_xxx | 3.0833 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T_T_FASH_2_N-2 | 3 | 4.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Tas
N^^Q_LS_VC_B4 | 2.9167 | 3.5833 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage | NSW
N^^V_MSDD2 | 2.9167 | 0 | Out = Dederang to Murray 330 kV line, avoid voltage collapse at Darlington Point for loss of the remaining Dederang to Murray 330 kV line | Outage | NSW
T>>T_PMSH_EXP_3B | 2.9167 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T_V_NIL_FCSPS | 2.9167 | 4.9167 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
VS_400 | 2.9167 | 0 | Victoria to SA on VicSA upper transfer limit of 400 MW | Outage | Vic
V:T_NIL_BL_1 | 2.8333 | 0 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
VN_1050 | 2.75 | 0 | Discretionary Vic to NSW transfer upper limit of 1050 MW | Outage | Vic
#PPCCGT_C_E | 2.6667 | 21.8333 | SPPT.ENERGY * 1 <= 340 (Wt = 27) | Other | Quick
T>T_PMSH_5A | 2.6667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L line terminal equipment of Hadspen to Palmerston No. 1 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 2 220 kV line, feedback | Outage | Tas
#BDL02_E | 2.5833 | 0 | VMWT3.ENERGY * 1 <= 30 (Wt = 360) | Other | Quick
N>N-ARKK_CH_CB892A | 2.5833 | 0 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Swamp out when all 3 directlink cable O/S, Feedback. TG formulation in PD/ST | Outage | NSW
NC_V_JLB03 | 2.5833 | 0 | Non Conformance Constraint for Jeeralang B - 03 Power Station | Other | Non-Conformance
NRM_NSW1_VIC1 | 2.5 | 0 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue
NC_Q_STAN-4 | 2.4167 | 0.91667 | Non Conformance Constraint for Stanwell STAN-4 Power Station | Other | Non-Conformance
T>T_NIL_TOV_5F | 2.4167 | 0 | Out = Nil, avoid TOV following NCSPS slow action for O/L of Hadspen to Georgetown No. 1 220 kV lines (flow to North) for trip of the Hadspen to Georgetown No. 2 220 kV line, considering status of Tamar CCGT, feedback equation | NIL | Tas
V::S_HYSE_MAXG_2 | 2.4167 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
V>SML_NSWRB_10 | 2.4167 | 3.0833 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
S>MKRB_BWMP_HUWT | 2.3333 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T>T_GTSH_2D | 2.3333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown 220 kV line (flow North) for trip of other Hadspen to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V_MTGBRAND_11WT | 2.3333 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 11 | Outage | Vic
Q>>BCCP_CLWU_LCCP_2 | 2.25 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
S>BLMK_BWPA_HUWT | 2.25 | 12.5 | Out= Belalie-Mokota 275kV line (This offloads Willalo substation and Willagoleche WF) OR Belalie-Willalo 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V>>V_NIL_5 | 2.25 | 34.75 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Vic
NC_V_YWPS2 | 2.1667 | 2.4167 | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Other | Non-Conformance
N^^V_MSUT_1 | 2.1667 | 20.0833 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
VSML_015 | 2.1667 | 0 | Vic to SA on ML upper transfer limit of 15 MW | Outage | Vic
V^^S_TBTX+CB_SETB | 2.1667 | 0 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
#LYA4_E | 2.0833 | 0 | VLYP4.ENERGY * 1 <= 250 (Wt = 360) | Other | Quick
N::V_BYGR_2 | 2.0833 | 0 | Out = Bannaby to Gullen Range(61), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | NSW
S>>BRBG_BGTX_HUWT | 2.0833 | 0 | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | SA
S>>X_MKRB+WERB_4 | 2.0833 | 0 | Out= Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (Note: Line Only O/S), avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, | Outage | SA
V>V_HWYP2_1_R | 2.0833 | 0.25 | Out = Hazelwood to Yallourn No. 2 220 kV line, avoid O/L Yallourn to Hazelwood PS No.1 220kV line on trip of Yallourn to Rowville No.5 220kV line, Radial mode, YWG1 on 220kV, Feedback | Outage | Vic
V_ARWF_FSTTRP_5 | 2.0833 | 0 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
#N-Q-MNSP1_RAMP_I_F | 2 | 1.75 | N-Q-MNSP1 <= MAX(-25, InitialFlow - 80) (Wt=35) | Other | Quick
N>N_LSDU_9U6_1 | 2 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | NSW
N_WRWF1_055 | 2 | 0 | WhiteRock WF upper limit of 55 MW | Outage | NSW
T::T_NIL_3 | 2 | 8.8333 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. Swamped if Tamar CCGT OOS. | NIL | Tas
N::V_CNLT_2 | 1.9167 | 0 | Out = Lower Tumut -Canberra(07), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | NSW
NC_Q_DDPS1 | 1.9167 | 0.16667 | Non Conformance Constraint for Darling Downs Power Station | Other | Non-Conformance
NC_Q_TARONG#3 | 1.9167 | 0.33333 | Non Conformance Constraint for Tarong 3 Power Station | Other | Non-Conformance
#DALNTH01_E | 1.8333 | 0 | SDAN1D.ENERGY * 1 <= 24 (Wt = 360) | Other | Quick
NC_Q_BRAEMAR2 | 1.8333 | 2.5 | Non Conformance Constraint for Braemar 2 Power Station | Other | Non-Conformance
NC_Q_HAMISF1 | 1.8333 | 0 | Non Conformance Constraint for HAMILTON SOLAR FARM | Other | Non-Conformance
Q>>LCCP_CLWU_BCCP_2 | 1.8333 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
S:V_PA_SVC_420 | 1.8333 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
S>>X_MKRB+WERB_11 | 1.8333 | 0 | Out=Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (Note: Line Only O/S) avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line | Outage | SA
N^^Q_ARDM_B1 | 1.75 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V>>V_KTS_TX_A2_2A_R | 1.75 | 9.0833 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
#DALNTHL1_E | 1.6667 | 0 | SDAN2D.ENERGY * 1 <= 30 (Wt = 360) | Other | Quick
NC_V_JLA03 | 1.6667 | 0 | Non Conformance Constraint for Jeeralang A - 03 Power Station | Other | Non-Conformance
V^^S_MLSY_2 | 1.6667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
N^^V_BUDP_1 | 1.5833 | 0 | Out = Buronga to Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
Q_CS_2000 | 1.5833 | 0 | Qld Central to Qld South upper transfer limit of 2000MW (discretionary) | Outage | Qld
S>NIL_NIL_SGMYSE-T2 | 1.5833 | 2.5 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | SA
V>>V_NIL_1B | 1.5833 | 1.0833 | Out = Nil, avoid O/L Murray to Dederang No.2 330kV line (flow MSS to DDTS) for loss of the parallel No.1 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
#GANNBG1_E | 1.5 | 0 | VKGB1G.ENERGY * 1 <= 10 (Wt = 360) | Other | Quick
#V-S-MNSP1_I_E | 1.5 | 0 | V-S-MNSP1.ENERGY * -1 >= 40 (Wt = 35) | Other | Quick
N^^N_NIL_1 | 1.5 | 0.083333 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
Q::N_AR_CP2_AR_2L-G | 1.5 | 0 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
S>NWB6021_TX3 | 1.5 | 0 | Out= North West Bend 132kV CB6021, avoid O/L North West Bend 66/132kV #3 TX on trip of Robertstown-NWB #1 132kV line, Feedback | Outage | SA
V::N_DDSM_xxx | 1.5 | 4.9167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V^SML_KGRC_4 | 1.5 | 0 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Vic
#GSTONE3_E | 1.4167 | 0 | QGLD3.ENERGY * 1 <= 98 (Wt = 360) | Other | Quick
I_QNI_ONE_PHASE_N-2 | 1.4167 | 0 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Other
NC_V_BALBG1 | 1.4167 | 0 | Non Conformance Constraint for BALLARAT BATT (GEN) | Other | Non-Conformance
NC_V_JLA02 | 1.4167 | 2.3333 | Non Conformance Constraint for Jeeralang A - 02 Power Station | Other | Non-Conformance
S>NIL_NIL_SGBN | 1.4167 | 1.0833 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
T>T_LIPM_110_2A | 1.4167 | 89.8333 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
#WATERLWF_E | 1.3333 | 118.75 | SWLE.ENERGY * 1 <= 0 (Wt = 360) | Other | Quick
N^^Q_TW_330_BUS3_B1 | 1.3333 | 1 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | NSW
N^^V_SMTXF2_1 | 1.3333 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
Q_CN0540 | 1.3333 | 0 | Qld Central to North upper transfer limit of 540 MW (discretionary) | Outage | Qld
V^^S_TBTX+CB_SETB_2 | 1.3333 | 0 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
NC_V_YWPS1 | 1.25 | 3.5 | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Other | Non-Conformance
NQTE_-070 | 1.25 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW | Outage | NSW
N_BLOWERNG_ZERO | 1.25 | 0.41667 | Blowering generation upper limit of 0 MW | Outage | NSW
S_SECB_LG3 | 1.25 | 12.6667 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
V::S_NIL_SETB_SECP_1 | 1.25 | 0.5 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
V_GANNAWR_ZERO | 1.25 | 0 | Gannawarra solar farm upper limit of 0 MW | Outage | Vic
V_MTMERCER_ZERO | 1.25 | 17.8333 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
NC_Q_MPP_2 | 1.1667 | 1.6667 | Non Conformance Constraint for Millmerran 2 Power Station | Other | Non-Conformance
N_BROKENH1_ZERO | 1.1667 | 6 | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
S>>PATW_NIL_WEMWP4 | 1.1667 | 0 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
T_T_FA_TX_1 | 1.1667 | 0 | Out = Farrell 220/110kV transformer, limit Mackintosh <= 110% of West Coast load | Outage | Tas
V>>V_ROTS_TX_3A_R | 1.1667 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
V^^S_SEVC1_SETB | 1.1667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | SA
N>>N-NIL_01N | 1.0833 | 0.16667 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
NC_N_MP1 | 1.0833 | 1.4167 | Non Conformance Constraint for Mt Piper 1 Power Station | Other | Non-Conformance
Q_CS_1950 | 1.0833 | 0 | Qld Central to Qld South upper transfer limit of 1950MW (discretionary) | Outage | Qld
S>>MKRB_NIL_WEMWP4 | 1.0833 | 0 | Out= Mokota-Robertstown 275kV line,, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
S>PATW_BWPA_HUWT | 1.0833 | 0 | Out= Para-Templers West 275kV line, avoid O/L Hummocks- Waterloo132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T_V_FCSPS_RAMP | 1.0833 | 0 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
V>>DDSH_DDGN_N-2 | 1.0833 | 1.3333 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
#BASTYAN_E | 1 | 0 | TFA11.ENERGY * 1 <= 44 (Wt = 360) | Other | Quick
N_MBTE1_A | 1 | 0.083333 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
Q::NIL_CS | 1 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW), 2008/2009 implementation | NIL | Qld
QN_ZERO | 1 | 0 | Qld to NSW on QNI upper transfer limit of 0 MW | Outage | Qld
Q_RS_200 | 1 | 0 | Qld, Ross cutset upper limit of 200MW (discretionary) | Outage | Qld
S>>BRTW_NIL_WEMWP4 | 1 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
S>NIL_BWMP_HUWT | 1 | 1.1667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
V:T_HAPM_BL_1 | 1 | 0 | Out = Hadspen to Palmerston 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to Palmerston 220 kV line, Tamar CCGT out of service | Outage | Vic
CA_MQS_49FC5770_02 | 0.91667 | 0 | Constraint Automation, O/L HADSPEN TRANSF T1 for CTG TTAG on trip of HADSPEN #2 220/110KV TRANSFORMER. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
N>>V-LTMS_5 | 0.91667 | 0 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage | NSW
NC_N_TALWA1 | 0.91667 | 2.9167 | Non Conformance Constraint for Tallawarra Power Station | Other | Non-Conformance
N::V_DDMS | 0.83333 | 1.6667 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage | NSW
NC_N_MP2 | 0.83333 | 0.91667 | Non Conformance Constraint for Mt Piper 2 Power Station | Other | Non-Conformance
NC_Q_STAN-1 | 0.83333 | 0.5 | Non Conformance Constraint for Stanwell STAN-1 Power Station | Other | Non-Conformance
NC_V_YWPS3 | 0.83333 | 0.66667 | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Other | Non-Conformance
NQTE_-010 | 0.83333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -10 MW | Outage | NSW
S_LB3_0 | 0.83333 | 0 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
S_LB_1+2+3_230 | 0.83333 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=230 MW | Outage | SA
#MSTUART2_D_E | 0.75 | 12.25 | QMSP2.ENERGY * 1 = 30 (Wt = 755) | Other | Quick
NC_N_HUMENSW | 0.75 | 0.58333 | Non Conformance Constraint for Hume Hydro Power Station | Other | Non-Conformance
NC_Q_BRAEMAR3 | 0.75 | 2.9167 | Non Conformance Constraint for Braemar 3 Power Station | Other | Non-Conformance
S>NIL_HUWT_STBG | 0.75 | 97 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=60 MW when Dalymple Battery (i.e. both Gen and Load component) is O/S] | NIL | SA
S>X_RBPA+CB_06 | 0.75 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage | SA
S_LB_1+2+3_150 | 0.75 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=150 MW | Outage | SA
V>>V_MLTS_TX_2A_R | 0.75 | 0 | Out = Moorabool A1 or A2 500/220kV transformer, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage | Vic
V>>V_SMTT2_2 | 0.75 | 0 | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the Thomastown to South Morang No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
VSML_-040 | 0.75 | 0.33333 | Vic to SA on ML upper transfer limit of -40 MW | Outage | Vic
#CROOKWF2_E | 0.66667 | 0 | NCKW1C.ENERGY * 1 <= 61 (Wt = 360) | Other | Quick
#MSTUART1_D_E | 0.66667 | 0 | QMSP1.ENERGY * 1 = 45 (Wt = 755) | Other | Quick
#V-SA_RAMP_I_F | 0.66667 | 0.58333 | V-SA >= MIN(-65, InitialFlow + 50) (Wt=35) | Other | Quick
N>>N-X_WGYS_99M_992 | 0.66667 | 0 | Out = Out = Murrumburrah to Yass 132kV line (99M) and Burrinjuck to Tumut132 132kV line (992), avoid Lower Tumut to Wagga 330kV (051) O/L on Murray - Dederang 330kV (67 or 68) trip with DBUSS action | Outage | NSW
NC_Q_STAN-3 | 0.66667 | 2.3333 | Non Conformance Constraint for Stanwell STAN-3 Power Station | Other | Non-Conformance
NC_Q_SWAN_E | 0.66667 | 0.75 | Non Conformance Constraint for Swanbank E Power Station | Other | Non-Conformance
NC_V_HUMEV | 0.66667 | 0 | Non Conformance Constraint for Hume Power Station | Other | Non-Conformance
S_LB2WF_CONF | 0.66667 | 1.25 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
S_V_NIL_ROCOF | 0.66667 | 10.75 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | SA
T_TAMAR_GCS_OUT | 0.66667 | 0 | Out = Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) - Limit output of Tamar Valley CCGT to 144 MW. | Outage | Tas
V::S_SEVC1_MAXG | 0.66667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
VS_250_DYN | 0.66667 | 10.5 | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Vic
#MTGELWF1_E | 0.58333 | 0 | VGTW1M.ENERGY * 1 <= 66 (Wt = 360) | Other | Quick
I_CTRL_ISSUE_ML | 0.58333 | 0.41667 | DC Link Control Issue Constraint for Murraylink | Outage | Other
NC_N_LD04 | 0.58333 | 0 | Non Conformance Constraint for Liddell LD04 Power Station | Other | Non-Conformance
NC_N_PARSF1 | 0.58333 | 0 | Non Conformance Constraint for Parkes Solar Farm | Other | Non-Conformance
NC_N_URANQ14 | 0.58333 | 0 | Non Conformance Constraint for Uranquinty 4 Power Station | Other | Non-Conformance
NC_Q_CSPVPS1 | 0.58333 | 0 | Non Conformance Constraint for C'VILLE SOLAR PV 1 | Other | Non-Conformance
NC_Q_GSTONE3 | 0.58333 | 0.083333 | Non Conformance Constraint for Gladstone 3 Power Station | Other | Non-Conformance
NC_Q_TARONG#1 | 0.58333 | 0.083333 | Non Conformance Constraint for Tarong 1 Power Station | Other | Non-Conformance
NC_T_JBUTTERS | 0.58333 | 0 | Non Conformance Constraint for John Butters Power Station | Other | Non-Conformance
NC_V_LYA2 | 0.58333 | 0.16667 | Non Conformance Constraint for Loy Yang A2 Power Station | Other | Non-Conformance
S:VS_PA_SVC_570 | 0.58333 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage | SA
T>T_PMSH_2A | 0.58333 | 1.0833 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow to George Town) for trip of the other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
T>T_X_BWLF_PMWA110_2 | 0.58333 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana AND Palmerston to Waddamana 110kV lines, avoid O/L Tungatinah to Meadowbank Tee2 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
V::N_JNWG_xxx | 0.58333 | 0 | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
#COLEASF1_E | 0.5 | 0 | NCLS1C.ENERGY * 1 <= 150 (Wt = 360) | Other | Quick
NC_N_BW01 | 0.5 | 0.16667 | Non Conformance Constraint for Bayswater 1 Power Station | Other | Non-Conformance
NC_Q_YABULU2 | 0.5 | 0.91667 | Non Conformance Constraint for Yabulu 2 Power Station | Other | Non-Conformance
NC_S_PPCCGT | 0.5 | 1.3333 | Non Conformance Constraint for Pelican Point Power Station | Other | Non-Conformance
NC_V_YWPS4 | 0.5 | 0.5 | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Other | Non-Conformance
N_V_HV1075 | 0.5 | 0 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 1075 MW | Outage | NSW
S>>BLMK_NIL_WEMWP4 | 0.5 | 0.66667 | Out= Belalie-Mokota 275kV line (This offloads Willalow substation and Willagoleche WF) OR Belalie-Willalow 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on Nil trip, Feedback | NIL | SA
S>RBPA_BWMP_HUWT | 0.5 | 0 | Out= Robertstown-Para 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | SA
T>T_HAPM_220_5A | 0.5 | 0 | Out = Hadspen to Palmerston 220kV line, avoid O/L either Palmerston to Hadspen (No. 3 or No. 4) 110kV line (flow to North) for loss of the remaining Hadspen to Palmerston 220kV line, Feedback | Outage | Tas
V>>V_NIL_3 | 0.5 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL | Vic
V>>V_ROTS_TX_3B_R | 0.5 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage | Vic
V^^S_KNPW_MAXG | 0.5 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
#BALBL1_E | 0.41667 | 0 | VBA22B.ENERGY * 1 <= 10 (Wt = 360) | Other | Quick
#NSW1-QLD1_RAMP_E_F | 0.41667 | 0.33333 | NSW1-QLD1 <= MAX(73, InitialFlow - 200) (Wt=35) | Other | Quick
N>Q-MUTW_2 | 0.41667 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage | NSW
NC_N_BW04 | 0.41667 | 0 | Non Conformance Constraint for Bayswater 4 Power Station | Other | Non-Conformance
NC_N_STWF1 | 0.41667 | 0 | Non Conformance Constraint for SILVERTON WIND FARM | Other | Non-Conformance
NC_Q_CPSA | 0.41667 | 1.8333 | Non Conformance Constraint for Condamine Power Station | Other | Non-Conformance
NC_Q_TARONG#2 | 0.41667 | 0.41667 | Non Conformance Constraint for Tarong 2 Power Station | Other | Non-Conformance
NQ_ZERO | 0.41667 | 0 | NSW to Qld on QNI upper transfer limit of zero MW | Outage | NSW
Q>>LCCP_BCCP_CLWU_2 | 0.41667 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Qld
Q_CN1200 | 0.41667 | 0 | Qld Central to North upper transfer limit of 1200 MW (discretionary) | Outage | Qld
S>>NIL_HUBG-T_WEWT2 | 0.41667 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Hummocks-Snowtown-Bungama 132kV T line (this trips Snowtown WF).[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
S>NIL_HUWT_STBG2 | 0.41667 | 0 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
SA_HYSE2 | 0.41667 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
T>T_HAPM_IMP_4A | 0.41667 | 0 | Out = Hadspen to Palmerston No. 2 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
V::S_BLKRG_TBSE_2 | 0.41667 | 0.5 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
V::S_KHKN_MAXG | 0.41667 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
V>>S_MOTB_TBCG_TBTU | 0.41667 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage | SA
VSML_020 | 0.41667 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage | Vic
V_MORTLAKE12_ZERO | 0.41667 | 1.0833 | Mortlake unit 1 & 2 upper limit of 0 MW | Outage | Vic
#SA1_E_20180728 | 0.33333 | 0 | Multiple SA1 LHS <= 200 (Wt = 35) | Other | Quick
#T-V-MNSP1_RAMP_E_F | 0.33333 | 0.33333 | T-V-MNSP1 <= MAX(0, InitialFlow - 200) (Wt=35) | Other | Quick
CA_MQS_49FC5770_01 | 0.33333 | 0 | Constraint Automation, O/L PALMSTN TRANSF T1 for CTG TTAG on trip of HADSPEN #2 220/110KV TRANSFORMER. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
NC_N_ER01 | 0.33333 | 0.41667 | Non Conformance Constraint for Eraring ER01 Power Station | Other | Non-Conformance
NC_N_ER03 | 0.33333 | 0 | Non Conformance Constraint for Eraring ER03 Power Station | Other | Non-Conformance
NC_N_SHGEN | 0.33333 | 0 | Non Conformance Constraint for Shoalhaven Power Station | Other | Non-Conformance
NC_V_MTGELWF1 | 0.33333 | 0 | Non Conformance Constraint for MT GELLIBRAND WF | Other | Non-Conformance
Q>CLWU_BCCP | 0.33333 | 0 | Constraint Automation, O/L 275KV_812 @H10_BCMB for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
Q_MEWF1_ZERO | 0.33333 | 0 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Qld
T>>T_NIL_BL_EXP_5F | 0.33333 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_HAPM_5A | 0.33333 | 0 | Out = Hadspen to Palmerston No. 2 220 kV line, avoid O/L line terminal equipment of Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line, feedback | Outage | Tas
V::N_SM330_2B_V22 | 0.33333 | 0 | Out = South Morang No.2 330kV bus, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage | Vic
V>>V_KTS_TX_A2_2B_R | 0.33333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Vic
N>N-BAMB_132_OPEN_A | 0.25 | 0.58333 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | NSW
NC_N_BW02 | 0.25 | 0 | Non Conformance Constraint for Bayswater 2 Power Station | Other | Non-Conformance
NC_N_ER04 | 0.25 | 0.083333 | Non Conformance Constraint for Eraring ER04 Power Station | Other | Non-Conformance
NC_Q_BARRON-2 | 0.25 | 0.083333 | Non Conformance Constraint for Barron Gorge 2 Power Station | Other | Non-Conformance
NC_Q_GSTONE1 | 0.25 | 0 | Non Conformance Constraint for Gladstone 1 Power Station | Other | Non-Conformance
NC_Q_TNPS1 | 0.25 | 0.83333 | Non Conformance Constraint for Tarong North Power Station | Other | Non-Conformance
NC_S_AGLHAL | 0.25 | 0 | Non Conformance Constraint for AGL Hallet Power Station | Other | Non-Conformance
NC_S_DALNTH01 | 0.25 | 0 | Non Conformance Constraint for Dalrymple Battery (Generation Component) | Other | Non-Conformance
NC_T_POAT220 | 0.25 | 0.083333 | Non Conformance Constraint for Poatina 220kV Power Station | Other | Non-Conformance
NC_V_JLA04 | 0.25 | 0 | Non Conformance Constraint for Jeeralang A - 04 Power Station | Other | Non-Conformance
NC_V_LOYYB2 | 0.25 | 1.0833 | Non Conformance Constraint for Loy Yang B2 Power Station | Other | Non-Conformance
NRM_VIC1_SA1 | 0.25 | 4.75 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
N^^Q_MUTW_1_B1 | 0.25 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage | NSW
N_SILVERWF_WT | 0.25 | 0 | Limit number of turbine online for Silverton wind farm to not exceed 13 with Broken Hill solar generating | Outage | NSW
Q>>PWSP_WOSP_PWCE | 0.25 | 0 | Out= Palmwoods to South Pine (808) line, avoid O/L Palmwood to Caboolture (746/4) 110kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
Q>N-MUTE_757 | 0.25 | 30.3333 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
Q_CLARESF1_ZERO | 0.25 | 0 | Clare solar farm upper limit of 0 MW | Outage | Qld
Q_RS_560 | 0.25 | 0 | Qld, Ross cutset upper limit of 560MW (discretionary) | Outage | Qld
S>>NIL_RBTU_WEWT | 0.25 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
S>KNPW_SETX_SETX1 | 0.25 | 0 | Out=Penola West-Kincraig 132kV line, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | Outage | SA
T>T_HATX_PMWAIM_4D | 0.25 | 0 | Out = Hadspen 220/110 kV txfmr and Palmerston to Waddamana 110kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T_FATI | 0.25 | 0.16667 | Out=Farrell-Tribute 220KV line. Energy <= 0MW | Outage | Tas
V::N_MLSY_xxx | 0.25 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>SML_NSWRB_9 | 0.25 | 0.16667 | Out = NSW Murraylink runback scheme, avoid O/L of Bendigo to Kerang 220 kV line for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
V^SML_HORC_2 | 0.25 | 0 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage | Vic
V_EILDON2_000 | 0.25 | 0 | Discretionary upper limit for Eildon unit 2 of 0 MW | Outage | Vic
V_MTGELIBRAND_ZERO | 0.25 | 0 | Mt Gelibrand wind farm upper limit of 0 MW | Outage | Vic
V_S_NIL_ROCOF | 0.25 | 134.4167 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | Vic
#V-S-MNSP1_E_E | 0.16667 | 0 | V-S-MNSP1. * 1 <= 190 (Wt = 35) | Other | Quick
#WGWF1_E | 0.16667 | 0 | SWGL1W.ENERGY * 1 <= 83 (Wt = 360) | Other | Quick
N>>Q_LDMU_B | 0.16667 | 13.1667 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage | NSW
N>N-KKLS_TE_2 | 0.16667 | 0.16667 | Out= Koolkhan to Lismore (967), avoid O/L Glen Innes to Tenterfield (96R) on trip of Coffs Harbour to Lismore (89), swamp out when all 3 directlink O/S, Feedback, TG formulation on PD & ST | Outage | NSW
N>N-LSTN_TE_C1 | 0.16667 | 0 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
NC_N_LD01 | 0.16667 | 0 | Non Conformance Constraint for Liddell LD01 Power Station | Other | Non-Conformance
NC_N_LD02 | 0.16667 | 0 | Non Conformance Constraint for Liddell LD02 Power Station | Other | Non-Conformance
NC_N_URANQ12 | 0.16667 | 0 | Non Conformance Constraint for Uranquinty 2 Power Station | Other | Non-Conformance
NC_Q_GSTONE4 | 0.16667 | 0.083333 | Non Conformance Constraint for Gladstone 4 Power Station | Other | Non-Conformance
NC_Q_GSTONE5 | 0.16667 | 1.8333 | Non Conformance Constraint for Gladstone 5 Power Station | Other | Non-Conformance
NC_Q_GSTONE6 | 0.16667 | 0.083333 | Non Conformance Constraint for Gladstone 6 Power Station | Other | Non-Conformance
NC_Q_MPP_1 | 0.16667 | 1 | Non Conformance Constraint for Millmerran 1 Power Station | Other | Non-Conformance
NC_Q_STAN-2 | 0.16667 | 1.5833 | Non Conformance Constraint for Stanwell STAN-2 Power Station | Other | Non-Conformance
NC_Q_TARONG#4 | 0.16667 | 0.66667 | Non Conformance Constraint for Tarong 4 Power Station | Other | Non-Conformance
NC_S_HDWF3 | 0.16667 | 0 | Non Conformance Constraint for Hornsdale 3 Wind Farm | Other | Non-Conformance
NC_S_MINTARO | 0.16667 | 0.58333 | Non Conformance Constraint for Mintaro Gas Turbine | Other | Non-Conformance
NC_V_BDL02 | 0.16667 | 0.16667 | Non Conformance Constraint for Bairnsdale 2 Power Station | Other | Non-Conformance
NC_V_LYA4 | 0.16667 | 0 | Non Conformance Constraint for Loy Yang A4 Power Station | Other | Non-Conformance
Q>>BCCP_CLWU_BCRG_2 | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Raglan (811) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
Q>>LCCP_CLWU_BCCP | 0.16667 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871), Feedback | Outage | Qld
Q^CN_FDR-180 | 0.16667 | 0 | Nominated Offset = -180MW, Central Qld to North Qld Voltage stability limit, Feeder trip equation, 2009/10 implementation. | Outage | Qld
S>>BRTW_BWPA_WTTP | 0.16667 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>>MKRB_BWPA_BRTW | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S>KNPW_NIL_SETX12 | 0.16667 | 0 | Out=Penola West-Kincraig 132kV line, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
T>>T_NIL_BL_EXP_7C | 0.16667 | 25.9167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_FASH_2_N-2 | 0.16667 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.2 transformer | Outage | Tas
T>T_GTSH_2A | 0.16667 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow North) for trip of other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
T>T_PMSH_IMP_4A | 0.16667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_PMWA_110_2 | 0.16667 | 0 | Out= Palmerston to Waddamana 110 kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Waddamana to Bridgewater 110kV line, Feedback | Outage | Tas
V::N_BURC_xxx | 0.16667 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V::N_MLTX_xxx | 0.16667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V>>BABE_DDGN_N-2 | 0.16667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage | Vic
V>>N_SM330_2B_3 | 0.16667 | 0 | Out = South Morang F2 500/330 kV and either H1 or H2 330/220 kV txfmr, SMTS 220kV bus tied, avoid O/L Ballarat to Bendigo 220kV line on trip of South Morang H2 or H1 220/330kV transformer, Feedback | Outage | Vic
V>>N_SMHTX_1 | 0.16667 | 0 | Out = South Morang H 330/220 kV txfmr, only one SMTS H txfmr in service, avoid O/L the remaining in service SMTS H 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V>>V_NIL1A_R | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL | Vic
VSML_040 | 0.16667 | 0 | Vic to SA on ML upper transfer limit of 40 MW | Outage | Vic
V^^S_NIL_TBSE_2 | 0.16667 | 0 | Out = Nil(Note: with one or both Black Range series capacitors O/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
V_MACARTHUR_ZERO | 0.16667 | 20.5833 | Macarthur upper limit of 0 MW | Outage | Vic
V_MTGBRAND_22WT | 0.16667 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 22 | Outage | Vic
S-LB2_0 | 0.16667 | 0 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
CA_SPS_4A3DEF97_02 | 0.083333 | 0 | Constraint Automation, O/L HWTS TRANSF A2TR_500 for CTG TVVN on trip of HWPS-HWTS4 220KV LINE & HWTS A4 TR. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
N::Q_MUTW_1 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | NSW
NC_Q_BARRON-1 | 0.083333 | 0 | Non Conformance Constraint for Barron Gorge 1 Power Station | Other | Non-Conformance
NC_Q_BRAEMAR1 | 0.083333 | 0.75 | Non Conformance Constraint for Braemar 1 Power Station | Other | Non-Conformance
NC_Q_KAREEYA4 | 0.083333 | 0 | Non Conformance Constraint for Kareeya 4 Power Station | Other | Non-Conformance
NC_Q_MACKAYGT | 0.083333 | 0 | Non Conformance Constraint for Mackay Gas Turbine | Other | Non-Conformance
NC_S_BNGSF1 | 0.083333 | 0 | Non Conformance Constraint for Bungala #1 Solar Farm | Other | Non-Conformance
NC_S_QPS5 | 0.083333 | 0.16667 | Non Conformance Constraint for Quarantine QPS5 Power Station | Other | Non-Conformance
NC_S_TORRB3 | 0.083333 | 0.16667 | Non Conformance Constraint for Torrens B3 Power Station | Other | Non-Conformance
NC_S_WGWF1 | 0.083333 | 0 | Non Conformance Constraint for Willogoleche Wind Farm | Other | Non-Conformance
NC_T_LI_WY_CA | 0.083333 | 0 | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations | Other | Non-Conformance
NC_T_TVCC201 | 0.083333 | 0 | Non Conformance Constraint for Tamar Valley 220 kV CCGT | Other | Non-Conformance
NC_V_GANNBG1 | 0.083333 | 0 | Non Conformance Constraint for GANNAWARRA BATT GEN | Other | Non-Conformance
NC_V_JLB01 | 0.083333 | 0 | Non Conformance Constraint for Jeeralang B - 01 Power Station | Other | Non-Conformance
NC_V_MORTLK12 | 0.083333 | 0 | Non Conformance Constraint for Mortlake GT unit 2 | Other | Non-Conformance
NQTE_-080 | 0.083333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -80 MW | Outage | NSW
N^^Q_ARTW_B1 | 0.083333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
Q:N_NIL_OSC | 0.083333 | 19.4167 | Out= Nil, QNI oscillatory stability limit of 1200 MW, limit reduced to 950 MW when any one SEQ SVC POD is out, limit is reduced to 853 MW when all three SEQ SVCs or PODs out. | NIL | Qld
QNTE_150 | 0.083333 | 19.6667 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW | Outage | Qld
Q_KSP1_ZERO | 0.083333 | 0 | Kidston solar farm upper limit of 0 MW | Outage | Qld
Q_RS_160 | 0.083333 | 0 | Qld, Ross cutset upper limit of 160MW (discretionary) | Outage | Qld
S>>BWMP_TWPA_TPRS | 0.083333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
S>>KNPW_SETB_SETB | 0.083333 | 0 | Out= Penola West-Kincraig 132 kV line (Note: with both Black Range series caps I/S or O/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage | SA
S>>MOTB_TBTU_TBCG | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
S>>PARB_TWPA_TPRS | 0.083333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
S>>V_MOTB_TUTB_CGTB | 0.083333 | 0 | Out=Mobilong - Tailem Bend 132kV line; avoid O/L Cherry Gardens -Tailem Bend 275kV on trip Tungkillo -Tailem Bend 275kV line, Feedback | Outage | SA
S>KHKN_NIL_SETX12 | 0.083333 | 0 | Out=Keith-Kincraig 132kV line, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
S>NIL_LKDV_CNRB | 0.083333 | 0.58333 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
S>VMLMHNW1 | 0.083333 | 0 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | SA
S>WIMK_BWPA_HUWT | 0.083333 | 0 | Out= Willalow-Mokota 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
T>>T_HAPM_EXP_3A | 0.083333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_GTSH_2C | 0.083333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
T>T_NIL_BL_3A | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Palmerston to Hadspen No. 1 220kV line (flow to North), feedback | NIL | Tas
T>T_NIL_BL_3B | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Palmerston to Hadspen No. 2 220kV line (flow to North), feedback | NIL | Tas
T>T_NIL_BL_IMP_3G | 0.083333 | 0 | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Sheffield 220 kV line with no SPS action, feedback | NIL | Tas
T>T_NIL_BL_IMP_3H | 0.083333 | 0 | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of either Sheffield to Georgetown 220 kV line with no SPS action, feedback | NIL | Tas
T>T_NIL_BL_IMP_6EE | 0.083333 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
T>T_PMWA_110_12_1 | 0.083333 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | Outage | Tas
T>T_PMWA_110_7 | 0.083333 | 0 | Out= Palmerston to Waddamana 110 kV line, avoid overloading the New Norfolk to Chapel St 110 kV line (flow to South) on trip of New Norfolk to Creek Road 110 kV line, feedback | Outage | Tas
T>T_PMWA_IMP_4D | 0.083333 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_PMWA_IMP_4DD | 0.083333 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 2 220 kV line on trip of the Palmerston to Hadspen No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_PMWA_IMP_4DDD | 0.083333 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Sheffield to Palmerston 220 kV line with no NCSPS action, feedback | Outage | Tas
T_FAMA | 0.083333 | 0 | Out=Farrell-Mackintosh 110KV line. Energy <= 0MW | Outage | Tas
T_FARC1 | 0.083333 | 0 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
T_MB_ZERO | 0.083333 | 0 | Limit Meadowbank to zero MW | Outage | Tas
V:SS_820_HY_TEST_DYN | 0.083333 | 6.5 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
V>>SML_NIL_8 | 0.083333 | 2.0833 | Out = Nil, avoid O/L Ballarat to Bendigo 220 kV line (flow North) for loss of Shepparton to Bendigo 220 kV line, 15 minute line ratings, feedback | NIL | Vic
V>>V_DDTX_C | 0.083333 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage | Vic
V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
V>SMLARHO3 | 0.083333 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Kerang to Wemen 220 kV line section on loss of Balranald to Darlington Point (X5/1) line | Outage | Vic
V>SMLARHO4 | 0.083333 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
V^SML_NIL_3 | 0.083333 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Vic
V^^S_MLSY_3 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
V_MTGBRAND_33WT | 0.083333 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 33 | Outage | Vic

## Binding FCAS
Constraint Equation ID | 2018 Hours | 2017 Hours | Description | Type
F_I+NIL_APD_TL_L5 | 6258.1667 | 3631.6667 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R5 | 5646.9167 | 7929.5 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL
F_I+NIL_APD_TL_L60 | 5400.25 | 3281.75 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL
F_I+NIL_MG_R6 | 4569.5 | 7512.9167 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL
F_I+NIL_MG_R60 | 4449.6667 | 7166 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL
F_I+LREG_0120 | 3998.0833 | 6988.9167 | NEM Lower Regulation Requirement greater than 120 MW | NIL
F_MAIN++NIL_MG_R60 | 2546.4167 | 1562.25 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R6 | 2404.3333 | 1139.6667 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_I+NIL_RREG | 2288.25 | 7314 | NEM Raise Regulation Requirement | NIL
F_T+LREG_0050 | 2258 | 483.25 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_T+NIL_ML_L6 | 2240.0833 | 483.25 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 2186.0833 | 483.25 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 2184.0833 | 483.3333 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 2182.9167 | 483.3333 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_T+NIL_ML_L60 | 2162.5 | 481.8333 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_I+ML_L6_0400 | 2092.4167 | 4516.3333 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN+TASCAP_LREG | 2077.1667 | 675.8333 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_T+NIL_ML_L5 | 1914.0833 | 184.0833 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L5 | 1893.0833 | 178.5 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_MAIN+APD_TL_L60 | 1870.6667 | 178.0833 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL
F_T+RREG_0050 | 1705.8333 | 497.1667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN+LREG_0120 | 1692.3333 | 431.75 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 1667.9167 | 1139.1667 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
F_MAIN++APD_TL_L5 | 1644.5833 | 1308.3333 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_MAIN+ML_L6_0400 | 1618.3333 | 466.25 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T_AUFLS2_R6 | 1491.1667 | 0 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL
F_T+NIL_MG_RECL_R60 | 1368.75 | 1115.9167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_RECL_R6 | 1344.5 | 1092.5833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN++APD_TL_L60 | 1332.8333 | 851.8333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
F_I+LREG_0150 | 1324.25 | 0 | NEM Lower Regulation Requirement greater than 150 MW | NIL
F_T+NIL_MG_R60 | 1318.5833 | 1220.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T_NIL_MINP_R6 | 1274.9167 | 0 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL
F_T+NIL_MG_RECL_R5 | 1243 | 718.25 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R6 | 1221.9167 | 1325.1667 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R60 | 1111.6667 | 1136.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_DYN_RREG | 1072.3333 | 869.5833 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL
F_T+NIL_WF_TG_R6 | 1066.8333 | 1204.9167 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T++NIL_ML_L6 | 1035.6667 | 119.25 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_T+NIL_WF_TG_R5 | 937.6667 | 864.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R5 | 933.5 | 762.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_RREG | 772.0833 | 424.9167 | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL
F_T++LREG_0050 | 733.0833 | 93.0833 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_MAIN++ML_L6_0400 | 687.5 | 2107.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T++NIL_ML_L60 | 673.9167 | 205.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_T++RREG_0050 | 572.1667 | 1154.6667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_MAIN+NIL_DYN_LREG | 535 | 862.25 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL
F_MAIN++LREG_0120 | 378.0833 | 1335.4167 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
F_MAIN+TASCAP_RREG | 233.5833 | 436.1667 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL
F_I+ML_L6_APD | 173.1667 | 142 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_T++NIL_MG_RECL_R60 | 162.75 | 270.5833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++NIL_MG_RECL_R6 | 157.5833 | 264.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_Q++MUTW_L6 | 139.9167 | 37.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
F_Q++MUTW_L60 | 129.25 | 36.5 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage
F_Q++MUTW_L5 | 128.5 | 28.0833 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
F_MAIN++ML_L6_APD | 109.5833 | 17.6667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_T++NIL_WF_TG_R60 | 107.3333 | 143.1667 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_I+NIL_MG_R5_PPN2 | 90.0833 | 0 | Out = Nil, Raise 5 min requirement for a NEM Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible) | NIL
F_Q++ARTW_L6 | 83.5833 | 62.25 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
F_Q++BCDM_L6 | 82.9167 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
F_Q++BCDM_L60 | 82.8333 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage
F_MAIN++NIL_MG_R6_PP | 82.3333 | 0 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R60_P | 82.25 | 0 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST t PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL
F_T++NIL_WF_TG_R6 | 80.9167 | 123.5 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+NIL_MG_R5_PP | 77.25 | 0 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R6_PP | 76.1667 | 0 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink unable transfer FCAS | NIL
F_T++NIL_WF_TG_R5 | 74.5 | 55.6667 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN+NIL_MG_R60_PP | 74.1667 | 0 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink unable transfer FCAS | NIL
F_Q++BCDM_L5 | 74.1667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
F_Q++ARTW_L60 | 73.75 | 61.5833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_T++NIL_ML_L5 | 72.6667 | 21.5 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
F_T++NIL_MG_RECL_R5 | 69.0833 | 88.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_MAIN++LREG_0150 | 66.4167 | 0 | Mainland Lower Regulation Requirement greater than 150 MW, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R5_PP | 65.4167 | 0 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5STt PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL
F_Q++ARTW_L5 | 64.4167 | 38.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
F_MAIN++NIL_RREG | 61.0833 | 87.6667 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
F_I+NIL_MG_R6_PPN2 | 60.5 | 0 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible) | NIL
F_T++NIL_MG_R60 | 59.75 | 57.4167 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_I+NIL_MG_R60_PPN2 | 59.1667 | 0 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible) | NIL
F_MAIN+LREG_0150 | 46.5 | 0 | Mainland Lower Regulation Requirement greater than 150 MW, Basslink unable to transfer FCAS | NIL
F_T++NIL_MG_R6 | 43.6667 | 56.9167 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_I+WIP_N-2_ML_L6 | 29.5833 | 15.6667 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage
F_Q++8C_L6 | 26.9167 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
F_T+FASH_N-2_RREG | 26.6667 | 10.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_I+ML_L5_0400 | 26 | 3037.4167 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL
F_Q++LDMU_L6 | 23.9167 | 5.1667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
F_Q++LDMU_L60 | 23.1667 | 5.25 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage
F_I+ML_L5_APD | 20.5 | 21 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_Q++LDMU_L5 | 20.4167 | 2.9167 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
F_T++NIL_MG_R5 | 20.3333 | 20.25 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
F_T++COGT_TL_L60 | 19.5 | 0.083333 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T++COGT_TL_L5 | 19.5 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T++COGT_TL_L6 | 19.5 | 2.8333 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_I+ML_L60_APD | 18.5833 | 20.25 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage
F_S+LREG_0035 | 17.8333 | 158.5833 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage
F_S+RREG_0035 | 17.5833 | 155.75 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage
F_Q++8C_L5 | 16.6667 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
F_T+FASH1_2C_RREG | 16.3333 | 0 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage
F_Q++8C_L60 | 16.0833 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage
F_T+FASH_N-2_TG_R6_1 | 12.9167 | 2.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage
F_I+ML_L60_0400 | 12.8333 | 1534.8333 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL
F_MAIN++ML_L60_APD | 11.6667 | 5.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_MAIN++ML_L5_APD | 9.9167 | 9.9167 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_S++HYSE_L6_1 | 9.4167 | 62.3333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
F_S++HYSE_L60 | 8.5 | 45.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
F_Q++ARDM_L6 | 8.25 | 107.25 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
F_Q++ARDM_L60 | 8.25 | 108.0833 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage
F_Q_TARONG#2_R60 | 8.0833 | 2.3333 | Out= NIL, Tarong 2 R60 Requirement <= 0MW | Outage
F_Q_TARONG#2_RREG | 8.0833 | 0.16667 | Out= NIL, Tarong 2 RREG Requirement <= 0MW | Outage
F_Q_TARONG#2_R5 | 7.6667 | 0 | Out= NIL, Tarong 2 R5 Requirement <= 0MW | Outage
F_MAIN+ML_L6_APD | 7.5 | 2.1667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_Q_TARONG#2_R6 | 7 | 0.33333 | Out= NIL, Tarong 2 R6 Requirement <= 0MW | Outage
F_Q_TARONG#1_R60 | 6.4167 | 1.9167 | Out= NIL, Tarong 1 R60 Requirement <= 0MW | Outage
F_Q_TARONG#1_RREG | 6.4167 | 0.16667 | Out= NIL, Tarong 1 RREG Requirement <= 0MW | Outage
F_Q_TARONG#1_R5 | 6.25 | 0 | Out= NIL, Tarong 1 R5 Requirement <= 0MW | Outage
F_T+FASH_N-2_TG_R60 | 6 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T++FASH1_2C_TG_R5 | 5.8333 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage
F_Q_TARONG#1_R6 | 5.5 | 0.33333 | Out= NIL, Tarong 1 R6 Requirement <= 0MW | Outage
F_Q++ARDM_L5 | 5.3333 | 91.8333 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
F_T++BLSPS_EXP_L5 | 4.5833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
F_T+FASH_N-2_TG_R5 | 4.4167 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_MAIN+ML_L5_0400 | 4 | 323.1667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_T++BLSPS_EXP_L6_2 | 3.8333 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage
F_T++BLSPS_EXP_L60_2 | 3.75 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2 | Outage
F_MAIN++WIP_N-2_MLL6 | 3.75 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage
F_MAIN+ML_L60_0400 | 3.6667 | 275.75 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_I+WIP_N-2_ML_L5 | 3.5833 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 5 Min requirement | Outage
F_V+NIL_APD01_R5 | 3.5833 | 3.9167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_APD01_L60 | 3.5833 | 3.1667 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_V+NIL_APD01_L5 | 3.5833 | 3.8333 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_APD01_R6 | 3.5 | 3.9167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_MAIN++ML_L5_0400 | 3.5 | 1528.75 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T++FASH_N-2_TG_R60 | 3.5 | 5.4167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_V+NIL_APD01_L6 | 3.4167 | 3.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_I+WIP_N-2_ML_L60 | 3.4167 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 60 sec requirement | Outage
F_V+NIL_APD01_R60 | 3.4167 | 4.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_T+FARE_N-2_TG_R5 | 2.5833 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage
F_T++FASH1_2C_TG_R60 | 2.5 | 0 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage
F_T+FARE_N-2_TG_R6_2 | 2.5 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage
F_MAIN++NIL_BL_L60 | 2.4167 | 1749.4167 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
F_ESTN++HYTR_L5 | 2.4167 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_ESTN++HYTR_L60 | 2.4167 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_T++FASH_N-2_TG_R5 | 2.25 | 1.1667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_T+COGT_TL_L5 | 2.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_T+COGT_TL_L6 | 2.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_T+COGT_TL_L60 | 2.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage
F_T++GTTE_TL_L6 | 2.0833 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q_TARONG#2_LREG | 1.9167 | 0 | Out= NIL, Tarong 2 LREG Requirement <= 0MW | Outage
F_MAIN++ML_L60_0400 | 1.8333 | 281.6667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
F_T++FASH_N-2_TG_R6 | 1.75 | 4 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_Q++NIL_R5 | 1.5833 | 1.0833 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
F_T+FARE_N-2_TG_R6_1 | 1.5 | 0.66667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage
F_Q+KC_R5 | 1.4167 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Kogan Creek) | Outage
F_Q+MG_R5 | 1.4167 | 0 | Raise 5 min Service Requirement for Qld Generation Event | Outage
F_Q+KC_R60 | 1.4167 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage
F_Q+KC_R6 | 1.4167 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage
F_Q+ML_L60_0400 | 1.4167 | 0 | Lower 60 sec Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+ML_L6_0400 | 1.4167 | 0 | Lower 6 sec Service Requirement for Qld Load Event, ML = 390 | Outage
F_Q+ML_L5_0400 | 1.4167 | 0 | Lower 5 min Service Requirement for Qld Load Event, ML = 390 | Outage
F_T+GTTE_TL_L60 | 1.3333 | 0 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_Q+TNT_R5 | 1.3333 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Tarong North) | Outage
F_Q+LREG_0110 | 1.3333 | 0 | Qld Lower Regulation Requirement greater than 110 MW | Outage
F_Q+MM1_R5 | 1.3333 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage
F_T+GTTE_TL_L6 | 1.3333 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_Q+MG_R6 | 1.25 | 0 | Raise 6 sec Service Requirement for Qld Generation Event | Outage
F_T+FARE_N-2_TG_R60 | 1.25 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_Q+RREG_0110 | 1.25 | 0 | Qld Raise Regulation Requirement greater than 110 MW | Outage
F_T++GTTE_TL_L60 | 1.25 | 0 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_T++FASH1_2C_TG_R6 | 1.0833 | 0 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage
F_Q+TNT_R6 | 1.0833 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Tarong North) | Outage
F_NVS++MG_R6 | 1.0833 | 0 | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_STHN+MG_R60 | 1.0833 | 0 | Raise 60 sec Service Requirement for a Southern Generation Event | Outage
F_Q+MM1_R60 | 1.0833 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage
F_NVS++MG_R60 | 1.0833 | 0 | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
F_Q+TNT_R60 | 1.0833 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Tarong North) | Outage
F_Q+MM1_R6 | 1.0833 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage
F_Q+MG_R60 | 1.0833 | 0 | Raise 60 sec Service Requirement for Qld Generation Event | Outage
F_T+FARE_N-2_RREG | 1 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage
F_Q+CC4_R5 | 1 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Callide C unit 4) | Outage
F_STHN+MG_R6 | 1 | 0 | Raise 6 sec Service Requirement for a Southern Generation Event | Outage
F_MAIN+WIP_N-2_ML_L6 | 1 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_STHN+MG_R5 | 1 | 0 | Raise 5 min Service Requirement for a Southern Generation Event | Outage
F_Q+CC3_R6 | 1 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage
F_Q+CC3_R5 | 0.91667 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Callide C unit 3) | Outage
F_T++BLSPS_EXP_L60_1 | 0.83333 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_MAIN++WIPN-2_MLL60 | 0.75 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 60 sec requirement, Basslink able to transfer FCAS | Outage
F_T++BLSPS_EXP_L6_1 | 0.75 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_MAIN++WIP_N-2_MLL5 | 0.75 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 5 Min requirement, Basslink able to transfer FCAS | Outage
F_V_APD01_R6 | 0.66667 | 64.4167 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage
F_V_APD01_R60 | 0.66667 | 64.4167 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage
F_STHN+APD_TL_L5 | 0.66667 | 0 | Lower 5 min requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_V_APD01_L6 | 0.66667 | 50.1667 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage
F_STHN+APD_TL_L60 | 0.66667 | 0 | Lower 60 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_V_APD01_L60 | 0.66667 | 53.1667 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage
F_Q+CC3_R60 | 0.66667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage
F_V_APD01_R5 | 0.66667 | 64.4167 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage
F_V_APD01_L5 | 0.58333 | 60.0833 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage
F_STHN+APD_TL_L6 | 0.58333 | 0 | Lower 6 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage
F_T++CSGO_TG_R5 | 0.58333 | 0.16667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
F_T+NIL_BB_TG_R60 | 0.5 | 4.5833 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_S++HYSE_L5 | 0.5 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage
F_S+PPT_R5 | 0.41667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_T+FASH_N-2_TG_R6_2 | 0.41667 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage
F_S+PPT_R6_1 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage
F_T++FARE_N-2_TG_R6 | 0.41667 | 3.0833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_S++OSB_R6_1 | 0.41667 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA, Segment 1 | Outage
F_Q+CC4_R6 | 0.41667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 4) | Outage
F_STHN+RREG_0130 | 0.33333 | 0 | Southern Raise Regulation Requirement greater than 130 MW | Outage
F_T+NIL_BB_TG_R6 | 0.33333 | 0.91667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_T+RREG_0100 | 0.33333 | 0 | Tasmania Raise Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS | Other
F_NVS+MG_R6 | 0.33333 | 0 | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink unable to transfer FCAS | Outage
F_STHN+ML_L60_0300 | 0.33333 | 0 | Lower 60 sec requirement for a Southern Load Event, ML = 300 | Outage
F_NVS+MG_R60 | 0.33333 | 0 | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink unable to transfer FCAS | Outage
F_STHN+ML_L6_0300 | 0.25 | 0 | Lower 6 sec requirement for a Southern Load Event, ML = 300 | Outage
F_NVS+MG_R5 | 0.25 | 0 | Raise 5 min Service Requirement for NSW, Vic and SA Generation Event, Basslink unable to transfer FCAS | Outage
F_V_EILDON2_R6 | 0.25 | 0 | Out= NIL, Eildon 2 R6 Requirement <= 0MW | Outage
F_V_EILDON2_R60 | 0.25 | 0 | Out= NIL, Eildon 2 R60 Requirement <= 0MW | Outage
F_V_EILDON2_R5 | 0.25 | 0 | Out= NIL, Eildon 2 R5 Requirement <= 0MW | Outage
F_T+LREG_0100 | 0.25 | 0 | Tasmania Lower Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS | Other
F_S+TL_L6_OD | 0.25 | 0 | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_Q++ARTW_R6 | 0.25 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
F_S++ML_L6_1 | 0.25 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage
F_S++ML_L5 | 0.25 | 0 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
F_S+TL_L5_OD | 0.25 | 0 | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_S+TL_L60_OD | 0.25 | 0 | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage
F_T_FATI_RREG | 0.16667 | 0 | Out=Farrell-Tribute 220KV line. RREG <= 0MW | Outage
F_T_FATI_R5 | 0.16667 | 0 | Out=Farrell-Tribute 220KV line. R5 <= 0MW | Outage
F_T+GTTE_TL_L5 | 0.16667 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage
F_NVS+RREG_0130 | 0.16667 | 0 | NSW, Vic and SA Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS | Outage
F_S++OSB_R5 | 0.16667 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage
F_QNV+RREG_0130 | 0.16667 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS | Outage
F_S++ML_L60 | 0.16667 | 0 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
F_T+NIL_BB_TG_R5 | 0.16667 | 2.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL
F_MAIN+ML_L60_APD | 0.16667 | 0.33333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_QNV+MLTR_L60 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+WIP_N-2_MLL60 | 0.083333 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_T++FARE_N-2_TG_R60 | 0.083333 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN+ML_L5_APD | 0.083333 | 0.33333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_STHN+LREG_0120 | 0.083333 | 0 | Southern Lower Regulation Requirement greater than 120 MW | Outage
F_QNV+MG_R5 | 0.083333 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage
F_Q_TARONG#1_LREG | 0.083333 | 0 | Out= NIL, Tarong 1 LREG Requirement <= 0MW | Outage
F_QNV++HYTR_L5 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++FARE_N-2_TG_R5 | 0.083333 | 0.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
F_MAIN+WIP_N-2_ML_L5 | 0.083333 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 5 Min requirement, Basslink unable to transfer FCAS | Outage
F_T++GTTE_TL_L5 | 0.083333 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
F_Q++BCDM_R6 | 0.083333 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage
F_ESTN+ML_L6_0400 | 0.083333 | 0 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage
F_ESTN+MG_R5 | 0.083333 | 0 | Raise 5 min Service Requirement for Eastern Generation Event | Outage
F_S++OSB_R60 | 0.083333 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage
F_T+FASH_N-2_TG_R6_4 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment4 | Outage
F_T+FASH_N-2_TG_R6_3 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment3 | Outage
F_S+PPT_R60 | 0.083333 | 0 | Raise 60 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage
F_ESTN+ML_L60_0400 | 0.083333 | 0 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage

## Binding Impact
Constraint Equation ID | 2018 Marginal Values | 2017 Marginal Values | 2018 Hours | 2017 Hours | Description | Type | Region
NSA_S_PORxxx | 29862638.4858 | 633602.6751 | 173.4167 | 22.75 | Port Lincoln >= 15 MW for Network Support Agreement | Outage | SA
S_WIND_1200_AUTO & S_NIL_STRENGTH_1 | 13582752.5298 | 4746491.0083 | 1094.4167 | 397.3333 | Upper limit (1460 to 1295 MW) for South Australian non-synchronous generation for minimum synchronous generators online for system strength requirements. Automatically swamps out when required HIGH combination is online. | NIL | SA
N_SILVERWF_MAX | 1562642.1245 | 0 | 119.0833 | 0 | Limit MW output of Silverton wind farm to not exceed 45 MW with Broken Hill solar generating | Outage | NSW
T>T_NIL_110_1 | 1518119.5609 | 2282347.5986 | 118.0833 | 178.25 | Out = NIL, avoid pre-contingent O/L of the Derby to Scottsdale Tee 110 kV line, feedback | NIL | Tas
N^^V_NIL_1 | 1000022.8137 | 736587.6863 | 1166.0833 | 1808.4167 | Out = Nil, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | NIL | NSW
S_SNOW_N+S_190 | 777639.0326 | 0 | 121.5833 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 190 MW | Outage | SA
F_I+NIL_MG_R5 | 757552.4563 | 661829.0286 | 5581.1667 | 7927.6667 | Out = Nil, Raise 5 min requirement for a NEM Generation Event | NIL | FCAS
S>SE6161_SETX2_SGBL | 601071.676 | 0 | 66.8333 | 0 | Out= South East 132kV CB6161, avoid O/L Snuggery-Blanche 132kV line on trip of South East 132/275 TX2 ( this offloads Mayura-South East T 132kV line), Feedback | Outage | SA
N_STWF1_ZERO | 589083.1609 | 0 | 45.3333 | 0 | Silverton wind farm upper limit of 0 MW | Outage | NSW
F_MAIN+NIL_DYN_RREG | 541024.5211 | 590159.5218 | 1076.3333 | 869.5833 | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s | NIL | FCAS
F_MAIN+NIL_MG_R5 | 493839.7628 | 82206.9969 | 2279.4167 | 483.4167 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
F_T+NIL_WF_TG_R6 | 478720.9504 | 761013.3893 | 1074 | 1211.1667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
V::S_SETB_TBSE_2 | 474614.658 | 11968.8425 | 172.25 | 45.3333 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
F_T_AUFLS2_R6 | 439302.184 | 0 | 1382.1667 | 0 | TAS AUFLS2 control scheme. Limit R6 enablement based on loaded armed for shedding by scheme. | NIL | FCAS
V>>V_NIL_1A | 433616.5918 | 164.8365 | 9.6667 | 0.33333 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
F_I+LREG_0120 | 430085.6586 | 1523661.4353 | 3920.1667 | 6959.75 | NEM Lower Regulation Requirement greater than 120 MW | NIL | FCAS
S_LB_1+2+3_190 | 404142.2959 | 0 | 59.9167 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms<= 190 MW | Outage | SA
F_MAIN+NIL_MG_R6 | 398917.722 | 149440.4665 | 2281 | 483.4167 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
F_S+LREG_0035 | 386344.5599 | 6679748.2302 | 17.5833 | 158.5833 | SA Lower Regulation FCAS Requirement greater than 35 MW | Outage | FCAS
F_S+RREG_0035 | 382426.3315 | 6751450.4514 | 17.5833 | 155.5833 | SA Raise Regulation FCAS Requirement greater than 35 MW | Outage | FCAS
F_T+NIL_MG_R6 | 364786.5503 | 436152.927 | 1230.0833 | 1330.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_T+RREG_0050 | 337884.9104 | 263753.9267 | 1752.8333 | 543.6667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
V_OWF_TGTSNRBHTN_30 | 335465.8393 | 228038.5399 | 26.0833 | 17.8333 | Out= Nil, TGTS-HTN-NRB-TGTS sub-transmission loop OPEN, Limit Oaklands Hill Windfarm upper limit to 30 MW, DS only. Swamp out if the loop closed. | NIL | Vic
F_MAIN++NIL_MG_R6 | 331057.7381 | 156764.5211 | 2339.1667 | 1140.5 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS
NSA_Q_BARCALDN | 326982.8027 | 61385.7792 | 29.4167 | 4.9167 | Network Support Agreement for Barcaldine GT to meet local islanded demand for the planned outage of 7153 T71 Clermont to H15 Lilyvale or 7154 T72 Barcaldine to T71 Clermont 132kV line | Outage | Qld
F_T+NIL_MG_RECL_R6 | 324887.7909 | 392954.5944 | 1350.1667 | 1091.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN++NIL_MG_R5 | 309872.5953 | 126189.2683 | 1615.9167 | 1141.3333 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS
F_T_NIL_MINP_R6 | 293912.5375 | 0 | 1277.8333 | 0 | Out= NIL, ensure minimum quantity of TAS R6 FCAS requirement provided through proportional response, considering Basslink headroom | NIL | FCAS
F_MAIN+NIL_MG_R60 | 277623.1052 | 84709.9548 | 2282.9167 | 483.3333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
F_MAIN++NIL_MG_R60 | 276004.9275 | 123178.0361 | 2460.5833 | 1563 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL | FCAS
S_HPRG1_E | 275838.0574 | 20077.2032 | 31.0833 | 2.5 | Out= Nil, Hornsdale Battery generation energy target <= 30 MW | NIL | SA
V>SMLARHO1 | 272269.9705 | 0 | 49.5833 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
F_T+LREG_0050 | 271971.3372 | 149937.0085 | 2351.9167 | 483.25 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
V_OAKHILL_TFB_42 | 268832.4489 | 0 | 20.6667 | 0 | Out = Nil, Oaklands Hill Windfarm upper limit of 42.7 MW due to Oaklands Hill windfarm TFB mode operation, DS only. Swamp out if TFB mode is OFF | NIL | Vic
S^NIL_PL_MAX | 264096.2377 | 6367.4105 | 9.5833 | 0.5 | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
F_I+NIL_MG_R6 | 256098.6958 | 1017635.5787 | 4517 | 7509.4167 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event | NIL | FCAS
F_I+NIL_RREG | 248430.3825 | 1481379.4495 | 2238.75 | 7280.9167 | NEM Raise Regulation Requirement | NIL | FCAS
V::S_SETB_MAXG_2 | 246813.8872 | 0 | 130.25 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with both Black Range series capacitors O/S). | Outage | SA
S::V_TBSE_TBSE_2 | 244517.3789 | 0 | 99.3333 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage | SA
F_Q+ML_L60_0400 | 241293.4388 | 0 | 1.4167 | 0 | Lower 60 sec Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS
VSML_ZERO | 234097.2069 | 2004.5359 | 546.5833 | 20.6667 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
Q_CN0540 | 230712.818 | 0 | 1.3333 | 0 | Qld Central to North upper transfer limit of 540 MW (discretionary) | Outage | Qld
NSA_V_BDL0xxx | 224446.4483 | 267715.9865 | 2.4167 | 4 | Bairnsdale Unit 1 >= 40 MW for Network Support Agreement | Outage | Vic
F_MAIN+LREG_0120 | 220320.4028 | 167915.1982 | 1727.3333 | 478.0833 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink unable to transfer FCAS | NIL | FCAS
S>X_RBPA+CB_01 | 217845.0338 | 0 | 12.8333 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV TX1 on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
V_BANNERTON_ZERO | 217721.5637 | 0 | 16.25 | 0 | Bannerton Solar Farm upper limit of 0 MW | Outage | Vic
N_BLOWERNG_ZERO | 213000 | 5483.1462 | 1.25 | 0.41667 | Blowering generation upper limit of 0 MW | Outage | NSW
V_GANNAWR_ZERO | 213000 | 0 | 1.25 | 0 | Gannawarra solar farm upper limit of 0 MW | Outage | Vic
S_WATERLWF_RB | 207403.9713 | 260514.302 | 16.6667 | 27.5 | Out= Nil, Limit Waterloo WF output to its runback MW capability, DS only | NIL | SA
S_PW-CB6156_LG1 | 201979.5804 | 0 | 15.4167 | 0 | Out=Penola West 132kV CB 6156 O/S (Note: with Penola West 132kV CB 6158 CLOSED), Oscillatory stability limit Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
V>>V_NIL_8 | 200212.9906 | 209.9594 | 12 | 0.83333 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL | Vic
S_SNOWNTH1_ZERO | 196622.701 | 0 | 14.3333 | 0 | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW | Outage | SA
S>V_NIL_NIL_RBNW | 195921.3558 | 112551.1516 | 315 | 283.25 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL | SA
T>>T_PMSH_EXP_3C | 183243.6903 | 0 | 9.4167 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
S_SNOWSTH1_ZERO | 181024.1325 | 0 | 14.25 | 0 | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW | Outage | SA
F_I+NIL_MG_R60 | 179632.406 | 408139.9473 | 4396.3333 | 7164.4167 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event | NIL | FCAS
F_I+LREG_0150 | 175601.265 | 0 | 1319.5833 | 0 | NEM Lower Regulation Requirement greater than 150 MW | NIL | FCAS
F_Q+ML_L5_0400 | 173400 | 0 | 1.0833 | 0 | Lower 5 min Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS
S_HALWF2_0 | 161194.4544 | 246487.125 | 12.75 | 18.3333 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
F_Q+ML_L6_0400 | 157334.1113 | 0 | 1.4167 | 0 | Lower 6 sec Service Requirement for Qld Load Event, ML = 390 | Outage | FCAS
V^SML_NSWRB_2 | 151775.6622 | 441280.0408 | 60.1667 | 52 | Out = NSW Murraylink runback scheme, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | NIL | Vic
S>>PATW_BWPA_TPRS | 145061.273 | 0 | 35.3333 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
Q_RS_200 | 141455.0828 | 0 | 0.83333 | 0 | Qld, Ross cutset upper limit of 200MW (discretionary) | Outage | Qld
Q>NIL_BI_xxx | 136204.5911 | 589995.8774 | 98.8333 | 139.9167 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104 and 7105 (T022 Callide A to T152 Gladstone South) 132 kV lines open with 132 kV intact between T022 Callide A and H015 Lilyvale. | NIL | Qld
F_MAIN+TASCAP_LREG | 133421.2436 | 33240.2368 | 2083.9167 | 677.75 | Mainland Lower Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
N_MBTE1_B | 120502.648 | 90623.913 | 126.5833 | 206 | Out= one Directlink cable, Qld to NSW limit | Outage | NSW
F_MAIN+NIL_DYN_LREG | 119630.1339 | 406317.0764 | 534.75 | 862.25 | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s | NIL | FCAS
V::N_NIL_xxx | 115464.4404 | 181973.4356 | 271.25 | 608.9167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL | Vic
F_MAIN+NIL_RREG | 113753.422 | 160378.222 | 784.6667 | 425 | Mainland Raise Regulation Requirement, Basslink unable transfer FCAS | NIL | FCAS
F_T++RREG_0050 | 111814.9603 | 201134.5522 | 510.0833 | 1109.4167 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
N_BODWF1_ZERO | 111575.1989 | 0 | 8.5833 | 0 | Bodangora wind farm upper limit of 0 MW | Outage | NSW
F_Q+MG_R6 | 111279.8561 | 0 | 0.66667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event | Outage | FCAS
T>T_HA_TX | 108133.1503 | 0 | 5.75 | 0 | Out = Hadspen 220/110 kV txfmr, avoid O/L Palmerston 220/110 kV txfmr (flow from 220 kV to 110 kV) on trip of remaining Hadspen 220/110 kV txfmr, feedback | Outage | Tas
S>NIL_SGBN_SGSE-T2 | 105339.3463 | 234062.2873 | 11.75 | 53.9167 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on trip of Snuggery-Blanche 132kV line (for Line component SECS assumed O/S), Feedback | NIL | SA
F_Q+RREG_0110 | 103667.6527 | 0 | 0.83333 | 0 | Qld Raise Regulation Requirement greater than 110 MW | Outage | FCAS
T_TAMARCCGT_GCS | 98388.4384 | 168519.0338 | 61.5 | 65.9167 | Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) constraint to manage effective size of generation contingency for loss of Tamar CCGT. Limit output of Tamar CCGT based on load available and/or armed for shedding by Tamar GCS. | NIL | Tas
NRM_SA1_VIC1 | 94463.3403 | 17049.5687 | 7.6667 | 1.25 | Negative Residue Management constraint for SA to VIC flow | NIL | Negative Residue
N_COLEASF1_ZERO | 94022.1295 | 0 | 7.4167 | 0 | Coleambally solar farm upper limit of 0 MW | Outage | NSW
F_Q+LREG_0110 | 92935.9294 | 0 | 0.66667 | 0 | Qld Lower Regulation Requirement greater than 110 MW | Outage | FCAS
T>T_NIL_BL_110_18_1 | 92735.7046 | 60742.1132 | 26.75 | 33.1667 | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
V>>V_NIL_1B | 92094.2854 | 129.5768 | 1.9167 | 1.0833 | Out = Nil, avoid O/L Murray to Dederang No.2 330kV line (flow MSS to DDTS) for loss of the parallel No.1 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL | Vic
F_T+NIL_MG_RECL_R60 | 88384.7133 | 49954.7652 | 1371.5833 | 1115.5833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
S_HDWF1_0 | 88216.5518 | 38668.9569 | 6.4167 | 1.8333 | Discretionary upper limit for Hornsdale #1 Wind Farm generation of 0 MW | Outage | SA
F_Q+MM1_R5 | 86607.3974 | 0 | 0.83333 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage | FCAS
S>NIL_NIL_SETX12 | 83169.2698 | 14260.0691 | 5.5 | 3.3333 | Out=NIL, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
F_Q+MG_R60 | 81194.7679 | 0 | 0.66667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event | Outage | FCAS
S_DVRB2_270 | 78852.9709 | 360127.0206 | 29.25 | 30.75 | Out = DV-LK 275kV line Or CN-RB 275kV line O/S, discretionary upper limit for Hornsdale WF1+ Hornsdale WF2+Hornsdale WF3+Hallet Hill GT + Hornsdale battery (i.e. generation + load component) <= 270 MW | Outage | SA
F_T+NIL_WF_TG_R5 | 78031.946 | 25315.2583 | 948.5833 | 865.75 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
NRM_VIC1_SA1 | 77671.77 | 6030.8075 | 0.5 | 4.75 | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
F_T+NIL_MG_RECL_R5 | 76621.8266 | 25853.159 | 1249.75 | 718.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
S>NIL_WERB_WEWT | 75482.364 | 389842.3203 | 7 | 105.1667 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Waterloo East-Morgan Whyalla 4 - Robertstown 132kV line, Feedback | NIL | SA
F_T+NIL_WF_TG_R60 | 74114.6853 | 68447.908 | 1121 | 1140 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
T>T_LIPM_110_2B | 73059.7307 | 1202.1219 | 126 | 2.1667 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to North) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
Q_CN1200 | 70211.2108 | 0 | 0.41667 | 0 | Qld Central to North upper transfer limit of 1200 MW (discretionary) | Outage | Qld
Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 70186.0854 | 151610.5032 | 144.5833 | 516.6667 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL | Qld
F_T+NIL_MG_R60 | 69053.3169 | 53531.605 | 1329.75 | 1223.5833 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
S>BRDV_BWPA_RHBR | 68427.0145 | 15877.6417 | 5.5833 | 1.5833 | Out= Brinkworth - Davenport 275kV line, avoid O/L Redhill tee - Brinkworth 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_Q++BCDM_L5 | 63546.5184 | 0 | 75.0833 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage | FCAS
V_OWF_NRB_0 | 62034.4505 | 87092.7289 | 4.8333 | 6.5833 | Out= Nareeb (NRB) to Oaklands Hill WF line, Limit Oaklands Hill Windfarm upper limit to 0 MW, DS only. Swamp out if the line in service. | NIL | Vic
N^N-LS_SVC | 60323.1631 | 0 | 481.1667 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage | NSW
F_T+NIL_MG_R5 | 60187.8736 | 19725.5517 | 941.4167 | 757.4167 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
F_Q+KC_R60 | 59567.9575 | 0 | 0.75 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage | FCAS
F_MAIN+NIL_MG_R6_PP | 58493.5049 | 0 | 74.9167 | 0 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink unable transfer FCAS | NIL | FCAS
V_MORTLAKE12_ZERO | 57887.8628 | 130181.36 | 0.41667 | 1.0833 | Mortlake unit 1 & 2 upper limit of 0 MW | Outage | Vic
F_Q+MM1_R6 | 57677.3824 | 0 | 0.58333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage | FCAS
V^^N_NIL_1 | 57328.8963 | 0 | 67.5 | 0 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL | Vic
F_T++NIL_MG_RECL_R6 | 57267.99 | 109899.9377 | 162.4167 | 263.3333 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_T++LREG_0050 | 55733.3892 | 9322.0483 | 708.75 | 93.3333 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
S_SECB_LG-1 | 54875.0923 | 2999.9983 | 4.0833 | 0.25 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line,Ladbroke Grove 1 can generate up to 40MW on a single unit OR 20MW max per unit (40MW total output) | Outage | SA
S:V_500_HY_TEST_DYN | 54435.4071 | 63489.0564 | 78.4167 | 189.5833 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
T_MRWF_QLIM_xx | 53843.5906 | 1546815.5053 | 4.0833 | 118.8333 | Out = NIL, limit Musselroe Wind Farm to 150 MW if less than 96% of DVAr capacity online. Swamped if 96% or more of DVAr capacity online. | NIL | Tas
S_SNOW_N+S_210 | 53165.3727 | 0 | 8.1667 | 0 | Discretionary upper limit for Snowtown North and South Windfarms of 210 MW | Outage | SA
V^^S_SETB_TBSE_2 | 50974.4751 | 449.7565 | 32.75 | 2.0833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage | SA
V:S_600_HY_TEST_DYN | 48945.8157 | 582676.9054 | 89.8333 | 289.25 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
S-BUPV1_0 | 47853.7469 | 0 | 3.6667 | 0 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW | Outage | SA
F_Q+MG_R5 | 45680.3177 | 0 | 0.33333 | 0 | Raise 5 min Service Requirement for Qld Generation Event | Outage | FCAS
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 43440.3774 | 143896.5996 | 145.1667 | 311.5 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL | Vic
F_Q+KC_R5 | 43346.3184 | 0 | 0.5 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Kogan Creek) | Outage | FCAS
N^^N_NIL_1 | 42750.7841 | 110.7605 | 1.5 | 0.083333 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL | NSW
T_FATI | 42600 | 198.4677 | 0.25 | 0.16667 | Out=Farrell-Tribute 220KV line. Energy <= 0MW | Outage | Tas
F_Q++BCDM_L6 | 42560.2093 | 0 | 82.9167 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage | FCAS
N>>N-NIL__3_OPENED | 41910.2427 | 801598.9429 | 18.3333 | 23.8333 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
V::N_SETB_xxx | 41779.8448 | 0 | 84.75 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
VS_250 | 40128.78 | 229.0772 | 5.4167 | 3.5833 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage | Vic
SVML_ROC_80 | 39228.1946 | 31448.1887 | 47.5833 | 21.3333 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL | SA
SVML_ZERO | 38914.9767 | 25260.0273 | 242.75 | 83.25 | SA to Vic on ML upper transfer limit of 0 MW | Outage | SA
N^^Q_LS_VC_B1 | 38843.9281 | 462.507 | 63.25 | 0.83333 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
T^V_NIL_11 | 38832.3731 | 11817.9508 | 70 | 21.5 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL | Tas
V_T_NIL_FCSPS | 38525.5556 | 87762.9926 | 107.25 | 194.5833 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL | Vic
F_MAIN++LREG_0120 | 38428.1904 | 333243.8217 | 328 | 1297.0833 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL | FCAS
N::V_BYGR_2 | 37990.4914 | 0 | 2.0833 | 0 | Out = Bannaby to Gullen Range(61), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage | NSW
T>T_HAPM_2A | 36545.4273 | 0 | 42.5 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
S>MKRB_BWMP_HUWT | 36231.2249 | 0 | 2.1667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
S_PW-CB6156_LG3 | 35109.6672 | 0 | 3.9167 | 0 | Out=Penola West 132kV CB 6156 O/S (Note: with with Penola West 132kV CB 6158 CLOSED), Oscillatory stability limit max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
S_LB_1+2+3_210 | 34936.9563 | 0 | 2.8333 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=210 MW | Outage | SA
T>T_FASH_1_2_C1 | 33803.4084 | 0 | 15.8333 | 0 | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, West Coast 220/110 kV parallel closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
F_MAIN+NIL_MG_R5_PP | 32748.9031 | 0 | 76.25 | 0 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink unable transfer FCAS | NIL | FCAS
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 32298.2571 | 10067.3352 | 20.1667 | 39.25 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL | Qld
VSML_ROC_80 | 31946.5082 | 137511.248 | 43.25 | 20.0833 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL | Vic
F_MAIN+NIL_MG_R60_PP | 31839.8543 | 0 | 73 | 0 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink unable transfer FCAS | NIL | FCAS
T^V_NIL_9 | 31730.7858 | 1151.6346 | 58.5833 | 1.1667 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL | Tas
F_S++HYSE_L60 | 31140.3029 | 333.1473 | 7.3333 | 45.8333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage | FCAS
V_T_NIL_BL1 | 31103.1857 | 60567.5107 | 27.5 | 152.0833 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL | Vic
F_S+TL_L60_OD | 30997.69 | 0 | 0.25 | 0 | Lower 60 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
F_Q+KC_R6 | 29848.8701 | 0 | 0.33333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Kogan Creek) | Outage | FCAS
F_Q++BCDM_L60 | 29724.1997 | 0 | 82.8333 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 60 sec Requirement | Outage | FCAS
S>NIL_NIL_NWMH2 | 29101.0599 | 81847.4014 | 10.6667 | 36.9167 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL | SA
N>N-NIL_DC | 29041.3331 | 0 | 87.25 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL | NSW
S>BLMK_BWPA_HUWT | 28809.8519 | 118867.1564 | 2.25 | 8.3333 | Out= Belalie-Mokota 275kV line (This offloads Willalo substation and Willagoleche WF) OR Belalie-Willalo 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N_X_MBTE_3A & N_X_MBTE_3B | 27924.6924 | 36347.5025 | 251.8333 | 223.25 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage | NSW
VSML_220 | 27129.0853 | 29626.0483 | 28.0833 | 22.3333 | Vic to SA on ML upper transfer limit of 220 MW | NIL | Vic
V_MTGBRAND_11WT | 26740.0379 | 0 | 2.0833 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 11 | Outage | Vic
F_Q+CC4_R5 | 26065.5953 | 0 | 0.91667 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Callide C unit 4) | Outage | FCAS
VTBL_ROC | 25578.4215 | 36023.1273 | 6.1667 | 12.5833 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL | Vic
S>NIL_BWMP_HUWT | 25345.6255 | 13849.508 | 0.91667 | 1.1667 | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West- Munno Para 275kV line, Feedback | NIL | SA
F_T++NIL_MG_R6 | 24957.7937 | 52917.2372 | 43.25 | 56.5 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V_BALDHILL_ZERO | 24212.3768 | 0 | 8.9167 | 0 | Bald Hill Windfarm upper limit of 0 MW | Outage | Vic
V>>N-NIL_HA | 24066.2253 | 8228.0732 | 29.9167 | 12.9167 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL | Vic
S>NIL_NIL_SGBN | 24012.6753 | 8046.2079 | 1.9167 | 1.0833 | Out= NIL, avoid O/L Snuggery-Blanche 132kV line on NIL trip, Feedback | NIL | SA
F_Q++MUTW_L6 | 23686.0295 | 5758.9918 | 140.5 | 37.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage | FCAS
F_Q++MUTW_L5 | 22965.8272 | 14914.1809 | 130.25 | 28.0833 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage | FCAS
F_Q+MM1_R60 | 22953.8224 | 0 | 0.33333 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Millmerran unit 1) | Outage | FCAS
S_HDWF3_0 | 22766.4193 | 5298.2794 | 6.4167 | 1.25 | Discretionary upper limit for Hornsdale #3 Wind Farm generation of 0 MW | Outage | SA
S-HDWF2_0 | 22766.403 | 9011.0063 | 6.4167 | 2.1667 | Discretionary upper limit for Hornsdale #2 Wind Farm generation of 0 MW | Outage | SA
S>>X_MKRB+WERB_11 | 22709.983 | 0 | 1.8333 | 0 | Out=Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (Note: Line Only O/S) avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line | Outage | SA
S>>BG6246_BGPR_HUWT | 22662.4294 | 0 | 3.8333 | 0 | Out= Bungama 132kV CB6246, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama-Port Pirie 132kV line (this offloads Snowtown-Bungama 132kV line), Feedback | Outage | SA
T^V_HA_GT_220_1 | 22500.9072 | 0 | 19.5833 | 0 | Out= one George Town to Hadspen 220kV line, limit post-contingency loading on Palmerston to Sheffield 220kV line (flow to north) to avoid voltage collapse on trip of the remaining Hadspen to George Town 220kV line. | Outage | Tas
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 22014.5713 | 556067.8533 | 79.0833 | 147.8333 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL | NSW
N^^V_NIL_MAXG_PP_N-2 | 21970.5476 | 0 | 30.1667 | 0 | Out = Nil, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit + Pelican Point when they declared as single credible contingency | NIL | NSW
F_Q+CC3_R5 | 21804.1918 | 0 | 0.66667 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Callide C unit 3) | Outage | FCAS
Q^CN_FDR-180 | 21436.7221 | 0 | 0.16667 | 0 | Nominated Offset = -180MW, Central Qld to North Qld Voltage stability limit, Feeder trip equation, 2009/10 implementation. | Outage | Qld
F_S+TL_L5_OD | 21205.9612 | 0 | 0.16667 | 0 | Lower 5 min Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
F_I+NIL_MG_R5_PPN2 | 21078.1872 | 0 | 89.8333 | 0 | Out = Nil, Raise 5 min requirement for a NEM Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible) | NIL | FCAS
S>>X_MKRB+WERB_4 | 20531.0423 | 0 | 2.0833 | 0 | Out= Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (Note: Line Only O/S), avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, | Outage | SA
T>>T_PMSH_EXP_3B | 20512.6347 | 0 | 2.9167 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
F_MAIN++NIL_MG_R6_PP | 20487.792 | 0 | 82.4167 | 0 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL | FCAS
F_T++NIL_WF_TG_R6 | 20152.9149 | 41924.75 | 80.5833 | 124 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
T>T_PMSH_IMP_4C | 19906.8315 | 2849.9901 | 27.0833 | 4 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T^V_NIL_8 | 19805.1663 | 1035.9341 | 46.1667 | 2.25 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL | Tas
S>>BRTW_WTTP_WEMWP4 | 19440.4304 | 0 | 0.75 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Waterloo-Templers 132kV line, Feedback | Outage | SA
NRM_NSW1_VIC1 | 18794.8279 | 0 | 2.5 | 0 | Negative Residue Management constraint for NSW to VIC flow | NIL | Negative Residue
N_X_MBTE2_A & N_X_MBTE2_B | 18624.8162 | 206087.1432 | 302.9167 | 1202.5833 | Out= two Directlink cables, NSW to Qld limit | Outage | NSW
S>>NIL_CNRB_WEMWP4 | 18618.3038 | 0 | 0.66667 | 0 | Out= Nil, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on trip of Canowi-Robertstown 275kV line (this offloads Mt Lock-Canowie 275kV line and trips Hallet WF and GTs), Feedback | NIL | SA
S_SECB_LG3 | 16946.8952 | 159985.7851 | 1.25 | 12.6667 | Out= South East 132kV CB 6186 Or 6187, Oscillatory stability limit for the loss of Penola West-South East 132kV line, max generation of Ladbrok Grove Gen 1 and 2 to a total of 40 MW | Outage | SA
F_Q++ARDM_L60 | 16727.9867 | 22269.8846 | 8.25 | 108.1667 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_MAIN+TASCAP_RREG | 16648.2278 | 43900.8675 | 241.0833 | 469.5 | Mainland Raise Regulation Requirement, Cap Tas contribution to 50 MW | NIL | FCAS
V_MTMERCER_ZERO | 16643.4278 | 235901.5035 | 1.25 | 17.8333 | Mt Mercer Windfarm upper limit of 0 MW | Outage | Vic
T_V_NIL_FCSPS | 16609.4534 | 2479.7877 | 3.0833 | 5.25 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
T::T_HA_GT_PM_4 | 16584.7657 | 6033.9554 | 9.1667 | 2.3333 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage | Tas
F_Q++ARDM_L6 | 16534.3545 | 20974.4629 | 8.25 | 107.25 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage | FCAS
V>SML_NSWRB_10 | 16487.4915 | 11973.9187 | 2.6667 | 3.1667 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
S>>PARB_RBTU_WEWT | 16262.8896 | 36.4015 | 25.8333 | 0.75 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
F_T++NIL_MG_RECL_R5 | 16096.4222 | 5063.5627 | 71.4167 | 86.6667 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
S:VS_650_HY_TEST_DYN | 16090.1156 | 30646.6613 | 11 | 22.5 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage | SA
S>RBTX2_RBTX1_WEMWP4 | 16071.8418 | 0 | 31.5 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage | SA
F_Q+TNT_R5 | 15941.8862 | 0 | 0.5 | 0 | Raise 5 min Service Requirement for Qld Generation Event (Tarong North) | Outage | FCAS
F_NVS+MG_R6 | 15920.5775 | 0 | 0.33333 | 0 | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
S>>SETB_TBSE_TBKH2_1 | 15672.3374 | 0 | 1 | 0 | Out= one South East to Tailem Bend 275kV line, avoid O/L Tailem Bend-Keith #2 132kV Line on trip of other Tailem Bend-South East 275kV line, Feedback (Note: with both SE series caps I/S or O/S) | Outage | SA
N_BROKENH1_ZERO | 15498.6414 | 79177.3463 | 1.1667 | 6 | Broken Hill Solar Farm upper limit of 0 MW | Outage | NSW
V>>DDSH_DDGN_N-2 | 15438.5853 | 23047.5284 | 1.0833 | 1.3333 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage | Vic
F_MAIN++NIL_MG_R5_PP | 15384.0917 | 0 | 66.25 | 0 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5STt PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL | FCAS
S>>MKRB_CNRB_WEMWP4 | 15084.8235 | 0 | 11.75 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage | SA
F_NVS+MG_R60 | 14750.4867 | 0 | 0.33333 | 0 | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
F_S+PPT_R5 | 14654.18 | 0 | 0.25 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA | Outage | FCAS
F_Q++ARDM_L5 | 14605.1499 | 21202.5228 | 5.3333 | 92.1667 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage | FCAS
F_NVS+RREG_0130 | 14562.3666 | 0 | 0.16667 | 0 | NSW, Vic and SA Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS | Outage | FCAS
T_T_FASH_3_N-2 | 14501.8966 | 28000 | 6.75 | 0.16667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, constrain Reece Unit 1 to 0 MW as per TAS Networks advice | Outage | Tas
F_S+PPT_R6_1 | 14500 | 0 | 0.083333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Pelican Point GT11 or GT12 or ST is the largest generation risk in SA, Segment 1 | Outage | FCAS
T_FAMA | 14500 | 0 | 0.083333 | 0 | Out=Farrell-Mackintosh 110KV line. Energy <= 0MW | Outage | Tas
Q_RS_160 | 14442.812 | 0 | 0.083333 | 0 | Qld, Ross cutset upper limit of 160MW (discretionary) | Outage | Qld
V^^S_NIL_MAXG_xxx | 14402.5801 | 71.4015 | 14.8333 | 0.75 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
T_FARC1 | 14200 | 0 | 0.083333 | 0 | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
T^V_HAPM_220_1 | 13927.1435 | 0 | 18.5 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage | Tas
F_T++NIL_WF_TG_R5 | 13917.8086 | 1883.3246 | 74.5833 | 54.75 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
S>NIL_DVTX_DVTX | 13766.3453 | 0 | 1.0833 | 0 | Out= NIL, avoid O/L one Davenport 132/275kV TX on trip of other Davenport 132/275kV TX (NOTE: for Bungala trip/runback scheme O/S), Feedback | NIL | SA
F_MAIN++NIL_MG_R60_P | 13713.6543 | 0 | 81.5833 | 0 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST t PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL | FCAS
T>T_FASH_1_N-2 | 12997.2081 | 1802.9789 | 10.6667 | 2 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
T_T_BA_JB_RC2_250 | 12973.3448 | 450.668 | 20 | 0.66667 | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
S>>V_NIL_WTTP_WEMW4 | 12484.4893 | 0 | 1.0833 | 0 | Out= Nil, avoid O/L Waterloo East - Morgan Whyalla 4 132kV on trip of Waterloo - Templers 132 kV line, Feedback | NIL | SA
N_V_HV1075 | 12038.2185 | 0 | 0.58333 | 0 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 1075 MW | Outage | NSW
T:T_LIPM_1 | 11968.2835 | 27896.8393 | 17.4167 | 63.1667 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to South) | Outage | Tas
F_Q++ARTW_L6 | 11879.8784 | 4527.9227 | 83 | 63.8333 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage | FCAS
F_Q++ARTW_L60 | 11724.4929 | 8172.1792 | 74.5833 | 62.5 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS
T>T_PMSH_IMP_4E | 11623.0831 | 0 | 9 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
F_I+NIL_APD_TL_L5 | 11523.2165 | 6551.1842 | 6268.25 | 3624.0833 | Lower 5 min Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS
F_T+COGT_TL_L6 | 11252.9065 | 0 | 9.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS
S>NIL_HUWT_STBG | 11249.0782 | 1227468.3407 | 0.83333 | 96.8333 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=60 MW when Dalymple Battery (i.e. both Gen and Load component) is O/S] | NIL | SA
S_LB_1+2+3_230 | 10894.3714 | 0 | 0.83333 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=230 MW | Outage | SA
F_Q++ARTW_L5 | 10802.8841 | 4611.9201 | 65.9167 | 42.5833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage | FCAS
F_MAIN+LREG_0150 | 10594.1167 | 0 | 51.25 | 0 | Mainland Lower Regulation Requirement greater than 150 MW, Basslink unable to transfer FCAS | NIL | FCAS
S>NIL_NIL_MYSG-T | 10493.877 | 1251.0804 | 2 | 0.91667 | Out = NIL; Limit LB2 and LB3 generation to avoid OL Mayura - Snuggery T 132kV line. | NIL | SA
I_CTRL_ISSUE_TE | 10433.1791 | 19419.3377 | 113.25 | 310.8333 | DC Link Control Issue Constraint for Terranora | Outage | Other
Q^^NIL_TR_CLHA | 10432.8353 | 0 | 0.16667 | 0 | Out = Nil, Tarong voltage stability limit, Calvale-Halys contingency equation | NIL | Qld
T_FASH_MAXGEN_1 | 10376.924 | 10413.0235 | 12.3333 | 14.5833 | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel closed. Constraint swamped if only one machine on line | Outage | Tas
N::V_CNLT_2 | 10341.8509 | 0 | 1.9167 | 0 | Out = Lower Tumut -Canberra(07), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage | NSW
V:S_600_HY_TEST | 10327.1785 | 111858.1309 | 36.5 | 76.1667 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
S:V_500_HY_TEST | 10071.2765 | 11198.3929 | 17.1667 | 45.25 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
F_Q++MUTW_L60 | 10015.5298 | 3411.3854 | 131.5833 | 36.5 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_T+NIL_ML_L6 | 9994.3283 | 578.7891 | 2322.75 | 483.3333 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
T>T_PMSH_IMP_4D | 9981.2804 | 404.0928 | 15.1667 | 0.5 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>S_MOTB_TBCG_TBTU | 9810.0698 | 0 | 0.33333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage | SA
V::N_WBHO_xxx | 9715.2701 | 0 | 21.25 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T_T_JB_RC1+2_TI_250 | 9645.647 | 0 | 8.0833 | 0 | Discretionary 250 MW upper limit on John Butters, Reece 1+2 and Tribute | Outage | Tas
F_S+TL_L6_OD | 9386.1841 | 0 | 0.25 | 0 | Lower 6 sec Service Requirement for SA Network Event, Loss of Davenport to Olympic Dam West 275kV line offload the entire Olympic Dam load | Outage | FCAS
S_PPT400 | 9082.1372 | 0 | 8.9167 | 0 | SA Pelican Point gen <= 400MW | NIL | SA
F_Q+CC3_R60 | 8922.8493 | 0 | 0.16667 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage | FCAS
V>>N-NIL_HG | 8906.7718 | 735.6078 | 7.4167 | 0.75 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL | Vic
S>X_RBPA+CB_06 | 8889.0724 | 0 | 0.75 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Robertstown 275/132kV #1 transformer on trip of Canowie-Robertstown(this this trips Hallet WF and Generation and splits Robertstown 275kV bus), Feedback | Outage | SA
V_ARARAT_ZERO | 8703.0586 | 896.8 | 3.6667 | 0.5 | Ararat Wind Farm upper limit of 0 MW | Outage | Vic
N>>V-NIL_O | 8134.8946 | 0 | 21.75 | 0 | Out = Nil, avoid overloading Upper Tumut to Murray (65) using 15 mins rating line on trip of Lower Tumut to Wagga (051) + 970,990,99M (out of Yass) line, Feedback | NIL | NSW
T_T_FASH_1_N-2 | 8001.4103 | 9343.8766 | 6.6667 | 7.5 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh <= 110% of West Coast load | Outage | Tas
T>T_NIL_BL_IMP_7CC | 7914.9913 | 5350.5583 | 50.25 | 14.8333 | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
T::T_NIL_4 | 7836.5439 | 8269.3914 | 14.1667 | 15.25 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
N^^V_CNCW_1 | 7799.6653 | 0 | 11.5833 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V::S_BLKRG_MAXG_2 | 7757.0674 | 0 | 19.6667 | 0 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
F_MAIN++NIL_RREG | 7655.0188 | 13297.2568 | 57.25 | 88.1667 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL | FCAS
F_MAIN+APD_TL_L5 | 7609.876 | 1550.557 | 1942.4167 | 219.4167 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_MG_R6_PPN2 | 7540.2591 | 0 | 59.5 | 0 | Out = Nil, Raise 6 sec requirement for a NEM Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible) | NIL | FCAS
F_S++HYSE_L6_1 | 7500.2296 | 42768.6004 | 8.0833 | 62.3333 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage | FCAS
Q>NIL_BI_CAGS_CALV_O | 7318.1464 | 0 | 33.6667 | 0 | Out= Nil, H8 Boyne Island feeder bushing (FB) limit on Calliope River to Boyne Island 132 kV lines, 7104/7105 (T022 Callide A to T152 Gladstone South) 132 kV lines closed with 132 kV split between T022 Callide A and H015 Lilyvale. | NIL | Qld
F_T+FASH_N-2_RREG | 7273.5676 | 1398.238 | 25.9167 | 10.25 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | FCAS
T>T_NIL_BL_5C | 7262.5688 | 2198.9509 | 15.0833 | 1.8333 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
T_T_FASH_2_N-2 | 6987.4464 | 13898.5657 | 3 | 4.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, West Coast 220/110 kV parallel open, limit Mackintosh >= 90% of West Coast load | Outage | Tas
F_T++NIL_MG_RECL_R60 | 6985.5697 | 7751.1746 | 170.9167 | 269.9167 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_Q++LDMU_L6 | 6952.9474 | 975.8259 | 24.75 | 5.1667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage | FCAS
T>T_PMSH_IMP_4F | 6850.41 | 0 | 8.3333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>V_ROTS_TX_2A_R | 6847.7244 | 1518.4795 | 24.3333 | 2.25 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage | Vic
T>T_NIL_BL_3A | 6637.6712 | 0 | 0.083333 | 0 | Out = Nil, avoid pre-contingent O/L of the Palmerston to Hadspen No. 1 220kV line (flow to North), feedback | NIL | Tas
T>T_X_BWLF_PMWA110_4 | 6282.9803 | 0 | 14.5833 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana AND Palmerston to Waddamana 110kV lines, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Tungatinah to Meadowbank Tee 2 to New Norfolk 110kV lines, Feedback | Outage | Tas
S>>PATW_NIL_WEMWP4 | 6119.4155 | 0 | 1.1667 | 0 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
T>T_LIPM_110_2A | 6101.2296 | 43399.3996 | 2.5833 | 89.8333 | Out= either Liapootah - Waddamana (tee) - Palmerston 220 kV line, avoid O/L Palmerston to Waddamana 110 line (flow to South) on trip of the remaining Liapootah to Waddamana (tee) to Palmerston 220 kV line, feedback | Outage | Tas
V::S_NIL_MAXG_xxx | 5960.3952 | 670.3092 | 32.9167 | 3.75 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL | SA
F_T++NIL_WF_TG_R60 | 5947.2597 | 5050.4615 | 118.4167 | 144.5 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
T^^V_GTSH_1 | 5889.7639 | 13.5535 | 9.5833 | 0.083333 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage | Tas
F_MAIN++LREG_0150 | 5661.1159 | 0 | 63.0833 | 0 | Mainland Lower Regulation Requirement greater than 150 MW, Basslink able transfer FCAS | NIL | FCAS
N_NIL_TE_B | 5550.4471 | 5284.3925 | 12.5 | 23.4167 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL | NSW
F_Q++LDMU_L60 | 5443.0401 | 2964.2402 | 23.4167 | 5.25 | Out = Liddell to Muswellbrook (83) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_T+NIL_ML_L60 | 5312.8175 | 856.78 | 2216.6667 | 481.9167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
S:VS_650_HY_TEST | 5139.7441 | 2787.092 | 3.3333 | 4 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage | SA
V_ARWF_FSTTRP_5 | 5044.5111 | 0 | 2.0833 | 0 | Out= Ararat WF fast tripping scheme (disabled), Limit Ararat Windfarm upper limit to 5 MW, DS only. Swamp out if the scheme is in service (enabled). | NIL | Vic
VS_350 | 4999.634 | 0 | 18.8333 | 0 | Victoria to SA on VicSA upper transfer limit of 350 MW | Outage | Vic
F_Q+CC3_R6 | 4887.119 | 0 | 0.5 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 3) | Outage | FCAS
S>>BRTW_NIL_WEMWP4 | 4864.6169 | 0 | 1.5833 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
V>>V_NIL_6A_R | 4836.0743 | 0 | 11 | 0 | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL | Vic
S>PATW_BWPA_HUWT | 4765.3088 | 0 | 1.0833 | 0 | Out= Para-Templers West 275kV line, avoid O/L Hummocks- Waterloo132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
F_T+FASH_N-2_TG_R6_1 | 4693.4839 | 472.9925 | 11.3333 | 2.0833 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment1 | Outage | FCAS
F_T+NIL_ML_L5 | 4646.2086 | 272.95 | 1924.0833 | 183.9167 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN++APD_TL_L5 | 4533.1843 | 5167.5672 | 1551.8333 | 1248.1667 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS
T_ROCOF_1 | 4520.5502 | 20678.1419 | 24.25 | 49.25 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
F_Q+CC4_R6 | 4502.8033 | 0 | 0.41667 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Callide C unit 4) | Outage | FCAS
Q:N_1078 | 4381.8721 | 0 | 18.5833 | 0 | QNI oscillatory stability limit of 1078 MW | Outage | Qld
Q_MEWF1_ZERO | 4282.294 | 0 | 0.33333 | 0 | Mt Emerald Wind Farm upper limit of 0 MW | Outage | Qld
CA_MQS_49FC5770_02 | 4271.2616 | 0 | 1.0833 | 0 | Constraint Automation, O/L HADSPEN TRANSF T1 for CTG TTAG on trip of HADSPEN #2 220/110KV TRANSFORMER. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
S>NIL_HUWT_STBG2 | 4267.444 | 0 | 0.33333 | 0 | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line.[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
S>>PARB_RBTU_WTTP | 4256.4509 | 0 | 7.25 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage | SA
F_Q++LDMU_L5 | 4088.3013 | 908.2682 | 21.5 | 2.9167 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage | FCAS
TVBL_ROC | 4007.6324 | 6348.9875 | 7.0833 | 12.6667 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL | Tas
V::N_HORC_xxx | 3878.3174 | 64.702 | 5.4167 | 0.58333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
S_PPT+TIPSB_800 | 3773.4128 | 0 | 18.1667 | 0 | Heywood IC (VIC-SA) <= 800- (Pelican Pt GT11) -Max(TIPS B units, TIPS A units, Osbourne, QPS5, Snowthown North+South, Mintaro, Pelican) - South East generation + South East Load; NOTE: Pelican PT output restricted to 400MW | NIL | SA
S::V_TBSE_TBSE_1 | 3732.6627 | 173.5603 | 4.75 | 2.1667 | Out = one Tailembend-South East 275kV line (NOTE: with both Black Range series capacitors I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines | Outage | SA
SA_HYSE2 | 3692.4021 | 0 | 0.41667 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage | SA
Q>>GGWU_GGCP2_GGCP1 | 3671.302 | 0 | 4.9167 | 0 | Out= Gin Gin to Wurdong (819), avoid O/L Gin Gin to Calliope River (813) on trip of Gin Gin to Calliope River (814) line, Feedback | Outage | Qld
F_T+FASH1_2C_RREG | 3460.0889 | 0 | 16.3333 | 0 | Out = Farrell to Sheffield No.1 or 2 line; John Butters, Tribute and Reece 1, 2 unavailable for raise FCAS | Outage | FCAS
F_Q++8C_L6 | 3433.3968 | 0 | 27.3333 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage | FCAS
V_MACARTHUR_ZERO | 3367.7312 | 48275.9721 | 0.33333 | 20.5833 | Macarthur upper limit of 0 MW | Outage | Vic
S>KHKN_NIL_SETX12 | 3318.115 | 0 | 0.33333 | 0 | Out=Keith-Kincraig 132kV line, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
S>>NIL_HUBG-T_WEWT2 | 3285.5257 | 0 | 0.41667 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Hummocks-Snowtown-Bungama 132kV T line (this trips Snowtown WF).[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL | SA
N^^V_DDSM1 | 3237.3533 | 3338.0314 | 6.25 | 12.5 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage | NSW
N_SILVERWF_WT | 3230.041 | 0 | 0.25 | 0 | Limit number of turbine online for Silverton wind farm to not exceed 13 with Broken Hill solar generating | Outage | NSW
Q_CS_1750 | 3175.0616 | 0 | 5.3333 | 0 | Qld Central to Qld South upper transfer limit of 1750MW (discretionary) | Outage | Qld
F_I+NIL_APD_TL_L60 | 3163.9779 | 1251.0838 | 5415.9167 | 3286.4167 | Lower 60 sec Service Requirement for the loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | NIL | FCAS
V_MTGELIBRAND_ZERO | 3145.8174 | 0 | 0.25 | 0 | Mt Gelibrand wind farm upper limit of 0 MW | Outage | Vic
T_V_NIL_BL1 | 3046.1384 | 2385.0688 | 6.6667 | 5 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL | Tas
F_T++NIL_MG_R60 | 2996.3348 | 2141.0275 | 61.1667 | 59.3333 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
F_I+NIL_MG_R60_PPN2 | 2975.0156 | 0 | 58.0833 | 0 | Out = Nil, Raise 60 sec requirement for a NEM Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible) | NIL | FCAS
F_T++NIL_MG_R5 | 2952.8572 | 733.3027 | 21.5833 | 20.0833 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL | FCAS
V>>V_ROTS_TX_2B_R | 2901.4307 | 0 | 13.9167 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
T>T_GTHA_IMP_4O | 2893.2598 | 0 | 3.25 | 0 | Out = Hadspen to George Town 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Sheffield) for trip of remaining Hadspen to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
NQTE_BLOCK_ECS | 2852.3919 | 0 | 64.4167 | 0 | Minimum of 29MW on Directlink QLD to NSW to ensure that Directlink ECS will not operate when Directlink support is required | Outage | NSW
F_MAIN+APD_TL_L60 | 2838.9591 | 180.77 | 1916.4167 | 218.8333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink unable to transfer FCAS | NIL | FCAS
S_LB3_0 | 2820.5682 | 0 | 0.83333 | 0 | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
N^N_KKLS_1 | 2767.3065 | 39788.3875 | 20 | 232.0833 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage | NSW
T^T_LIPM_1 | 2752.5689 | 0 | 2.5833 | 0 | Out = Liapootah to Waddamana to Palmerston 220 kV line, avoid voltage instability or violations for loss of the other Liapootah to Waddamana to Palmerston line | Outage | Tas
Q:NIL_CS | 2748.6657 | 0 | 7.5 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW) | NIL | Qld
VN_1050 | 2727.8113 | 0 | 2.75 | 0 | Discretionary Vic to NSW transfer upper limit of 1050 MW | Outage | Vic
S_HPRL1_E | 2647.6904 | 64847.8263 | 3.1667 | 1.3333 | Out= Nil, Hornsdale Battery load energy target <= 40 MW | NIL | SA
N>>N-NIL__G_15M | 2527.7143 | 0 | 5.9167 | 0 | Out= Nil, avoid O/L Upper Tumut to Yass (2) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL | NSW
Q>N-MUTE_758 | 2515.3888 | 4852.2021 | 47.8333 | 68.8333 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
S>RBPA_BWMP_HUWT | 2487.5308 | 0 | 0.33333 | 0 | Out= Robertstown-Para 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Blyth Munno Para 275kV line, Feedback | Outage | SA
V>>V-MSUT_1 | 2484.9675 | 0 | 4.4167 | 0 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage | Vic
F_T++FASH_N-2_TG_R5 | 2366.8855 | 24.6036 | 2.4167 | 1.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
S>NIL_LKDV_CNRB | 2363.829 | 11040.3751 | 0.25 | 0.91667 | Out= NIL, avoid O/L Canowi-Robertstown 275kV on trip of Mt Lock-Davenport 275kV line, Feedback | NIL | SA
F_S++ML_L5 | 2349.7101 | 0 | 0.25 | 0 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage | FCAS
N_WRWF1_055 | 2331.2629 | 0 | 1.6667 | 0 | WhiteRock WF upper limit of 55 MW | Outage | NSW
T^^V_PMSH_1 | 2295.8806 | 0 | 4.0833 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of either one Sheffield to Georgetown 220kV line or one Hadspen to Georgetown 220kV line. | Outage | Tas
V^SML_HORC_3 | 2253.3327 | 3.7568 | 16.9167 | 0.33333 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
S_LB2WF_CONF | 2237.5445 | 4541.3898 | 0.66667 | 1.25 | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
F_T++COGT_TL_L6 | 2203.9378 | 3.9123 | 12.5 | 2.8333 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_Q+TNT_R6 | 2177.2835 | 0 | 0.58333 | 0 | Raise 6 sec Service Requirement for Qld Generation Event (Tarong North) | Outage | FCAS
V::S_HYSE_MAXG_2 | 2172.0484 | 0 | 3.1667 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage | SA
S>KNPW_NIL_SETX12 | 2167.4258 | 0 | 0.16667 | 0 | Out=Penola West-Kincraig 132kV line, avoid O/L of either South East 132/275kV TX1 or TX2 on Nil trip ( for Transformer SECS assumed I/S or O/S), Feedback | NIL | SA
QNTE_ROC | 2116.0317 | 2264.2143 | 43.5 | 8.1667 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
Q_CLARESF1_ZERO | 2113.4694 | 0 | 0.16667 | 0 | Clare solar farm upper limit of 0 MW | Outage | Qld
N^^V_DDWG | 2091.4779 | 10756.9677 | 3.8333 | 14.75 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V_MTGBRAND_22WT | 2088.6822 | 0 | 0.16667 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 22 | Outage | Vic
T>T_NIL_BL_IMP_7C | 2071.2001 | 0 | 11.5 | 0 | Out = Nil, avoid O/L Farrell to Sheffield No. 1 220 kV line for trip of the Farrell to Sheffield No. 2 220 kV line with no SPS action, feedback | NIL | Tas
F_T++NIL_ML_L60 | 2035.9827 | 384.8854 | 656.9167 | 206.4167 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
NQ_ZERO | 1960.5649 | 0 | 0.41667 | 0 | NSW to Qld on QNI upper transfer limit of zero MW | Outage | NSW
F_T+FARE_N-2_TG_R6_2 | 1924.5062 | 0 | 2.5 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 2 | Outage | FCAS
V>>V_NIL_5 | 1897.642 | 86009.0246 | 2.25 | 35 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL | Vic
V>V_HWYP2_1_R | 1891.6976 | 262.5967 | 2.0833 | 0.25 | Out = Hazelwood to Yallourn No. 2 220 kV line, avoid O/L Yallourn to Hazelwood PS No.1 220kV line on trip of Yallourn to Rowville No.5 220kV line, Radial mode, YWG1 on 220kV, Feedback | Outage | Vic
T>T_NIL_BL_3C | 1853.2154 | 241.2419 | 5.4167 | 0.16667 | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
VS_050 | 1804.4761 | 195427.8757 | 8.4167 | 59.4167 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage | Vic
N>>N-964__3_OPENED | 1802.1633 | 0 | 4.1667 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | Outage | NSW
T>T_PMSH_2B | 1687.0606 | 125.1676 | 7.5 | 0.41667 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
S>NIL_NIL_SGMYSE-T2 | 1682.2811 | 2372.9336 | 1.5833 | 2.25 | Out= NIL, avoid O/L Snuggery Mayura -South East T 132kV line on Nil trip (for Line component SECS assumed O/S or I/S), Feedback | NIL | SA
N>>N-NIL_01N | 1675.4656 | 21901.7897 | 1.0833 | 0.16667 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL | NSW
N^N-89_LSTX_SVC | 1651.9549 | 0 | 11.3333 | 0 | Out= Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage | NSW
VS_300 | 1638.1745 | 0 | 3.4167 | 0 | Victoria to SA on VicSA upper transfer limit of 300 MW | Outage | Vic
S>NWB6021_TX3 | 1629.8284 | 0 | 1.75 | 0 | Out= North West Bend 132kV CB6021, avoid O/L North West Bend 66/132kV #3 TX on trip of Robertstown-NWB #1 132kV line, Feedback | Outage | SA
S>>MKRB_BWPA_BRTW | 1625.0656 | 0 | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V:T_NIL_BL_1 | 1597.47 | 0 | 2.8333 | 0 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL | Vic
T>T_NIL_TOV_5F | 1498.6322 | 0 | 2.4167 | 0 | Out = Nil, avoid TOV following NCSPS slow action for O/L of Hadspen to Georgetown No. 1 220 kV lines (flow to North) for trip of the Hadspen to Georgetown No. 2 220 kV line, considering status of Tamar CCGT, feedback equation | NIL | Tas
T>T_PM_TX_1A | 1483.1851 | 0 | 5.8333 | 0 | Out= Palmerston 220/110kV transformer, prevent overload of either Palmerston to Hadspen 110kV line (flow to North) for trip of the parallel Palmerston to Hadspen 110 kV line, feedback | Outage | Tas
S>BRTW_BWPA_HUWT | 1440.3125 | 50055.746 | 0.083333 | 4.0833 | Out= Brinkworth- Templers West 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
N^^Q_NIL_A | 1425.3606 | 1391.5017 | 6.9167 | 8.5 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL | NSW
S>KNPW_SETX_SETX1 | 1424.128 | 0 | 0.25 | 0 | Out=Penola West-Kincraig 132kV line, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS O/S), Feedback | Outage | SA
T>>T_NIL_BL_EXP_5F | 1418.5756 | 0 | 0.33333 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
F_T++FASH1_2C_TG_R6 | 1412.3621 | 0 | 1.0833 | 0 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage | FCAS
SVML_233 | 1348.5425 | 364.2511 | 3.5 | 0.5 | SA to Vic on ML upper transfer limit of 233 MW | NIL | SA
QNTE_OSCILLATE | 1334.9034 | 490.3384 | 4.9167 | 9.4167 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage | Qld
F_Q_TARONG#2_RREG | 1279.2412 | 17.1005 | 8.0833 | 0.16667 | Out= NIL, Tarong 2 RREG Requirement <= 0MW | Outage | FCAS
Q::N_ARSVC_AR_2L-G | 1265.236 | 0 | 14.9167 | 0 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
NQTE_ROC | 1218.5704 | 13766.606 | 48.75 | 16.6667 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | NSW
V::N_HYSE_xxx | 1215.1264 | 0 | 4.25 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_T++FASH1_2C_TG_R5 | 1214.207 | 0 | 5.8333 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage | FCAS
S:V_PA_SVC_420 | 1209.5097 | 0 | 1.3333 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage | SA
T>T_GTSH_IMP_4K | 1188.6571 | 2715.8572 | 3.25 | 3.6667 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
F_T+FARE_N-2_TG_R6_1 | 1169.3009 | 153.6346 | 1.5 | 0.66667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink unable to transfer FCAS, Segment 1 | Outage | FCAS
F_MAIN++APD_TL_L60 | 1156.3701 | 443.1486 | 1232.9167 | 805.8333 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL | FCAS
V>>V_DDSM_1 | 1117.2664 | 196.0694 | 4.0833 | 0.16667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage | Vic
N^^V_BUDP_1 | 1113.9697 | 0 | 1.5833 | 0 | Out = Buronga to Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
V_MTGBRAND_33WT | 1089.4284 | 0 | 0.083333 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 33 | Outage | Vic
V>V_NIL_7 | 1087.306 | 0 | 0.083333 | 0 | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Vic
VSML_VFRB_OFF | 1066.1083 | 11.6181 | 4.4167 | 0.083333 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL | Vic
V::N_HWSM_xxx | 1054.8256 | 21877.1245 | 8.6667 | 48.9167 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_S++OSB_R6_1 | 1038.0672 | 0 | 0.33333 | 0 | Raise 6 sec Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA, Segment 1 | Outage | FCAS
F_T++NIL_ML_L6 | 1032.0469 | 122.8562 | 995.1667 | 119.0833 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
T>T_PMSH_5A | 1024.7265 | 0 | 2.6667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L line terminal equipment of Hadspen to Palmerston No. 1 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 2 220 kV line, feedback | Outage | Tas
T>T_PMWA_110_7 | 1005.19 | 0 | 0.083333 | 0 | Out= Palmerston to Waddamana 110 kV line, avoid overloading the New Norfolk to Chapel St 110 kV line (flow to South) on trip of New Norfolk to Creek Road 110 kV line, feedback | Outage | Tas
F_S++ML_L6_1 | 989.0651 | 0 | 0.25 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage | FCAS
N>>V-LTMS_5 | 966.2142 | 0 | 0.91667 | 0 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage | NSW
I_CTRL_ISSUE_ML | 963.8263 | 22.2175 | 0.58333 | 0.41667 | DC Link Control Issue Constraint for Murraylink | Outage | Other
F_T+COGT_TL_L5 | 961.4038 | 0 | 9.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS
F_Q_TARONG#2_R5 | 951.617 | 0 | 7.6667 | 0 | Out= NIL, Tarong 2 R5 Requirement <= 0MW | Outage | FCAS
F_Q_TARONG#1_RREG | 946.9039 | 17.1005 | 6.4167 | 0.16667 | Out= NIL, Tarong 1 RREG Requirement <= 0MW | Outage | FCAS
V::N_JNWO_xxx | 944.2402 | 0 | 2.6667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
N>N-ARKK_CH_CB892A | 930.1141 | 0 | 2.5833 | 0 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Swamp out when all 3 directlink cable O/S, Feedback. TG formulation in PD/ST | Outage | NSW
N^^Q_TW_330_BUS3_B1 | 930.0696 | 885.8167 | 1.3333 | 1 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage | NSW
N^^V_MSDD2 | 921.4212 | 0 | 2.9167 | 0 | Out = Dederang to Murray 330 kV line, avoid voltage collapse at Darlington Point for loss of the remaining Dederang to Murray 330 kV line | Outage | NSW
N^^V_SMTXF2_1 | 835.9719 | 0 | 1.3333 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
F_Q++8C_L5 | 816.1684 | 0 | 16.5 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage | FCAS
T>T_GTSH_2D | 811.5001 | 0 | 2.3333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown 220 kV line (flow North) for trip of other Hadspen to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
F_Q_TARONG#1_R5 | 768.8982 | 0 | 6.25 | 0 | Out= NIL, Tarong 1 R5 Requirement <= 0MW | Outage | FCAS
F_MAIN+ML_L6_0400 | 718.75 | 160.69 | 1663.9167 | 515.6667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_NVS++MG_R6 | 716.889 | 0 | 1.0833 | 0 | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS
V>>V_SMTT2_2 | 708.4367 | 0 | 0.75 | 0 | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the Thomastown to South Morang No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
F_NVS++MG_R60 | 704.4772 | 0 | 1.0833 | 0 | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage | FCAS
V::N_DDSM_xxx | 682.1571 | 3506.5355 | 1.3333 | 4.9167 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
T_T_FA_TX_1 | 670.5886 | 0 | 1.1667 | 0 | Out = Farrell 220/110kV transformer, limit Mackintosh <= 110% of West Coast load | Outage | Tas
V^SML_BUDP_3 | 648.089 | 0 | 5.3333 | 0 | Out = Buronga to Balranald to Darlington Pt (X5) 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage | Vic
VSML_000 | 639.2572 | 0 | 3.4167 | 0 | Vic to SA on ML upper transfer limit of 0 MW | Outage | Vic
N^^V_MSUT_1 | 618.0509 | 5837.8511 | 2.1667 | 20.0833 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage | NSW
Q>>LCCP_CLWU_BCCP_2 | 589.8442 | 0 | 1.6667 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
T_V_FCSPS_RAMP | 586.028 | 0 | 1.0833 | 0 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
T:T_LIPM_2 | 576.0043 | 0 | 1.3333 | 0 | Out = Liapootah to Palmerston 220kV line, avoid transient instability for fault and trip of remaining Liapootah to Palmerston line (flow to North) | Outage | Tas
T>T_HAPM_IMP_4A | 568.6046 | 0 | 0.41667 | 0 | Out = Hadspen to Palmerston No. 2 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
F_I+ML_L6_0400 | 562.4403 | 953.7252 | 2086.5833 | 4520.5 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS
F_T+FARE_N-2_RREG | 560.1774 | 17.4584 | 0.58333 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Reece 1 & 2 Raise Regulation Requirement = 0 | Outage | FCAS
F_T++BLSPS_EXP_L6_2 | 558.1219 | 0 | 3.8333 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage | FCAS
N>LSDU_LSDU | 530.8382 | 27705.4928 | 12 | 32.5833 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
F_Q++8C_L60 | 507.5702 | 0 | 16.4167 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 60 sec Requirement | Outage | FCAS
F_V+NIL_APD01_R5 | 500.2766 | 278.2833 | 3.5 | 3.9167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
S_LB_1+2+3_150 | 499.9321 | 0 | 0.75 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=150 MW | Outage | SA
N>LSDU9U6_LSDU9U7 | 492.5812 | 0 | 6.6667 | 0 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
VS_400 | 474.6291 | 0 | 2.9167 | 0 | Victoria to SA on VicSA upper transfer limit of 400 MW | Outage | Vic
N>N_LSDU_9U6_1 | 455.348 | 0 | 2 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage | NSW
S>>X_RBPA+CB_03 | 446.8139 | 0 | 8.6667 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage | SA
F_Q+TNT_R60 | 433.04 | 0 | 0.25 | 0 | Raise 60 sec Service Requirement for Qld Generation Event (Tarong North) | Outage | FCAS
V^^S_NIL_TBSE_2 | 430.1134 | 0 | 0.33333 | 0 | Out = Nil(Note: with one or both Black Range series capacitors O/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL | SA
Q_CS_1950 | 418.9061 | 0 | 1.5 | 0 | Qld Central to Qld South upper transfer limit of 1950MW (discretionary) | Outage | Qld
Q_CS_2000 | 413.9815 | 0 | 1.5833 | 0 | Qld Central to Qld South upper transfer limit of 2000MW (discretionary) | Outage | Qld
V>>V_NIL_3 | 409.8728 | 0 | 0.5 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL | Vic
Q::N_AR_CP2_AR_2L-G | 403.3262 | 0 | 1.5 | 0 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage | Qld
F_Q_TARONG#2_R60 | 398.7714 | 459.1328 | 8.0833 | 2.3333 | Out= NIL, Tarong 2 R60 Requirement <= 0MW | Outage | FCAS
V_EILDON2_000 | 393.3946 | 0 | 0.25 | 0 | Discretionary upper limit for Eildon unit 2 of 0 MW | Outage | Vic
T>T_PMSH_2A | 390.1328 | 298.5442 | 0.58333 | 1.0833 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow to George Town) for trip of the other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
N^^Q_MUTW_1_B1 | 381.7424 | 0 | 0.25 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage | NSW
T_GO_300 | 376.091 | 0 | 3.75 | 0 | Discretionary 300 MW upper limit on total Gordon generation | Outage | Tas
V:T_HAPM_BL_1 | 372.0751 | 0 | 1 | 0 | Out = Hadspen to Palmerston 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to Palmerston 220 kV line, Tamar CCGT out of service | Outage | Vic
V>>V_KTS_TX_A2_2A_R | 369.2916 | 4701.8228 | 1.75 | 9.0833 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage | Vic
N>>N-X_WGYS_99M_992 | 355.8011 | 0 | 0.66667 | 0 | Out = Out = Murrumburrah to Yass 132kV line (99M) and Burrinjuck to Tumut132 132kV line (992), avoid Lower Tumut to Wagga 330kV (051) O/L on Murray - Dederang 330kV (67 or 68) trip with DBUSS action | Outage | NSW
S>>NIL_RBTX1_WTWE | 346.6691 | 0 | 0.083333 | 0 | Out= NIL, avoid O/L Waterloo-Waterloo East 132kV line on trip of Robertstown 275/132kV TX1, Feedback | NIL | SA
V::N_EPMB_xxx | 335.6252 | 352.9106 | 3.8333 | 0.66667 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
V^SML_KGRC_4 | 328.8384 | 0 | 1.5 | 0 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage | Vic
QN_ZERO | 326.7007 | 0 | 1 | 0 | Qld to NSW on QNI upper transfer limit of 0 MW | Outage | Qld
Q::NIL_CS | 321.6754 | 0 | 2.0833 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW), 2008/2009 implementation | NIL | Qld
V>SMLARHO3 | 319.281 | 0 | 0.083333 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Kerang to Wemen 220 kV line section on loss of Balranald to Darlington Point (X5/1) line | Outage | Vic
F_Q_TARONG#1_R60 | 318.6183 | 404.1328 | 6.4167 | 1.9167 | Out= NIL, Tarong 1 R60 Requirement <= 0MW | Outage | FCAS
F_STHN+MG_R5 | 316.3325 | 0 | 1 | 0 | Raise 5 min Service Requirement for a Southern Generation Event | Outage | FCAS
F_Q_TARONG#2_R6 | 310.2529 | 23.2 | 7 | 0.33333 | Out= NIL, Tarong 2 R6 Requirement <= 0MW | Outage | FCAS
V^^S_MLSY_2 | 310.0612 | 0 | 1.6667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
VSML_-040 | 307.601 | 185.7213 | 0.75 | 0.33333 | Vic to SA on ML upper transfer limit of -40 MW | Outage | Vic
F_T++NIL_ML_L5 | 305.2553 | 8.6363 | 73.25 | 21.5 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL | FCAS
V>>SML_NIL_8 | 305.1293 | 185106.6913 | 0.16667 | 2.4167 | Out = Nil, avoid O/L Ballarat to Bendigo 220 kV line (flow North) for loss of Shepparton to Bendigo 220 kV line, 15 minute line ratings, feedback | NIL | Vic
S>>MKRB_NIL_WEMWP4 | 296.0492 | 0 | 0.91667 | 0 | Out= Mokota-Robertstown 275kV line,, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL | SA
N>>Q_LDMU_B | 289.8083 | 241466.3429 | 1.25 | 11.9167 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage | NSW
F_S++OSB_R5 | 267.462 | 0 | 0.083333 | 0 | Raise 5 min Service Requirement for SA Generation Event, where Osborne Power Station is the largest generation risk in SA | Outage | FCAS
F_T+FASH_N-2_TG_R60 | 266.5566 | 15.93 | 6 | 0.58333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
N>N-NIL_LSDU | 265.3292 | 23087.3702 | 6 | 7.8333 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
T::T_NIL_3 | 262.8822 | 3818.5061 | 1.9167 | 8.5 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. Swamped if Tamar CCGT OOS. | NIL | Tas
F_Q_TARONG#1_R6 | 259.3614 | 23.2 | 5.5 | 0.33333 | Out= NIL, Tarong 1 R6 Requirement <= 0MW | Outage | FCAS
S>V_NIL_SETX_SETX | 256.1299 | 0 | 0.16667 | 0 | Out= Nil, avoid overloading a South East 132/275 kV transformer on trip of the remaining South East 132/275 kV transformer(for Transformer component SECS I/S), Feedback | NIL | SA
V::S_KNPW_MAXG | 249.6351 | 0 | 2.8333 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA.. | Outage | SA
T>>T_HAPM_EXP_3A | 246.8136 | 0 | 0.083333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
V::N_JNWG_xxx | 242.9541 | 0 | 0.41667 | 0 | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
S>>BLMK_NIL_WEMWP4 | 240.218 | 1572.348 | 0.58333 | 0.58333 | Out= Belalie-Mokota 275kV line (This offloads Willalow substation and Willagoleche WF) OR Belalie-Willalow 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on Nil trip, Feedback | NIL | SA
T>T_HAPM_220_5A | 238.9209 | 0 | 0.5 | 0 | Out = Hadspen to Palmerston 220kV line, avoid O/L either Palmerston to Hadspen (No. 3 or No. 4) 110kV line (flow to North) for loss of the remaining Hadspen to Palmerston 220kV line, Feedback | Outage | Tas
S-LB2_0 | 238.3763 | 0 | 0.16667 | 0 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
V>>V_MLTS_TX_2A_R | 230.6281 | 0 | 0.66667 | 0 | Out = Moorabool A1 or A2 500/220kV transformer, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage | Vic
F_V+NIL_APD01_R60 | 228.95 | 273.2801 | 3.5833 | 4.0833 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
Q>>BCCP_CLWU_LCCP_2 | 224.238 | 0 | 1.5 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
F_MAIN++ML_L6_0400 | 222.0729 | 555.8295 | 610.75 | 2051.9167 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS
CA_SPS_4A3DEF97_02 | 216.5597 | 0 | 0.083333 | 0 | Constraint Automation, O/L HWTS TRANSF A2TR_500 for CTG TVVN on trip of HWPS-HWTS4 220KV LINE & HWTS A4 TR. Generated by STNET[NORFL] Host NOREEMP4(SP) | Outage | Constraint Automation
S>>MOTB_TBTU_TBCG | 204.8565 | 0 | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
VSML_015 | 200.5494 | 0 | 2.25 | 0 | Vic to SA on ML upper transfer limit of 15 MW | Outage | Vic
N^^Q_ARDM_B1 | 198.9204 | 0 | 1.6667 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V>>V_ROTS_TX_3A_R | 198.3035 | 0 | 1.0833 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage | Vic
V^^S_TBTX+CB_SETB | 197.3081 | 0 | 2.1667 | 0 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
V::S_KHKN_MAXG | 184.5001 | 0 | 1.0833 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
F_T++FASH_N-2_TG_R6 | 182.6174 | 1527.6622 | 1.75 | 3.8333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
Q_KSP1_ZERO | 182.3699 | 0 | 0.083333 | 0 | Kidston solar farm upper limit of 0 MW | Outage | Qld
F_T++FASH1_2C_TG_R60 | 178.8632 | 0 | 2.5 | 0 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage | FCAS
F_V+NIL_APD01_R6 | 176.8579 | 598.9901 | 3.5 | 3.9167 | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
T_MB_ZERO | 171.32 | 0 | 0.083333 | 0 | Limit Meadowbank to zero MW | Outage | Tas
V_S_NIL_ROCOF | 161.1965 | 27221.0258 | 2.4167 | 134.1667 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | Vic
F_Q_TARONG#2_LREG | 159.757 | 0 | 1.9167 | 0 | Out= NIL, Tarong 2 LREG Requirement <= 0MW | Outage | FCAS
N^^Q_LS_VC_B4 | 153.0126 | 154.2712 | 2.1667 | 1.9167 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage | NSW
F_S++ML_L60 | 146.2139 | 0 | 0.16667 | 0 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage | FCAS
F_V_APD01_R5 | 144.9243 | 9402.365 | 0.66667 | 64.4167 | Out= NIL, APD Potline 1 R5 Requirement <= 0MW | Outage | FCAS
F_T+FARE_N-2_TG_R5 | 139.6305 | 5.147 | 2.6667 | 0.083333 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink unable to transfer FCAS | Outage | FCAS
V^^S_TBTX+CB_SETB_2 | 137.7176 | 0 | 1.3333 | 0 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage | SA
S>>BRTW_BWPA_WTTP | 136.3539 | 0 | 0.25 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA
V>>N-LTUT_B | 135.1948 | 2122.4495 | 0.33333 | 1.5833 | Out = LowerTumut-UpperTumut(64), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
Q>>PWSP_WOSP_PWCE | 131.0262 | 0 | 0.25 | 0 | Out= Palmwoods to South Pine (808) line, avoid O/L Palmwood to Caboolture (746/4) 110kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage | Qld
F_V_APD01_R6 | 130.26 | 18386.7038 | 0.66667 | 64.4167 | Out= NIL, APD Potline 1 R6 Requirement <= 0MW | Outage | FCAS
F_T++FASH_N-2_TG_R60 | 129.4877 | 208.1177 | 3.8333 | 4.9167 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
T>T_X_BWLF_PMWA110_2 | 122.1529 | 0 | 0.58333 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana AND Palmerston to Waddamana 110kV lines, avoid O/L Tungatinah to Meadowbank Tee2 110kV line on trip of Tungatinah to Meadowbank Tee 1 to New Norfolk 110kV lines, Feedback | Outage | Tas
I_QNI_ONE_PHASE_N-2 | 118.571 | 0 | 1.4167 | 0 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage | Other
V>>N_SM330_2B_3 | 115.5501 | 0 | 0.25 | 0 | Out = South Morang F2 500/330 kV and either H1 or H2 330/220 kV txfmr, SMTS 220kV bus tied, avoid O/L Ballarat to Bendigo 220kV line on trip of South Morang H2 or H1 220/330kV transformer, Feedback | Outage | Vic
V:SS_820_HY_TEST_DYN | 114.865 | 17614.4335 | 0.16667 | 6.5 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL | Vic
F_T+FASH_N-2_TG_R5 | 113.928 | 1.2 | 4.25 | 0.083333 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
N::V_DDMS | 108.8064 | 3611.6904 | 0.83333 | 1.4167 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage | NSW
N>Q-MUTW_2 | 105.5738 | 0 | 0.41667 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage | NSW
V:SS_820_HY_TEST | 101.9453 | 1079.6816 | 0.083333 | 2.8333 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade. | NIL | Vic
V::S_NIL_SETB_SECP_1 | 99.9158 | 274.9595 | 2.4167 | 0.5 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL | SA
N>N-GITN_TE_C1 | 95.0685 | 0 | 0.75 | 0 | Out= Glen Innes to Tenterfield (96R), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
NQTE_-070 | 93.0858 | 0 | 1.25 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW | Outage | NSW
Q>>LCCP_BCCP_CLWU_2 | 92.4807 | 0 | 0.33333 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage | Qld
N^N_CHLS_1 | 92.4042 | 0 | 2.75 | 0 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage | NSW
F_NVS+MG_R5 | 86.8 | 0 | 0.25 | 0 | Raise 5 min Service Requirement for NSW, Vic and SA Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
VS_250_DYN | 82.504 | 5055.532 | 0.75 | 10.3333 | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage | Vic
F_V_EILDON2_R5 | 77.9103 | 0 | 0.25 | 0 | Out= NIL, Eildon 2 R5 Requirement <= 0MW | Outage | FCAS
F_T+RREG_0100 | 75.2357 | 0 | 0.33333 | 0 | Tasmania Raise Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS | Other | FCAS
QNTE_150 | 75.1632 | 10469.2959 | 0.083333 | 19.5833 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW | Outage | Qld
V^^S_SEVC1_SETB | 73.6023 | 0 | 1.1667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage | SA
T>T_GTSH_2C | 73.4704 | 0 | 0.083333 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
S>>V_MOTB_TUTB_CGTB | 72.4809 | 0 | 0.083333 | 0 | Out=Mobilong - Tailem Bend 132kV line; avoid O/L Cherry Gardens -Tailem Bend 275kV on trip Tungkillo -Tailem Bend 275kV line, Feedback | Outage | SA
F_Q++NIL_R5 | 71.5019 | 143.0909 | 2.25 | 1.0833 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL | FCAS
S>>NIL_TBTU_TBMO_1 | 70.9652 | 122.1295 | 0.75 | 0.5 | Out= NIL, avoid O/L Tailem Bend-Mobilong 132kV line on trip of Tailem Bend-Tungkillo 275kV line, Feedback | NIL | SA
V>>BABE_DDGN_N-2 | 68.7371 | 0 | 0.16667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage | Vic
F_QNV+RREG_0130 | 67.3507 | 0 | 0.16667 | 0 | Qld, NSW and Vic Raise Regulation Requirement greater than 130 MW, Basslink unable to transfer FCAS | Outage | FCAS
F_T++CSGO_TG_R5 | 66.91 | 0.1 | 0.58333 | 0.16667 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage | FCAS
F_V_APD01_R60 | 66.8742 | 7929.9714 | 0.66667 | 64.4167 | Out= NIL, APD Potline 1 R60 Requirement <= 0MW | Outage | FCAS
V>>V_ROTS_TX_3B_R | 66.2962 | 0 | 0.75 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage | Vic
F_T++COGT_TL_L5 | 63.65 | 0 | 12.5 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_T+LREG_0100 | 61.5613 | 0 | 0.25 | 0 | Tasmania Lower Regulation Requirement greater than 100 MW, Basslink unable to transfer FCAS | Other | FCAS
F_V_EILDON2_R6 | 60.6651 | 0 | 0.25 | 0 | Out= NIL, Eildon 2 R6 Requirement <= 0MW | Outage | FCAS
V>>N_SMHTX_1 | 59.6253 | 0 | 0.16667 | 0 | Out = South Morang H 330/220 kV txfmr, only one SMTS H txfmr in service, avoid O/L the remaining in service SMTS H 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage | Vic
V::S_SEVC1_MAXG | 58.5896 | 0 | 0.66667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage | SA
S>NIL_TINO3_TINO4 | 55.4436 | 0 | 0.083333 | 0 | Out = Nil, avoid O/L of TIPS-New Osborne #4 66kV line on trip of TIPS-New Osborne #3 66kV line (Note: Assumed CB 5536 at New Osborne is CLOSED). This constraint swamps out if New Osborne CB 5536 is OPEN. | NIL | SA
V>>V_MLSY_4BR | 54.5918 | 0 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage | Vic
V>>N-LTUT_G | 54.3126 | 8.2389 | 0.16667 | 0.16667 | Out = LowerTumut-UpperTumut(64), avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | Outage | Vic
Q>>BCCP_CLWU_BCRG_2 | 49.7459 | 0 | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Raglan (811) on trip of Calvale to Wurdong (871) line, Feedback | Outage | Qld
T>T_PMWA_110_2 | 49.6023 | 0 | 0.16667 | 0 | Out= Palmerston to Waddamana 110 kV line, avoid O/L Tungatinah to Meadowbank Tee 1 110kV line on trip of Waddamana to Bridgewater 110kV line, Feedback | Outage | Tas
T>T_HATX_PMWAIM_4D | 48.7311 | 0 | 0.25 | 0 | Out = Hadspen 220/110 kV txfmr and Palmerston to Waddamana 110kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
F_STHN+MG_R60 | 48.6 | 0 | 1.0833 | 0 | Raise 60 sec Service Requirement for a Southern Generation Event | Outage | FCAS
T_TAMAR_GCS_OUT | 48.3913 | 0 | 0.66667 | 0 | Out = Tamar Valley 220 kV CCGT Generation Control Scheme (GCS) - Limit output of Tamar Valley CCGT to 144 MW. | Outage | Tas
F_STHN+MG_R6 | 47.6007 | 0 | 1 | 0 | Raise 6 sec Service Requirement for a Southern Generation Event | Outage | FCAS
F_I+ML_L5_APD | 41.79 | 41.4581 | 20.5 | 21 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS
N>N-NIL_MBDU | 39.9128 | 1935.9208 | 1.25 | 3.4167 | Out = Nil, avoid overloading Mullumbimby to Dunoon line (9U6 or 9U7) on trip of the other Mullumbimby to Dunoon line (9U7 or 9U6), Feedback | NIL | NSW
NQTE_-010 | 39.081 | 0 | 0.83333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -10 MW | Outage | NSW
V::S_BLKRG_TBSE_2 | 38.5509 | 342.6106 | 0.41667 | 0.5 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage | SA
F_I+ML_L6_APD | 37.57 | 37.3973 | 172.9167 | 142 | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
S_V_NIL_ROCOF | 35.9783 | 7275.1777 | 0.66667 | 9 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL | SA
S>>PARB_TWPA_TPRS | 33.9701 | 0 | 0.083333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
F_MAIN++ML_L6_APD | 33.0199 | 3.96 | 109.5833 | 17.6667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
V::N_MLSY_xxx | 32.2171 | 0 | 0.41667 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_ESTN+MG_R5 | 30 | 0 | 0.083333 | 0 | Raise 5 min Service Requirement for Eastern Generation Event | Outage | FCAS
V>S_NIL_HYSE | 29.4439 | 3.3501 | 0.25 | 0.083333 | Out = NIL, avoid O/L either Heywood to South East 275 kV line on trip of parallel circuit, flow VIC to SA, feedback | NIL | Vic
T>T_GTSH_2A | 29.3592 | 0 | 0.16667 | 0 | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow North) for trip of other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V::N_BURC_xxx | 29.1113 | 0 | 0.16667 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
F_STHN+RREG_0130 | 28.9965 | 0 | 0.33333 | 0 | Southern Raise Regulation Requirement greater than 130 MW | Outage | FCAS
F_QNV+MG_R5 | 28.4 | 0 | 0.083333 | 0 | Raise 5 min Service Requirement for QLD, NSW, and VIC Generation Event, Basslink unable to transfer FCAS | Outage | FCAS
T>T_PMWA_110_12_1 | 27.2074 | 0 | 0.083333 | 0 | Out = Palmerston to Waddamana 110 kV line, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | Outage | Tas
V>>V_KTS_TX_A2_2B_R | 26.7852 | 0 | 0.33333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage | Vic
F_T+NIL_BB_TG_R60 | 26.7 | 131.45 | 0.5 | 4.5833 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
V^^S_KNPW_MAXG | 26.5783 | 0 | 0.5 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
F_MAIN++ML_L5_APD | 26.51 | 49.2025 | 9.9167 | 9.9167 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
F_I+ML_L5_0400 | 25.6064 | 5804.0144 | 26.1667 | 3036.9167 | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = 400 | NIL | FCAS
F_T+FASH_N-2_TG_R6_4 | 25.4182 | 0 | 0.083333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment4 | Outage | FCAS
S>>RBTX2_RBTX1_WEWT | 24.8326 | 0 | 3.1667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage | SA
V^^S_MLSY_3 | 23.7426 | 0 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage | Vic
V>>V_DDTX_C | 22.9282 | 0 | 0.083333 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage | Vic
Q:N_NIL_OSC | 22.541 | 3696.7798 | 0.083333 | 19.4167 | Out= Nil, QNI oscillatory stability limit of 1200 MW, limit reduced to 950 MW when any one SEQ SVC POD is out, limit is reduced to 853 MW when all three SEQ SVCs or PODs out. | NIL | Qld
Q>>LCCP_CLWU_BCCP | 20.6608 | 0 | 0.16667 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871), Feedback | Outage | Qld
F_T++FARE_N-2_TG_R6 | 19.6721 | 581.9718 | 0.33333 | 3.0833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
T>T_HAPM_5A | 19.374 | 0 | 0.33333 | 0 | Out = Hadspen to Palmerston No. 2 220 kV line, avoid O/L line terminal equipment of Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line, feedback | Outage | Tas
V>>N-JNWO_RADIAL_2 | 19.2704 | 0 | 0.083333 | 0 | Out = Jindera to Wodonga(060), avoid O/L Murray to Lower Tumut (66) using 15 mins rating on trip of Murray to Upper Tumut (65) line, Feedback | Outage | Vic
T>T_NIL_BL_IMP_6EE | 18.2216 | 0 | 0.083333 | 0 | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
F_T++FARE_N-2_TG_R5 | 17.801 | 0.3 | 0.083333 | 0.5 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
T>>T_NIL_BL_EXP_7C | 16.5312 | 6497.9679 | 0.16667 | 25.9167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
N>N-LSTN_TE_C1 | 15.8889 | 0 | 0.16667 | 0 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
F_T+FARE_N-2_TG_R60 | 14.4905 | 0 | 0.5 | 0 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
V>>V_NIL1A_R | 14.0597 | 0 | 0.083333 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL | Vic
VSML_040 | 13.9025 | 0 | 0.16667 | 0 | Vic to SA on ML upper transfer limit of 40 MW | Outage | Vic
F_I+WIP_N-2_ML_L6 | 13.4586 | 22.2151 | 29.6667 | 15.6667 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 6 sec requirement | Outage | FCAS
F_T+FASH_N-2_TG_R6_2 | 12.4651 | 0 | 0.33333 | 0 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS, Segment2 | Outage | FCAS
Q>CLWU_BCCP | 12.401 | 0 | 0.33333 | 0 | Constraint Automation, O/L 275KV_812 @H10_BCMB for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage | Qld
F_S++HYSE_L5 | 11.9375 | 0 | 0.5 | 0 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 5 min Requirement for risk of islanding | Outage | FCAS
F_Q++ARTW_R6 | 10.7559 | 0 | 0.16667 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage | FCAS
F_MAIN+ML_L5_0400 | 10.55 | 965.4232 | 3.9167 | 332.1667 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_T++COGT_TL_L60 | 10.34 | 0.16 | 12.5 | 0.083333 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_T+NIL_BB_TG_R5 | 9.4 | 71.4 | 0.16667 | 2.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
F_V_EILDON2_R60 | 9.29 | 0 | 0.25 | 0 | Out= NIL, Eildon 2 R60 Requirement <= 0MW | Outage | FCAS
F_T++BLSPS_EXP_L5 | 9.02 | 0 | 4.5833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage | FCAS
V^^S_MOTB_MAXG_2 | 8.735 | 0 | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
F_T+COGT_TL_L60 | 7.77 | 0 | 9.25 | 0 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink unable to transfer FCAS | Outage | FCAS
CA_MQS_49FC5770_01 | 7.1489 | 0 | 0.083333 | 0 | Constraint Automation, O/L PALMSTN TRANSF T1 for CTG TTAG on trip of HADSPEN #2 220/110KV TRANSFORMER. Generated by STNET[MANBL] Host MANEEMP1(MQ) | Outage | Constraint Automation
F_V+NIL_APD01_L5 | 6.94 | 17.41 | 3.6667 | 3.8333 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
NQTE_-080 | 6.6656 | 0 | 0.083333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -80 MW | Outage | NSW
F_I+ML_L60_APD | 6.45 | 4.3942 | 18.5833 | 20.25 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_MAIN++ML_L60_APD | 6.37 | 2.12 | 11.6667 | 5.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
N_MBTE1_A | 6.1906 | 0.38375 | 1.1667 | 0.16667 | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
F_T+NIL_BB_TG_R6 | 5.8 | 200.6161 | 0.33333 | 0.91667 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink unable to transfer FCAS | NIL | FCAS
F_I+WIP_N-2_ML_L5 | 5.7 | 0 | 3.5833 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 5 Min requirement | Outage | FCAS
F_ESTN++HYTR_L60 | 5.05 | 0 | 2.4167 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_ESTN++HYTR_L5 | 4.93 | 0 | 2.4167 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage | FCAS
F_I+ML_L60_0400 | 4.71 | 386.2774 | 12.75 | 1534.9167 | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = 400 | NIL | FCAS
F_MAIN++WIP_N-2_MLL6 | 4.5614 | 0 | 3.8333 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
V^SML_HORC_2 | 4.5441 | 0 | 0.25 | 0 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage | Vic
F_MAIN++ML_L5_0400 | 4.2536 | 3534.2212 | 3.25 | 1519.0833 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS
VSML_020 | 4.2245 | 0 | 0.41667 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage | Vic
V::N_MLTX_xxx | 4.0997 | 0 | 0.16667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage | Vic
N::Q_MUTW_1 | 3.8955 | 0 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage | NSW
F_STHN+LREG_0120 | 3.81 | 0 | 0.083333 | 0 | Southern Lower Regulation Requirement greater than 120 MW | Outage | FCAS
F_MAIN+ML_L60_0400 | 2.99 | 132.2634 | 3.5833 | 275.8333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
F_T+GTTE_TL_L60 | 2.88 | 0 | 1.3333 | 0 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS
F_T_FATI_R5 | 2.8431 | 0 | 0.16667 | 0 | Out=Farrell-Tribute 220KV line. R5 <= 0MW | Outage | FCAS
F_T_FATI_RREG | 2.8431 | 0 | 0.16667 | 0 | Out=Farrell-Tribute 220KV line. RREG <= 0MW | Outage | FCAS
F_Q_W/HOE_R5 | 2.78 | 428.1946 | 0.083333 | 1.75 | Out= Nil, Wivenhoe Raise 5 services <= 0 MW when both units are online in gen mode | Outage | FCAS
F_MAIN+ML_L6_APD | 2.75 | 1.24 | 7.5 | 2.1667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_I+WIP_N-2_ML_L60 | 2.69 | 0 | 3.4167 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Global Lower 60 sec requirement | Outage | FCAS
F_V+NIL_APD01_L60 | 2.32 | 5.61 | 3.5833 | 3.1667 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_T++BLSPS_EXP_L60_2 | 2.25 | 0 | 3.75 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2 | Outage | FCAS
F_MAIN++WIP_N-2_MLL5 | 2.24 | 0 | 0.75 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 5 Min requirement, Basslink able to transfer FCAS | Outage | FCAS
V>SML_NSWRB_9 | 1.9618 | 0 | 0.25 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Bendigo to Kerang 220 kV line for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL | Vic
Q>N-MUTE_757 | 1.9612 | 1634.7018 | 0.5 | 28.5833 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage | Qld
F_T+GTTE_TL_L6 | 1.92 | 0 | 1.3333 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS
S>>KNPW_SETB_SETB | 1.8237 | 0 | 0.083333 | 0 | Out= Penola West-Kincraig 132 kV line (Note: with both Black Range series caps I/S or O/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage | SA
F_MAIN+WIP_N-2_ML_L6 | 1.57 | 0 | 1 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_Q_TARONG#1_LREG | 1.5254 | 0 | 0.083333 | 0 | Out= NIL, Tarong 1 LREG Requirement <= 0MW | Outage | FCAS
F_V_APD01_L5 | 1.5 | 184.61 | 0.58333 | 60 | Out= NIL, APD Potline 1 L5 Requirement <= 0MW | Outage | FCAS
F_MAIN++NIL_BL_L60 | 1.47 | 1430.0977 | 2.3333 | 1749.1667 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL | FCAS
F_T++FARE_N-2_TG_R60 | 1.4 | 56.2412 | 0.083333 | 1.25 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage | FCAS
S>VMLMHNW1 | 1.3222 | 0 | 0.083333 | 0 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage | SA
V^SML_NIL_3 | 1.2793 | 0 | 0.083333 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL | Vic
V>SMLARHO4 | 1.1278 | 0 | 0.083333 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage | Vic
F_V_APD01_L60 | 1.1 | 36.6015 | 0.66667 | 53.0833 | Out= NIL, APD Potline 1 L60 Requirement <= 0MW | Outage | FCAS
F_V+NIL_APD01_L6 | 1.07 | 1.98 | 3.5 | 3.25 | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_QNV+MLTR_L5 | 1 | 0 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink unable to transfer FCAS | Outage | FCAS
T>T_FASH_3_N-2 | 0.97176 | 5262.7737 | 0.16667 | 5.6667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, West Coast 220/110 kV parallel closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Tas
N^^Q_ARTW_B1 | 0.79199 | 0 | 0.083333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage | NSW
F_QNV+MLTR_L60 | 0.74 | 0 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T++GTTE_TL_L6 | 0.74 | 0 | 2.0833 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_MAIN++WIPN-2_MLL60 | 0.7 | 0 | 0.75 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
F_Q++BCDM_R6 | 0.69868 | 0 | 0.083333 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Raise 6 sec Requirement | Outage | FCAS
F_STHN+APD_TL_L5 | 0.59 | 0 | 0.66667 | 0 | Lower 5 min requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
S>>NIL_RBTU_WEWT | 0.58379 | 0 | 0.33333 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL | SA
F_STHN+APD_TL_L60 | 0.55 | 0 | 0.66667 | 0 | Lower 60 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
F_MAIN++ML_L60_0400 | 0.53 | 71.1855 | 1.8333 | 281.6667 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL | FCAS
F_T++BLSPS_EXP_L60_1 | 0.5 | 0 | 0.83333 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
F_MAIN+ML_L5_APD | 0.45 | 11.16 | 0.083333 | 0.33333 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
N>N-BAMB_132_OPEN_A | 0.44932 | 155.1191 | 0.083333 | 0.58333 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage | NSW
F_MAIN+WIP_N-2_ML_L5 | 0.44 | 0 | 0.083333 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 5 Min requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T+GTTE_TL_L5 | 0.34 | 0 | 0.16667 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink unable to transfer FCAS | Outage | FCAS
F_T++GTTE_TL_L60 | 0.30247 | 0 | 1.25 | 0 | Out = one George Town to Temco 110 kV line, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
F_STHN+APD_TL_L6 | 0.21 | 0 | 0.58333 | 0 | Lower 6 sec requirement for a Southern Network Event, TL = loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line | Outage | FCAS
F_MAIN+WIP_N-2_MLL60 | 0.19 | 0 | 0.083333 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T++BLSPS_EXP_L6_1 | 0.18 | 0 | 0.75 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
V::N_SM330_2B_V22 | 0.16831 | 0 | 0.083333 | 0 | Out = South Morang No.2 330kV bus, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage | Vic
T>T_PMSH_IMP_4A | 0.15496 | 0 | 0.16667 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
F_MAIN+ML_L60_APD | 0.12 | 0.65 | 0.16667 | 0.33333 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_STHN+ML_L60_0300 | 0.12 | 0 | 0.33333 | 0 | Lower 60 sec requirement for a Southern Load Event, ML = 300 | Outage | FCAS
F_V_APD01_L6 | 0.1 | 16.6298 | 0.5 | 50.1667 | Out= NIL, APD Potline 1 L6 Requirement <= 0MW | Outage | FCAS
F_STHN+ML_L6_0300 | 0.09 | 0 | 0.25 | 0 | Lower 6 sec requirement for a Southern Load Event, ML = 300 | Outage | FCAS
S_BRBG_CMWF_0 | 0.07066 | 23279.5391 | 3.9167 | 1.6667 | Out = Brinkworth to Redhill to Bungama 132kV lines, Clements Gap WF unavailable due to line outage. | Outage | SA
F_QNV+MLTR_L6 | 0.06 | 0 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 6 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T++GTTE_TL_L5 | 0.06 | 0 | 0.083333 | 0 | Out = one George Town to Temco 110 kV line, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage | FCAS
S>>BRBG_BGTX_HUWT | 0.03387 | 0 | 2.1667 | 0 | Out= Brinkworth to Redhill to Bungama 132kV lines (this takes out Clements Gap WF), avoid O/L Hummocks to Waterloo 132kV on trip of Bungama 132/275kV TX2, Feedback | Outage | SA
F_ESTN+ML_L60_0400 | 0.03 | 0 | 0.083333 | 0 | Lower 60 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS
F_ESTN+ML_L6_0400 | 0.03 | 0 | 0.083333 | 0 | Lower 6 sec requirement for a Eastern Load Event, ML = 400 | Outage | FCAS
F_QNV++HYTR_L5 | 0.02 | 0 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
S>>BWMP_TWPA_TPRS | 0.01612 | 0 | 0.16667 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage | SA
S>WIMK_BWPA_HUWT | 0.00173 | 0 | 0.083333 | 0 | Out= Willalow-Mokota 275kV line, avoid O/L Hummocks-Waterloo 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage | SA

## Summary By Region
Binding Hours
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Ad-Hoc | 0.16667 |  |  |  |  | 0
Constraint Automation | 13.3333 | 12.25 | 5.5 | 24.9167 | 4.75 | 1.3333
FCAS
NSW | 5095.5833 | 3586.0833 | 3112.1667 | 2768.5 | 4260.0833 | 3057.8333
Negative Residue | 38 | 12.25 | 13.0833 | 46.8333 | 25.75 | 10.4167
Non-Conformance | 479.6667 | 358.5 | 228.6667 | 156.6667 | 97.3333 | 61.0833
Other | 11.5 | 35.5833 | 142.6667 | 50.5833 | 311.8333 | 115.25
Outage Ramping | 197.5 | 162.5833 | 236.8333 | 251.8333 | 142.25 | 174.4167
Qld | 1265.1667 | 2850.25 | 913.75 | 1756.6667 | 996.6667 | 511.3333
Quick | 1149.8333 | 132.3333 | 281.5 | 1018.4167 | 3070.3333 | 20807.75
SA | 2568.1667 | 2144.9167 | 3383.5833 | 3995.1667 | 2013.25 | 3285.75
Tas | 3387.9167 | 1247.1667 | 354.5833 | 895.9167 | 923.1667 | 1027.6667
Vic | 2605.25 | 3277.5833 | 5660.4167 | 6854 | 2618 | 1914.5
Binding Impact
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Ad-Hoc | 0 | 0 | 0 | 0 | 0 | 0
Constraint Automation | 118018.5319 | 72630.7349 | 61543.4159 | 64122.5584 | 6287.0142 | 4494.9703
FCAS | 2025902.8396 | 2312077.1775 | 11967737.2201 | 27702893.4048 | 24018595.0767 | 11563905.7935
NSW | 2061311.3279 | 2666446.6314 | 3008201.0876 | 2981579.7124 | 3811263.7887 | 4130424.9984
Negative Residue | 346084.2837 | 193679.0393 | 133618.843 | 159141.1919 | 65879.5695 | 190929.9383
Other | 162.4387 | 1327.1417 | 5944.8762 | 35445.6298 | 19441.5552 | 11515.5764
Qld | 8241677.7744 | 3351642.8339 | 17832407.3191 | 3412397.6405 | 1557960.0849 | 1092572.6105
SA | 4307596.7546 | 7308788.4534 | 7975370.452 | 19175976.6502 | 19603528.2545 | 49743082.8304
Tas | 15879751.959 | 7917341.1843 | 2498349.5552 | 3312667.8479 | 4771966.3751 | 2671514.9731
Vic | 4550348.9087 | 6717447.0811 | 3149671.2278 | 6498415.4069 | 3681628.8597 | 3495766.3104
Total | 37530854.8184 | 30541380.2775 | 46632843.9969 | 63342640.0428 | 57536550.5786 | 72904208.0013
Note on A5: FCAS excluded as it will swamp the graph

## NIL vs Outage
Binding Hours
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Commissioning | 1849.75 | 36.3333 | 166.5 | 71.1667 | 453 | 12116
FCAS - NIL | 67438.5 | 71339 | 78805.6667 | 98153.9167 | 83335.5 | 89035.8333
FCAS - Outage | 6939.25 | 5271.75 | 2785.8333 | 6213.6667 | 5623.9167 | 6087.5833
System Normal | 7521.0833 | 8116.3333 | 7848.6667 | 9089.5 | 6047.6667 | 4947.25
Network Support | 339.6667 | 155.8333 | 204.5 | 128.3333 | 55.6667 | 210.3333
Negative Residues | 38 | 12.25 | 13.0833 | 46.8333 | 25.75 | 10.4167
Outage | 6841.0833 | 5240.1667 | 5748.1667 | 7284.5833 | 5121.75 | 4817.0833
Total (non-FCAS) | 16589.5833 | 13560.9167 | 13980.9167 | 16620.4167 | 11703.8333 | 22101.0833
Binding Impact
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Commissioning | 11072953.0178 | 23582.5681 | 1122946.4259 | 123874.3701 | 695791.4608 | 48442546.0203
FCAS - NIL | 1330596.4579 | 1920731.4196 | 1523297.0635 | 4284769.1816 | 9691374.8176 | 8309289.3932
FCAS - Outage | 695306.3817 | 391353.9579 | 10444462.1066 | 23418124.2233 | 14327220.2591 | 3254616.4004
System Normal | 17466013.2732 | 20601341.3495 | 7628472.3458 | 13101240.0894 | 16979263.4586 | 20382744.3293
Network Support | 5680587.956 | 4678541.5594 | 22261395.2873 | 8878912.2779 | 965379.2057 | 30414067.7368
Negative Residues | 346084.2837 | 193679.0393 | 134581.6187 | 159141.1919 | 65879.5695 | 190929.9383
Outage | 2940926.3226 | 2769291.9038 | 4643343.5874 | 13500453.0789 | 15507433.2681 | 10352560.2034
Total | 39532467.6929 | 30578521.7976 | 47758498.4352 | 63466514.413 | 58232342.0394 | 121346754.0216

## Interconnector Binding
Interconnector Direction | Constraint Equation ID | 2018 Hours | 2017 Hours | Description | Type
N-Q-MNSP1 Export | N^N-LS_SVC | 461.0833 | 0 | Out= Lismore SVC O/S or in reactive power control mode, avoid Voltage collapse on Armidale to Coffs Harbour (87) trip; TG formulation only | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 109.25 | 308.25 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_I_E | 79.3333 | 31.6667 | N-Q-MNSP1.ENERGY * -1 = 65 (Wt = 0.0005) | Other
N-Q-MNSP1 Export | NQTE_ROC | 72.8333 | 18.4167 | Out=Nil, Rate of Change (NSW to Qld) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Export | NQTE_BLOCK_ECS | 64.1667 | 0 | Minimum of 29MW on Directlink QLD to NSW to ensure that Directlink ECS will not operate when Directlink support is required | Outage
N-Q-MNSP1 Export | N_X_MBTE_3A | 57.1667 | 34.75 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Export | N_X_MBTE2_A | 44.5833 | 45.4167 | Out= two Directlink cables, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 38.6667 | 77.5 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 34.1667 | 0.16667 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 19.3333 | 229.6667 | Out= Koolkhan to Lismore (967), avoid voltage collapse on trip of Coffs Harbour to Lismore (89), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N^N-89_LSTX_SVC | 10.5833 | 0 | Out= Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode, avoid Voltage collapse on Koolkhan to Lismore (967) trip; TG formulation only | Outage
N-Q-MNSP1 Export | N>LSDU_LSDU | 9.1667 | 18.0833 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_E_E | 6.0833 | 0 | N-Q-MNSP1.ENERGY * 1 = -40 (Wt = 0.0001) | Other
N-Q-MNSP1 Export | QNTE_OSCILLATE | 4.8333 | 7.3333 | Qld to NSW on Terranora Interconnector minimum transfer >= Terranora load plus 29 MW threshold. | Outage
N-Q-MNSP1 Export | N^^Q_NIL_A | 4.25 | 10.5 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
N-Q-MNSP1 Export | N>LSDU9U6_LSDU9U7 | 3.5833 | 0 | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | N>N-NIL_LSDU | 3.5 | 3.5 | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) on trip of the other Lismore to Dunoon line (9U7 or 9U6), Feedback | NIL
N-Q-MNSP1 Export | N^N_CHLS_1 | 3.1667 | 0 | Out= Coffs Harbour to Lismore (89), avoid voltage collapse on trip of Koolkhan to Lismore (967), swamp out when all 3 Directlink O/S | Outage
N-Q-MNSP1 Export | N>>N-NIL__3_OPENED | 2.6667 | 1.75 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
N-Q-MNSP1 Export | N>N-ARKK_CH_CB892A | 2.5 | 0 | Out= Armidale to Koolkhan (966) and Coffs Harbour CB 892 opened, avoid O/L Armidale to Coffs Harbour (96C)132kV line, on trip of Armidale to Coffs Harbour (87) 330kV line, Swamp out when all 3 directlink cable O/S, Feedback. TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B4 | 1.5833 | 2.25 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage
N-Q-MNSP1 Export | N>>N-964__3_OPENED | 1.5 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | Outage
N-Q-MNSP1 Export | N^^Q_TW_330_BUS3_B1 | 1.3333 | 1 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
N-Q-MNSP1 Export | NQTE_-070 | 1.25 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 1 | 0.083333 | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N>N_LSDU_9U6_1 | 0.91667 | 0 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L the remaining 132kV line, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N^^Q_ARDM_B1 | 0.83333 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | #R017115_001_RAMP_F | 0.75 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | NQTE_-010 | 0.75 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -10 MW | Outage
N-Q-MNSP1 Export | #R016707_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016739_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017248_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017685_001_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016891_001_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016891_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | N>Q-MUTW_2 | 0.41667 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage
N-Q-MNSP1 Export | #R017023_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017072_003_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N^N_CHLS_1, Effective Date: 29/09/2015, Version: 1 | Other
N-Q-MNSP1 Export | #R017115_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017782_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | Q>CLWU_BCCP | 0.33333 | 0 | Constraint Automation, O/L 275KV_812 @H10_BCMB for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_RAMP_I_F | 0.25 | 0 | N-Q-MNSP1 <= MAX(-25, InitialFlow - 80) (Wt=35) | Other
N-Q-MNSP1 Export | #R016780_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016939_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017293_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | F_Q++ARTW_R6 | 0.25 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-BAMB_132_OPEN_A | 0.25 | 0.33333 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path, avoid Lismore132 to Dunoon 132kV line (9U6 or 9U7) O/L on trip of the other 9U7 or 9U6 line, Swamp out when all 3 directlink cable O/S, feedback | Outage
N-Q-MNSP1 Export | N^^Q_MUTW_1_B1 | 0.25 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage
N-Q-MNSP1 Export | #R017819_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | N>>Q_LDMU_B | 0.16667 | 5.5833 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage
N-Q-MNSP1 Export | N>N-KKLS_TE_2 | 0.16667 | 0.16667 | Out= Koolkhan to Lismore (967), avoid O/L Glen Innes to Tenterfield (96R) on trip of Coffs Harbour to Lismore (89), swamp out when all 3 directlink O/S, Feedback, TG formulation on PD & ST | Outage
N-Q-MNSP1 Export | N>N-LSTN_TE_C1 | 0.16667 | 0 | Out= Lismore to Tenterfield (96L), avoid O/L Koolkhan to Lismore (967), on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | #R016657_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R016894_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017081_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^N_CHLS_1, Effective Date: 29/09/2015, Version: 1 | Other
N-Q-MNSP1 Export | #R017282_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 04/12/2017, Version: 1 | Other
N-Q-MNSP1 Export | #R017290_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B2, Effective Date: 26/06/2014, Version: 1 | Other
N-Q-MNSP1 Export | #R017741_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017789_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017809_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | #R017964_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Export | N::Q_MUTW_1 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
N-Q-MNSP1 Export | NQTE_-080 | 0.083333 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -80 MW | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_B1 | 0.083333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 256.0833 | 1157.9167 | Out= two Directlink cables, Qld to NSW limit | Outage
N-Q-MNSP1 Import | N_X_MBTE_3B | 196.25 | 189.25 | Out= all three Directlink cables, Terranora_I/C_import <= Terranora_Load | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 130.3333 | 206 | Out= one Directlink cable, Qld to NSW limit | Outage
N-Q-MNSP1 Import | QNTE_ROC | 71.0833 | 15.8333 | Out=Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | F_Q++MUTW_L6 | 68.0833 | 24.4167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | F_Q++MUTW_L5 | 64.3333 | 9.9167 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | Q>N-MUTE_758 | 47.8333 | 68.9167 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 47.5 | 45.0833 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N>N-NIL_DC | 46.4167 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 27.8333 | 18.3333 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | F_Q++LDMU_L6 | 13.25 | 1.1667 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
N-Q-MNSP1 Import | N_NIL_TE_B | 12.5 | 23.4167 | Out=Nil, Terranora Interconnector Qld to NSW flow overall limits | NIL
N-Q-MNSP1 Import | F_Q++LDMU_L5 | 10.3333 | 0.58333 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
N-Q-MNSP1 Import | Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 4.5 | 9.1667 | Out= Nil, ECS for managing 757 H4 Mudgeeraba to T174 Terranora 110kV line, Summer and Winter ECS ratings selected by SCADA status. | NIL
N-Q-MNSP1 Import | I_CTRL_ISSUE_TE | 4 | 3.1667 | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_I_F | 1.75 | 1.75 | N-Q-MNSP1 <= MAX(-25, InitialFlow - 80) (Wt=35) | Other
N-Q-MNSP1 Import | Q_CS_1950 | 1.0833 | 0 | Qld Central to Qld South upper transfer limit of 1950MW (discretionary) | Outage
N-Q-MNSP1 Import | Q::NIL_CS | 1 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW), 2008/2009 implementation | NIL
N-Q-MNSP1 Import | #R018140_002_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017425_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017875_002_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016657_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016707_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016739_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016780_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016798_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016851_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016894_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017248_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017386_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q^^TR_CLHA_-350, Effective Date: 03/05/2018, Version: 1 | Other
N-Q-MNSP1 Import | #R017425_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017741_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017793_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017798_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017802_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017819_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017875_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017902_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R018140_002_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017023_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017685_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017782_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017789_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017802_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017809_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017908_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017964_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016798_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016851_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017714_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017789_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017798_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | Q>N-MUTE_757 | 0.25 | 30.3333 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line, avoid O/L on remaining Terranora to Mudgeeraba line on trip of Condong generator. | Outage
N-Q-MNSP1 Import | #R016739_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016894_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017248_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017321_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint Q>N-MUTE_758, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R017809_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017819_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017908_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016657_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016707_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R016780_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017023_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017321_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint Q>N-MUTE_758, Effective Date: 15/06/2017, Version: 1 | Other
N-Q-MNSP1 Import | #R017685_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017714_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE2_B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | #R017793_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 25/11/2013, Version: 1 | Other
N-Q-MNSP1 Import | QNTE_150 | 0.083333 | 19.4167 | Qld to NSW on Terranora Interconnector upper transfer limit of 150 MW | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 82 | 148.0833 | Out= Nil, avoid Voltage Collapse on loss of Kogan Creek | NIL
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 69.8333 | 0.83333 | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N>>N-NIL__3_OPENED | 15.75 | 21.1667 | Out= Nil, avoid O/L Liddell to Muswellbrook (83) using 15 mins rating on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_NIL_A | 7 | 11.25 | Out= Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) line | NIL
NSW1-QLD1 Export | Q>>GGWU_GGCP2_GGCP1 | 4.9167 | 0 | Out= Gin Gin to Wurdong (819), avoid O/L Gin Gin to Calliope River (813) on trip of Gin Gin to Calliope River (814) line, Feedback | Outage
NSW1-QLD1 Export | N>>N-964__3_OPENED | 3.8333 | 0 | Out= Taree to Port Macquarie (964) 132kV line, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_LS_VC_B4 | 2.9167 | 3.5833 | Out= Lismore SVC, avoid Voltage Collapse on loss of Tarong North | Outage
NSW1-QLD1 Export | Q>>BCCP_CLWU_LCCP_2 | 2.25 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Larcom Creek to Calliope River (8859) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | Q>>LCCP_CLWU_BCCP_2 | 1.8333 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | N^^Q_ARDM_B1 | 1.75 | 0 | Out= one Armidale - Dumaresq (8C or 8E) line, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N^^Q_TW_330_BUS3_B1 | 1.3333 | 1 | Out= Tamworth No.3 330kV bus, NSW to Qld voltage stability limit for trip of Kogan Creek generator | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_E_F | 0.41667 | 0.33333 | NSW1-QLD1 <= MAX(73, InitialFlow - 200) (Wt=35) | Other
NSW1-QLD1 Export | N>Q-MUTW_2 | 0.41667 | 0 | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of largest QLD unit; Fb | Outage
NSW1-QLD1 Export | NQ_ZERO | 0.41667 | 0 | NSW to Qld on QNI upper transfer limit of zero MW | Outage
NSW1-QLD1 Export | Q>>LCCP_BCCP_CLWU_2 | 0.41667 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Calvale to Wurdong (871) on trip of Bouldercombe to Calliope River (812) line, Feedback | Outage
NSW1-QLD1 Export | #R017656_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q>>LCCP_CLWU_BCCP_2, Effective Date: 19/07/2018, Version: 1 | Other
NSW1-QLD1 Export | Q>CLWU_BCCP | 0.33333 | 0 | Constraint Automation, O/L 275KV_812 @H10_BCMB for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage
NSW1-QLD1 Export | #NSW1-QLD1_RAMP_I_F | 0.25 | 0 | NSW1-QLD1 >= MIN(-400, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Export | #R017293_005_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint N^^Q_MUTW_1_B1, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | #R017655_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q>>LCCP_CLWU_BCCP_2, Effective Date: 19/07/2018, Version: 1 | Other
NSW1-QLD1 Export | F_Q++ARTW_R6 | 0.25 | 0 | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_MUTW_1_B1 | 0.25 | 0 | Out = Muswellbrook to Tamworth (88), avoid Voltage collapse on loss of Kogan Creek generator | Outage
NSW1-QLD1 Export | Q>>PWSP_WOSP_PWCE | 0.25 | 0 | Out= Palmwoods to South Pine (808) line, avoid O/L Palmwood to Caboolture (746/4) 110kV line on trip of Woolooga to South Pine (807) 275kV line, Feedback | Outage
NSW1-QLD1 Export | #R016885_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>>CPGG1_CPGG2_WUGG, Effective Date: 05/04/2017, Version: 1 | Other
NSW1-QLD1 Export | #R017656_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint Q>>LCCP_CLWU_BCCP_2, Effective Date: 19/07/2018, Version: 1 | Other
NSW1-QLD1 Export | N>>Q_LDMU_B | 0.16667 | 13.1667 | Out= Liddell-Muswellbrook(83), avoid Liddell->Tamworth(84) OL on largest QLD generator trip ; FBk | Outage
NSW1-QLD1 Export | Q>>BCCP_CLWU_BCRG_2 | 0.16667 | 0 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, avoid O/L Bouldercombe to Raglan (811) on trip of Calvale to Wurdong (871) line, Feedback | Outage
NSW1-QLD1 Export | Q>>LCCP_CLWU_BCCP | 0.16667 | 0 | Out= Larcom Creek to Calliope River (8859), avoid O/L Bouldercombe to Calliope River (812) on trip of Calvale to Wurdong (871), Feedback | Outage
NSW1-QLD1 Export | #R016885_001_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q>>CPGG1_CPGG2_WUGG, Effective Date: 05/04/2017, Version: 1 | Other
NSW1-QLD1 Export | #R017282_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>Q-MUTW_2, Effective Date: 04/12/2017, Version: 1 | Other
NSW1-QLD1 Export | #R017290_007_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^Q_ARTW_B2, Effective Date: 26/06/2014, Version: 1 | Other
NSW1-QLD1 Export | N::Q_MUTW_1 | 0.083333 | 0 | Out = Muswellbrook to Tamworth (88), NSW to QLD Transient Stability limit on loss of largest Qld unit | Outage
NSW1-QLD1 Export | N^^Q_ARTW_B1 | 0.083333 | 0 | Out = Armidale to Tamworth (85 or 86), avoid Voltage Collapse on loss of Kogan Creek generators | Outage
NSW1-QLD1 Import | Q:N_NIL_AR_2L-G & Q::N_NIL_AR_2L-G | 142.25 | 516.3333 | Out=Nil, limit Qld to NSW on QNI to avoid transient instability for a 2L-G fault at Armidale | NIL
NSW1-QLD1 Import | N>N-NIL_DC | 78.4167 | 0 | Out= Nil, avoid O/L Armidale to Tamworth (85 or 86) on trip of the other Armidale to Tamworth line (85 or 86), Feedback | NIL
NSW1-QLD1 Import | F_Q++MUTW_L6 | 72.9167 | 27 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++MUTW_L5 | 67.25 | 11 | Out = Muswellbrook to Tamworth (88) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L6 | 52.5833 | 45.9167 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++BCDM_L6 | 46.25 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++BCDM_L5 | 36.6667 | 0 | Out = Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L5 | 31 | 16.8333 | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++8C_L6 | 17.75 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | Q:N_1078 | 17.4167 | 0 | QNI oscillatory stability limit of 1078 MW | Outage
NSW1-QLD1 Import | Q::N_ARSVC_AR_2L-G | 14.5833 | 0 | Out = Armidale SVC, limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | F_Q++LDMU_L6 | 13.5 | 3.3333 | Out = Liddell to Muswellbrook (83) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | F_Q++LDMU_L5 | 10.4167 | 1.4167 | Out = Liddell to Muswellbrook (83) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++8C_L5 | 9.25 | 0 | Out = Armidale to Dumaresq (8C), Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | F_Q++ARDM_L6 | 6.25 | 62 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 6 sec Requirement | Outage
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 4.1667 | 11.5 | NSW1-QLD1 >= MIN(-400, InitialFlow + 200) (Wt=35) | Other
NSW1-QLD1 Import | F_Q++ARDM_L5 | 1.9167 | 44.9167 | Out = Armidale to Dumaresq (8C) or Sapphire to Armidale (8E) line, Qld Lower 5 min Requirement | Outage
NSW1-QLD1 Import | Q::N_AR_CP2_AR_2L-G | 1.5 | 0 | Out = Armidale capacitor bank (120MVAr), limit Qld to NSW on QNI to avoid transient instability on 2L-G fault at Armidale | Outage
NSW1-QLD1 Import | I_QNI_ONE_PHASE_N-2 | 1.4167 | 0 | Out = Nil, Single Phase fault on both 8L and 8M circuits declared a credible contingency - No risk of QLD separation, QLD to NSW on QNI upper transfer limit of 850 MW, dynamic headroom | Outage
NSW1-QLD1 Import | QN_ZERO | 1 | 0 | Qld to NSW on QNI upper transfer limit of 0 MW | Outage
NSW1-QLD1 Import | Q_CS_1950 | 1 | 0 | Qld Central to Qld South upper transfer limit of 1950MW (discretionary) | Outage
NSW1-QLD1 Import | Q::NIL_CS | 0.91667 | 0 | Out = Nil, CQ-SQ transient stability limit (upper limit of 2100MW), 2008/2009 implementation | NIL
NSW1-QLD1 Import | #R017386_002_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint Q^^TR_CLHA_-350, Effective Date: 03/05/2018, Version: 1 | Other
NSW1-QLD1 Import | #R017244_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | #R017577_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R017592_001_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint Q::N_AR_CP2_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | #R017244_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint Q:N_1078, Effective Date: 24/07/2013, Version: 1 | Other
NSW1-QLD1 Import | F_Q++NIL_R5 | 0.25 | 0.16667 | Out=Nil, limit Qld to NSW on QNI and Qld Raise 5 min requirement for loss of a NSW 750 MW unit | NIL
NSW1-QLD1 Import | #R017264_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint Q::N_LDMU_AR_2L-G, Effective Date: 16/01/2018, Version: 1 | Other
NSW1-QLD1 Import | Q:N_NIL_OSC | 0.083333 | 19.4167 | Out= Nil, QNI oscillatory stability limit of 1200 MW, limit reduced to 950 MW when any one SEQ SVC POD is out, limit is reduced to 853 MW when all three SEQ SVCs or PODs out. | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 998.1667 | 625.9167 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 552 | 575 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 496.3333 | 470.3333 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L6 | 225.1667 | 22.1667 | Out = Nil, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 187.8333 | 287.5833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
T-V-MNSP1 Export | F_T++NIL_ML_L60 | 133.3333 | 45.6667 | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_T++LREG_0050 | 85.9167 | 10.8333 | Tasmania Lower Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T^V_NIL_9 | 54.0833 | 0.75 | Out = Nil, limit Basslink to 350 MW under conditions of sustained low fault levels at George Town 220 kV, to avoid uncoordinated switching of EHV capacitor banks around George Town resulting in insufficient reactive margin at George Town 220 kV. | NIL
T-V-MNSP1 Export | T^V_NIL_11 | 47.1667 | 18.6667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for trip of Basslink HF7 98 MVAr harmonic filter, swamped if TVCC in service | NIL
T-V-MNSP1 Export | V>>V_ROTS_TX_2A_R | 36.5 | 2.0833 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5_PP | 33 | 0 | Out = Nil, Raise 5 min requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5STt PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60_P | 30.5 | 0 | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST t PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T^V_NIL_8 | 30.4167 | 2.1667 | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, considering action of GTRSPS, swamped if TVCC in service | NIL
T-V-MNSP1 Export | T^V_HAPM_220_1 | 17.9167 | 0 | Out = Hadspen to Palmerston 220 kV line, prevent voltage collapse at George Town 220 kV bus for loss of parallel Hadspen to Palmerston 220 kV line | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_2B_R | 16.1667 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage
T-V-MNSP1 Export | F_T++NIL_ML_L5 | 12.5833 | 3.25 | Out = Nil, Lower 5 min requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6_PP | 10 | 0 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event (when Pelican Point GT11 +0.5ST PLUS the max Gen declared credible), Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_NIL_6A_R | 9.1667 | 0 | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL
T-V-MNSP1 Export | TVBL_ROC | 7.1667 | 12.4167 | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Export | T^^V_GTSH_1 | 7.1667 | 0.083333 | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of the remaining Sheffield to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | F_MAIN++NIL_RREG | 6.0833 | 10.4167 | Mainland Raise Regulation Requirement, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | T_V_NIL_BL1 | 4.3333 | 3.25 | Out=Nil, Basslink no go zone limits Tas to Vic | NIL
T-V-MNSP1 Export | T^^V_PMSH_1 | 3.75 | 0 | Out = Palmerston to Sheffield 220 kV line, prevent voltage collapse at Georgetown 220 kV bus for loss of either one Sheffield to Georgetown 220kV line or one Hadspen to Georgetown 220kV line. | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L5 | 2.9167 | 0 | Out = one Comalco to George Town line, Tasmania Lower 5 min requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 2.6667 | 2.75 | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 2.6667 | 4.4167 | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 2.25 | 0.083333 | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L60_2 | 1.5 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2 | Outage
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 1.3333 | 9 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L5 | 1.25 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_2 | 1.0833 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage
T-V-MNSP1 Export | T_V_FCSPS_RAMP | 0.91667 | 0 | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage
T-V-MNSP1 Export | F_NVS++MG_R6 | 0.83333 | 0 | Raise 6 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_3A_R | 0.75 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
T-V-MNSP1 Export | V>>V_MLTS_TX_2A_R | 0.66667 | 0 | Out = Moorabool A1 or A2 500/220kV transformer, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
T-V-MNSP1 Export | #R018136_051_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 22/03/2018, Version: 1 | Other
T-V-MNSP1 Export | F_T++GTTE_TL_L6 | 0.5 | 0 | Out = one George Town to Temco 110 kV line, Lower 6 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink | Outage
T-V-MNSP1 Export | #R018127_051_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 22/03/2018, Version: 1 | Other
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2B_R | 0.33333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
T-V-MNSP1 Export | #R018136_051_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 22/03/2018, Version: 1 | Other
T-V-MNSP1 Export | F_NVS++MG_R60 | 0.16667 | 0 | Raise 60 sec Service Requirement for NSW, Vic and SA Generation Event, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | V>>V_ROTS_TX_3B_R | 0.16667 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage
T-V-MNSP1 Export | #R017693_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 03/09/2018, Version: 1 | Other
T-V-MNSP1 Export | #R018127_051_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint T^^V_GTSH_1, Effective Date: 22/03/2018, Version: 1 | Other
T-V-MNSP1 Export | F_T++BLSPS_EXP_L60_1 | 0.083333 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_1 | 0.083333 | 0 | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage
T-V-MNSP1 Import | F_MAIN++APD_TL_L5 | 758.9167 | 638.5833 | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APD_TL_L60 | 292.75 | 262.0833 | Out = Nil, Lower 60 sec Service Requirement for a Mainland Network Event-loss of APD potlines due to undervoltage following a fault on MOPS-HYTS-APD 500 kV line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V::N_NILxxx | 216.0833 | 279.3333 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 111.5 | 276.6667 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V_T_NIL_FCSPS | 98.1667 | 171.0833 | Basslink limit from Vic to Tas for load enabled for FCSPS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R60 | 64.1667 | 90.0833 | Out = Nil, Raise 60 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 55.4167 | 86.1667 | Tasmania Raise Regulation Requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0120 | 49.4167 | 131.8333 | Mainland Lower Regulation Requirement greater than 120 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R6 | 45.6667 | 72.0833 | Out = Nil, Raise 6 sec requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_SETB_V2 | 36 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 32.5 | 46.0833 | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 20.6667 | 37.0833 | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V_T_NIL_BL1 | 19.9167 | 118.1667 | Out=Nil, Basslink no go zone limits Vic to Tas | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 19.6667 | 20.75 | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 18.25 | 12.8333 | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | T_ROCOF_1 | 17.6667 | 33.4167 | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL
T-V-MNSP1 Import | F_T++NIL_MG_RECL_R5 | 17.4167 | 23.25 | Out = Nil, Raise 5 min requirement for a Tasmania Reclassified Woolnorth Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_SETB_S2 | 15.8333 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_SETB_V1 | 14.8333 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 14.75 | 1.5833 | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | T::T_NIL_4 | 11.5 | 12.1667 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | F_MAIN++LREG_0150 | 10.3333 | 0 | Mainland Lower Regulation Requirement greater than 150 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | V::N_WBHO_V2 | 10.1667 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | T>>T_PMSH_EXP_3C | 9.3333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | T::T_HA_GT_PM_4 | 9.1667 | 2.3333 | Out = Hadspen to George Town or Hadspen to Palmerston 220 kV line, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT out of service. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 8.75 | 13.8333 | Out = Nil, Raise 6 sec requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_WBHO_S2 | 6.3333 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | VTBL_ROC | 5.8333 | 12.5833 | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | NIL
T-V-MNSP1 Import | V::N_HYSE_V2 | 5.5 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 4.75 | 4.5833 | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | NIL
T-V-MNSP1 Import | V::N_HORC_V2 | 4.75 | 0.58333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_HWSM_V1 | 4.75 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_EPMB_S2 | 3.4167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R5 | 3.25 | 0 | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage
T-V-MNSP1 Import | V::N_EPMB_V2 | 2.9167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_JNWO_S2 | 2.9167 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | T>>T_PMSH_EXP_3B | 2.8333 | 0 | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | V::N_HWSM_V2 | 2.25 | 4.5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | T::T_NIL_3 | 2 | 8.75 | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT in service. Swamped if Tamar CCGT OOS. | NIL
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 1.5833 | 1.75 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R60 | 1.0833 | 0 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 1.0833 | 0.16667 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_DDSM_V2 | 1 | 3 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V:T_NIL_BL_1 | 1 | 0 | Outage = Nil, Basslink in service, limit Basslink flow to Tasmania at low Tas fault levels to avoid inverter commutation instability | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 0.83333 | 265.75 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_APD | 0.83333 | 6.5 | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | V:T_HAPM_BL_1 | 0.75 | 0 | Out = Hadspen to Palmerston 220 kV line, limit Basslink flow VIC to TAS at low TAS fault levels to avoid inverter commutation instability following trip of remaining Hadspen to Palmerston 220 kV line, Tamar CCGT out of service | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 0.66667 | 2 | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | V::N_WBHO_V1 | 0.66667 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_JNWG_xxx | 0.58333 | 0 | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | #R017533_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++WIP_N-2_MLL5 | 0.5 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 5 Min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | #R017148_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017496_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017525_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017533_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017883_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
T-V-MNSP1 Import | F_T++CSGO_TG_R5 | 0.41667 | 0 | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS, reduce by very fast response on Basslink, include fault-ride through on windfarms+Basslink | Outage
T-V-MNSP1 Import | #R017278_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017358_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017449_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017481_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017485_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017520_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017525_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017597_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017818_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
T-V-MNSP1 Import | #T-V-MNSP1_RAMP_E_F | 0.33333 | 0.33333 | T-V-MNSP1 <= MAX(0, InitialFlow - 200) (Wt=35) | Other
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 0.33333 | 97.5833 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_5F | 0.33333 | 0 | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_SM330_2B_V22 | 0.33333 | 0 | Out = South Morang No.2 330kV bus, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R017128_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 05/04/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017148_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017152_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017451_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017485_004_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017497_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017512_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017597_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++WIP_N-2_MLL6 | 0.25 | 0 | Out= Nil, loss of both Wivenhoe pumps declared credible, Mainland Lower 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R6 | 0.25 | 0 | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS, Basslink fast response | Outage
T-V-MNSP1 Import | V::N_MLSY_V2 | 0.25 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R017366_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017451_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017497_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017506_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017512_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017512_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017638_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017677_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMTT_V2, Effective Date: 10/09/2018, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++ML_L60_APD | 0.16667 | 2.4167 | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 0.16667 | 23.4167 | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
T-V-MNSP1 Import | V::N_JNWO_V2 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_MLTX_V2 | 0.16667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | #R017278_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017284_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017449_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017499_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017501_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017506_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017506_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017543_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017840_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 10/09/2018, Version: 1 | Other
T-V-MNSP1 Import | #R017883_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 0.083333 | 328.5833 | Mainland Lower 60 second Requirement for loss of Basslink, Basslink flow into Tas | NIL
T-V-MNSP1 Import | F_QNV++HYTR_L5 | 0.083333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.083333 | 2.0833 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 0.083333 | 0.41667 | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS, reduce FCAS by very fast response on Basslink, include fault-ride through on windfarms and Basslink | Outage
T-V-MNSP1 Import | T>>T_HAPM_EXP_3A | 0.083333 | 0 | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | V::N_BURC_S2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
T-V-MNSP1 Import | V::N_BURC_V2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | VSML_ZERO | 488.3333 | 20.4167 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V::N_NILxxx | 216.25 | 560.25 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 169.9167 | 272.1667 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-S-MNSP1 Export | V^^N_NIL_1 | 71.9167 | 0 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
V-S-MNSP1 Export | V^SML_NSWRB_2 | 58.5 | 53 | Out = NSW Murraylink runback scheme, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | NIL
V-S-MNSP1 Export | V>SMLARHO1 | 49 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | VSML_ROC_80 | 43.0833 | 20.1667 | Out=Nil, Rate of Change (VIC to SA) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Export | S>>PATW_BWPA_TPRS | 35.3333 | 0 | Out= Para-Templers West 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_SETB_V2 | 31.25 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | VSML_220 | 25 | 22.1667 | Vic to SA on ML upper transfer limit of 220 MW | NIL
V-S-MNSP1 Export | S>>PARB_RBTU_WEWT | 22.3333 | 0.75 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo East-Waterloo 132kV on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N-NIL_HA | 19.5833 | 11.3333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
V-S-MNSP1 Export | V^SML_HORC_3 | 17 | 0.33333 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V::N_SETB_V1 | 13.75 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>V_NIL_8 | 12 | 0.5 | Out = Nil, avoid O/L DDTS to WOTS 330kV line for trip of LowerTumut-Wagga (051) + (991,990,99P) or (990,99M,970) ex_Yass lines - status switched ; Feedback | NIL
V-S-MNSP1 Export | V::N_SETB_S2 | 11.4167 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_WBHO_V2 | 10.5 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>X_RBPA+CB_03 | 8.6667 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line(this offloads Robertstown 275/132kV TX2), Feedback | Outage
V-S-MNSP1 Export | V>>V_DDSM_1 | 7 | 0.16667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
V-S-MNSP1 Export | V>>N-NIL_HG | 6.9167 | 0.5 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
V-S-MNSP1 Export | V::N_HYSE_V2 | 6.3333 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>PARB_RBTU_WTTP | 6 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Waterloo-Templers 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_WBHO_S2 | 6 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HORC_V2 | 5.6667 | 0.58333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V^SML_BUDP_3 | 5.5 | 0 | Out = Buronga to Balranald to Darlington Pt (X5) 220kV line, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V::N_HWSM_V1 | 5 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | VSML_VFRB_OFF | 4.25 | 0.083333 | Out=Nil, Vic to SA on Murraylink <=10 for Murraylink VFRB disabled, Dispatch only | NIL
V-S-MNSP1 Export | VSML_000 | 3.4167 | 0 | Vic to SA on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V::N_EPMB_S2 | 3.3333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | S>>RBTX2_RBTX1_WEWT | 3.1667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown #1 132/275kV TX, Feedback | Outage
V-S-MNSP1 Export | V::N_EPMB_V2 | 2.8333 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V::N_HWSM_V2 | 2.5833 | 18.5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SML_NSWRB_10 | 2.3333 | 2.3333 | Out = NSW Murraylink runback scheme, avoid O/L of Kerang to Wemen 220 kV line section for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL
V-S-MNSP1 Export | S>>X_MKRB+WERB_4 | 2 | 0 | Out= Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (Note: Line Only O/S), avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, | Outage
V-S-MNSP1 Export | V>>V-MSUT_1 | 1.9167 | 0 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage
V-S-MNSP1 Export | VSML_015 | 1.9167 | 0 | Vic to SA on ML upper transfer limit of 15 MW | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2A_R | 1.75 | 8 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_5 | 1.75 | 21.5 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | S>>X_MKRB+WERB_11 | 1.6667 | 0 | Out=Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (Note: Line Only O/S) avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line | Outage
V-S-MNSP1 Export | #V-S-MNSP1_I_E | 1.5 | 0 | V-S-MNSP1.ENERGY * -1 >= 40 (Wt = 35) | Other
V-S-MNSP1 Export | V^SML_KGRC_4 | 1.5 | 0 | Out = Kerang to Wemen or Red Cliffs to Wemen 220kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line, avoid voltage collapse for loss of Horsham to Ararat 220kV line | Outage
V-S-MNSP1 Export | V::N_DDSM_V2 | 1.3333 | 4.5833 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>DDSH_DDGN_N-2 | 1.0833 | 1.3333 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-S-MNSP1 Export | V>>V_MLTS_TX_2A_R | 0.75 | 0 | Out = Moorabool A1 or A2 500/220kV transformer, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
V-S-MNSP1 Export | V>>V_SMTT2_2 | 0.75 | 0 | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the Thomastown to South Morang No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | VSML_-040 | 0.75 | 0.33333 | Vic to SA on ML upper transfer limit of -40 MW | Outage
V-S-MNSP1 Export | V::N_WBHO_V1 | 0.66667 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | #R018020_011_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | I_CTRL_ISSUE_ML | 0.58333 | 0.33333 | DC Link Control Issue Constraint for Murraylink | Outage
V-S-MNSP1 Export | N>>N-X_WGYS_99M_992 | 0.58333 | 0 | Out = Out = Murrumburrah to Yass 132kV line (99M) and Burrinjuck to Tumut132 132kV line (992), avoid Lower Tumut to Wagga 330kV (051) O/L on Murray - Dederang 330kV (67 or 68) trip with DBUSS action | Outage
V-S-MNSP1 Export | #R017366_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017497_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>>V_MLTS_TX_2A_R, Effective Date: 27/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017533_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017930_012_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>SMLARHO1, Effective Date: 27/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017128_016_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 09/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017358_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017445_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017496_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017525_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017533_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017551_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017635_010_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>SMLARHO1, Effective Date: 03/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017883_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017925_026_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 01/06/2017, Version: 1 | Other
V-S-MNSP1 Export | VSML_020 | 0.41667 | 0 | Vic to SA on ML upper transfer limit of 20 MW | Outage
V-S-MNSP1 Export | #R016832_001_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_015, Effective Date: 08/01/2014, Version: 1 | Other
V-S-MNSP1 Export | #R017148_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017251_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017251_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017255_023_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 09/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017255_023_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 09/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017278_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017358_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017416_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017485_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017485_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017520_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017525_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017543_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017597_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017612_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017612_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017702_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017725_010_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017732_010_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017786_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017818_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017930_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>SMLARHO1, Effective Date: 27/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R018016_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018090_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R018111_011_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018135_002_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | S>>NIL_HUBG-T_WEWT2 | 0.33333 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Hummocks-Snowtown-Bungama 132kV T line (this trips Snowtown WF).[Note: Wattle PT trips when generating >=80 MW when Dalymple Battery (i.e. both Gen and Load component) is I/S] | NIL
V-S-MNSP1 Export | V::N_SM330_2B_V22 | 0.33333 | 0 | Out = South Morang No.2 330kV bus, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | #R016837_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VSML_015, Effective Date: 08/01/2014, Version: 1 | Other
V-S-MNSP1 Export | #R016837_001_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VSML_015, Effective Date: 08/01/2014, Version: 1 | Other
V-S-MNSP1 Export | #R016950_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017148_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017152_017_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>N_SM330_2B_3, Effective Date: 26/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017152_017_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>>N_SM330_2B_3, Effective Date: 26/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017416_010_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017449_004_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017451_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017481_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017497_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017512_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017597_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017732_010_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017775_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint S>>PATW_BWPA_TPRS, Effective Date: 12/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017818_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R018090_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R018111_011_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018135_002_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | V::N_MLSY_V2 | 0.25 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>SML_NSWRB_9 | 0.25 | 0 | Out = NSW Murraylink runback scheme, avoid O/L of Bendigo to Kerang 220 kV line for loss of Balranald to Darlington Point (X5/1) 220 kV line, feedback | NIL
V-S-MNSP1 Export | V^SML_HORC_2 | 0.25 | 0 | Out = Horsham to Red Cliffs 220kV line, avoid voltage collapse for loss of Darlington Pt to Buronga (X5) 220kV line | Outage
V-S-MNSP1 Export | #R016804_029_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_BUDP_3, Effective Date: 01/06/2017, Version: 1 | Other
V-S-MNSP1 Export | #R016832_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint VSML_015, Effective Date: 08/01/2014, Version: 1 | Other
V-S-MNSP1 Export | #R016950_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017128_016_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 09/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017152_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017278_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017344_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V>SMLARHO2, Effective Date: 28/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017366_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017497_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017506_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017512_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017512_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017638_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017658_010_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017702_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017725_010_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017775_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint S>>PATW_BWPA_TPRS, Effective Date: 12/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017786_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Export | #R017883_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017965_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017997_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #V-S-MNSP1_E_E | 0.16667 | 0 | V-S-MNSP1. * 1 <= 190 (Wt = 35) | Other
V-S-MNSP1 Export | S>>MKRB_BWPA_BRTW | 0.16667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Brinkworth-Templers West 275kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>NIL_RBTU_WEWT | 0.16667 | 0 | Out= Nil, avoid O/L Waterloo East-Waterloo 132kV line on trip of Robertstown-Tungkillo 275kV line, Feedback | NIL
V-S-MNSP1 Export | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-S-MNSP1 Export | V::N_MLTX_V2 | 0.16667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V>>BABE_DDGN_N-2 | 0.16667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
V-S-MNSP1 Export | V>>N_SM330_2B_3 | 0.16667 | 0 | Out = South Morang F2 500/330 kV and either H1 or H2 330/220 kV txfmr, SMTS 220kV bus tied, avoid O/L Ballarat to Bendigo 220kV line on trip of South Morang H2 or H1 220/330kV transformer, Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL1A_R | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Export | VSML_040 | 0.16667 | 0 | Vic to SA on ML upper transfer limit of 40 MW | Outage
V-S-MNSP1 Export | #R017148_017_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>N_SM330_2B_3, Effective Date: 26/04/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017278_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017284_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017368_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017371_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>SMLARHO1, Effective Date: 02/07/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017371_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>SMLARHO2, Effective Date: 28/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017449_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017449_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>SMLARHO2, Effective Date: 28/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017449_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>SMLARHO3, Effective Date: 28/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017449_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>SMLARHO3, Effective Date: 28/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017451_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017454_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017499_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017501_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017506_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017506_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017635_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>SMLARHO1, Effective Date: 03/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017658_009_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_2, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017677_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_SMTT_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017684_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R017840_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 10/09/2018, Version: 1 | Other
V-S-MNSP1 Export | #R017872_008_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_KGRC_4, Effective Date: 30/08/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018045_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018045_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018117_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018117_011_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^SML_HORC_3, Effective Date: 02/05/2017, Version: 1 | Other
V-S-MNSP1 Export | #R018129_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 21/11/2018, Version: 1 | Other
V-S-MNSP1 Export | NRM_VIC1_SA1 | 0.083333 | 2.0833 | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | S>>BRTW_BWPA_WTTP | 0.083333 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo-Templers 132kV on trip of Blyth West-Munno Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>BWMP_TWPA_TPRS | 0.083333 | 0 | Out= Blyth West- Munno Para 275kV line with Blyth West CB8002 OPEN, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | S>>PARB_TWPA_TPRS | 0.083333 | 0 | Out=Para-Robertstown 275kV line, avoid O/L Templers-Roseworthy 132kV line on trip of Templers West-Para 275kV line, Feedback | Outage
V-S-MNSP1 Export | V::N_BURC_S2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-S-MNSP1 Export | V:SS_820_HY_TEST_DYN | 0.083333 | 1.75 | VIC to SA on Heywood and Murraylink combined upper transfer limit of 820 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-S-MNSP1 Export | V>>N_SMHTX_1 | 0.083333 | 0 | Out = South Morang H 330/220 kV txfmr, only one SMTS H txfmr in service, avoid O/L the remaining in service SMTS H 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
V-S-MNSP1 Export | V>>V_DDTX_C | 0.083333 | 0 | Out = Dederang H1 or H2 330/220kV txfmr, avoid pre-contingent overload of the Dederang H3 330/220 kV txfmr, feedback | Outage
V-S-MNSP1 Export | V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage
V-S-MNSP1 Export | V>SMLARHO3 | 0.083333 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Kerang to Wemen 220 kV line section on loss of Balranald to Darlington Point (X5/1) line | Outage
V-S-MNSP1 Export | V>SMLARHO4 | 0.083333 | 0 | Out = Ararat to Crowlands or Crowlands to Horsham 220kV line, avoid O/L Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang 220kV line | Outage
V-S-MNSP1 Export | V^SML_NIL_3 | 0.083333 | 0 | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line | NIL
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 338.75 | 282.4167 | Out = Nil, avoid overloading Robertstown-North West Bend #1 or #2 132kV lines for no contingencies, feedback | NIL
V-S-MNSP1 Import | SVML_ZERO | 287.25 | 80.3333 | SA to Vic on ML upper transfer limit of 0 MW | Outage
V-S-MNSP1 Import | SVML_ROC_80 | 49.9167 | 21.6667 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | NIL
V-S-MNSP1 Import | S>RBTX2_RBTX1_WEMWP4 | 33.6667 | 0 | Out= Robertstown 275/132kV TX2, avoid O/L Waterloo East-MWP4-Roberstown 132kV line on trip of Robertstown 275/132kV TX1, Feedback | Outage
V-S-MNSP1 Import | S>NIL_NIL_NWMH2 | 14.6667 | 37 | Out= Nil, avoid O/L North West Bend-Monash #2 132kV on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>>MKRB_CNRB_WEMWP4 | 14.1667 | 0 | Out= Mokota-Robertstown 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on trip of Canowi-Robertstown 275kV line(this offloads Davenport-Canowie 275kV line and trips Hallet GTs and Hallet Windfarm), Feedback | Outage
V-S-MNSP1 Import | V>>V_NIL_1A | 8.8333 | 0.33333 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
V-S-MNSP1 Import | S:VS_650_HY_TEST_DYN | 5.5 | 6.9167 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-S-MNSP1 Import | NRM_SA1_VIC1 | 4.5 | 1.1667 | Negative Residue Management constraint for SA to VIC flow | NIL
V-S-MNSP1 Import | S:VS_650_HY_TEST | 3.9167 | 4.0833 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-S-MNSP1 Import | V>>V_NIL_1B | 1.5833 | 1.0833 | Out = Nil, avoid O/L Murray to Dederang No.2 330kV line (flow MSS to DDTS) for loss of the parallel No.1 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
V-S-MNSP1 Import | S>NWB6021_TX3 | 1.5 | 0 | Out= North West Bend 132kV CB6021, avoid O/L North West Bend 66/132kV #3 TX on trip of Robertstown-NWB #1 132kV line, Feedback | Outage
V-S-MNSP1 Import | S>>BRTW_NIL_WEMWP4 | 1 | 0 | Out= Brinkworth- Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>>MKRB_NIL_WEMWP4 | 1 | 0 | Out= Mokota-Robertstown 275kV line,, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S>>PATW_NIL_WEMWP4 | 0.91667 | 0 | Out= Para-Templers West 275kV line, avoid O/L Waterloo East-MWP4-Robertstown 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | #R017670_019_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint S>RBTX2_RBTX1_WEMWP4, Effective Date: 20/04/2018, Version: 1 | Other
V-S-MNSP1 Import | V>>V_ROTS_TX_3A_R | 0.83333 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-S-MNSP1 Import | V>>V_NIL_3 | 0.5 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL
V-S-MNSP1 Import | V>>V_ROTS_TX_3B_R | 0.5 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage
V-S-MNSP1 Import | #R016795_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R017217_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint S>VMLMHNW1, Effective Date: 02/04/2015, Version: 1 | Other
V-S-MNSP1 Import | #R017469_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R017583_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R017689_001_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | S>>BLMK_NIL_WEMWP4 | 0.41667 | 0.5 | Out= Belalie-Mokota 275kV line (This offloads Willalow substation and Willagoleche WF) OR Belalie-Willalow 275kV line, avoid O/L Waterloo East-Morgan Whyalla 4 132kV line on Nil trip, Feedback | NIL
V-S-MNSP1 Import | S:VS_PA_SVC_570 | 0.33333 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-S-MNSP1 Import | #R017689_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R016795_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R017583_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R018033_001_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | #R018033_001_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | F_S++ML_L6_1 | 0.16667 | 0 | Lower 6 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA, Segment 1 | Outage
V-S-MNSP1 Import | #R017251_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Other
V-S-MNSP1 Import | F_S++ML_L5 | 0.083333 | 0 | Lower 5 min Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
V-S-MNSP1 Import | F_S++ML_L60 | 0.083333 | 0 | Lower 60 sec Service Requirement for SA Load Event, where Murraylink (SA to Vic transfer) is the largest load risk in SA | Outage
V-S-MNSP1 Import | S>VMLMHNW1 | 0.083333 | 0 | Out = Monash to North West Bend # 1 132kV line, limit Murraylink (SA to Vic) to avoid overloading Monash-North West Bend # 2 132kV line | Outage
V-SA Export | V::N_NILxxx | 247.9167 | 453.4167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
V-SA Export | V::S_SETB_TBSE_2 | 156.6667 | 44.5833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V::S_SETB_MAXG_2 | 98.4167 | 0 | Out= one South East to Tailem Bend 275kV line; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). (NOTE: with both Black Range series capacitors O/S). | Outage
V-SA Export | V^^S_SETB_TBSE_2 | 32.5833 | 2.0833 | Out= one South East to Tailem Bend 275kV line (NOTE: with both Black Range series capacitors O/S or I/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | Outage
V-SA Export | V:S_600_HY_TEST_DYN | 31.25 | 97.5833 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | NIL
V-SA Export | V:S_600_HY_TEST | 27.0833 | 75.3333 | VIC to SA on Heywood upper transfer limit of 600 MW, limit for testing of Heywood interconnection upgrade. | NIL
V-SA Export | V::N_SETB_V2 | 20.25 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | VS_350 | 18.8333 | 0 | Victoria to SA on VicSA upper transfer limit of 350 MW | Outage
V-SA Export | V::S_BLKRG_MAXG_2 | 15.8333 | 0 | Out = both Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 13.9167 | 3.0833 | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | S_PPT+TIPSB_800 | 13.0833 | 0 | Heywood IC (VIC-SA) <= 800- (Pelican Pt GT11) -Max(TIPS B units, TIPS A units, Osbourne, QPS5, Snowthown North+South, Mintaro, Pelican) - South East generation + South East Load; NOTE: Pelican PT output restricted to 400MW | NIL
V-SA Export | V::N_WBHO_V2 | 10.6667 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_SETB_V1 | 9.75 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V^^S_NIL_MAXG_xxx | 9.4167 | 0.41667 | Out = Nil; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (South East Capacitor Available). | NIL
V-SA Export | V::N_SETB_S2 | 9.0833 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | VS_050 | 7.1667 | 57.5833 | Victoria to SA on VicSA upper transfer limit of 50 MW | Outage
V-SA Export | V::N_WBHO_S2 | 6.4167 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_HORC_V2 | 5.6667 | 0.58333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | VS_250 | 5.5 | 0 | Victoria to SA on Heywood upper transfer limit of 250 MW | Outage
V-SA Export | V::N_HWSM_V1 | 4.9167 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::N_HYSE_V2 | 4.3333 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_EPMB_S2 | 3.4167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | VS_300 | 3.4167 | 0 | Victoria to SA on VicSA upper transfer limit of 300 MW | Outage
V-SA Export | V::N_EPMB_V2 | 2.9167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_JNWO_S2 | 2.9167 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | VS_400 | 2.9167 | 0 | Victoria to SA on VicSA upper transfer limit of 400 MW | Outage
V-SA Export | V::N_HWSM_V2 | 2.5833 | 18.5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V^^S_TBTX+CB_SETB | 2.1667 | 0 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage
V-SA Export | V::S_HYSE_MAXG_2 | 1.75 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S); Vic to SA Transient Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | V^^S_MLSY_2 | 1.6667 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, avoid excessive change in network voltages on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Export | V^^S_TBTX+CB_SETB_2 | 1.3333 | 0 | Out= Tailembend 275/132kV #4 TX +associated transformer CBs O/S (Note: with both Black Range series caps O/S); Vic to SA Long Term Voltage Stability limit for loss of South East - Tailem Bend 275kV line. | Outage
V-SA Export | V::S_NIL_SETB_SECP_1 | 1.25 | 0.41667 | Out = Nil(Note: with both Black Range series capacitors I/S); Vic to SA transient stability limit (South East Capacitor OOS or not available for switching) for loss of one South East- Tailembend 275kV line. | NIL
V-SA Export | F_ESTN++HYTR_L60 | 1.1667 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V^^S_SEVC1_SETB | 1.1667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line. | Outage
V-SA Export | V>>DDSH_DDGN_N-2 | 1.0833 | 1.3333 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
V-SA Export | #R017370_004_RAMP_V | 0.66667 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | V::N_WBHO_V1 | 0.66667 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Export | V::S_SEVC1_MAXG | 0.66667 | 0 | Out= South East one SVC (Note: with both Black Range series caps I/S); Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | VS_250_DYN | 0.66667 | 10.25 | Victoria to SA on Heywood upper transfer limit of 250 MW. Limit is dynamically reduced when actual flow exceeds limit by at least 10 MW. Limit is reduced by amount of exceedance, capped at 25 MW | Outage
V-SA Export | F_ESTN++HYTR_L5 | 0.58333 | 0 | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V::N_JNWG_xxx | 0.58333 | 0 | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | #R017533_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-SA Export | V^^S_KNPW_MAXG | 0.5 | 0 | Out= Kincraig - Penola West 132 kV line (Note: with both Black Range series caps I/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R017148_012_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
V-SA Export | #R017358_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017496_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017525_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-SA Export | #R017533_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-SA Export | #R017883_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-SA Export | V::S_BLKRG_TBSE_2 | 0.41667 | 0.5 | Out = both or one Black Range series capacitors O/S; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines. | Outage
V-SA Export | V>>S_MOTB_TBCG_TBTU | 0.41667 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailembend - Tungkillo 275kV on trip of Tailembend - Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | #R016738_012_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Other
V-SA Export | #R017358_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017370_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R017449_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017481_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017485_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017485_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017520_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017525_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-SA Export | #R017597_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
V-SA Export | #R017818_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-SA Export | #R017954_013_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R017954_013_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | V::N_SM330_2B_V22 | 0.33333 | 0 | Out = South Morang No.2 330kV bus, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | #R017148_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
V-SA Export | #R017152_012_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
V-SA Export | #R017278_008_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
V-SA Export | #R017364_001_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::S_HYSE_MAXG_2, Effective Date: 03/04/2017, Version: 1 | Other
V-SA Export | #R017451_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017512_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017597_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
V-SA Export | #R017818_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-SA Export | NRM_VIC1_SA1 | 0.25 | 4.75 | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | V::N_MLSY_V2 | 0.25 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V_S_NIL_ROCOF | 0.25 | 133.3333 | Out = NIL, limit VIC to SA Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Export | #R017278_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
V-SA Export | #R017278_014_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
V-SA Export | #R017366_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017366_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017377_003_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::S_SETB_MAXG_2, Effective Date: 31/10/2016, Version: 1 | Other
V-SA Export | #R017497_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017497_002_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017506_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017512_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017512_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017638_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
V-SA Export | #R017677_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMTT_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-SA Export | #R017883_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
V-SA Export | F_QNV+MLTR_L60 | 0.16667 | 0 | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
V-SA Export | V::N_JNWO_V2 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_MLTX_V2 | 0.16667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::S_KHKN_MAXG | 0.16667 | 0 | Out= Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S) ; Vic to SA Transient Stability limit for loss of the largest generator in SA | Outage
V-SA Export | V^^S_NIL_TBSE_2 | 0.16667 | 0 | Out = Nil(Note: with one or both Black Range series capacitors O/S); Vic to SA Long Term Voltage Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available). | NIL
V-SA Export | #R016738_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^S_MLSY_3, Effective Date: 19/04/2016, Version: 1 | Other
V-SA Export | #R016902_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R016902_003_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R017110_010_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_SETB_MAXG_2, Effective Date: 31/10/2016, Version: 1 | Other
V-SA Export | #R017110_013_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R017284_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
V-SA Export | #R017370_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V^^S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R017377_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_SETB_TBSE_2, Effective Date: 14/02/2017, Version: 1 | Other
V-SA Export | #R017449_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017487_012_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_SETB_MAXG_2, Effective Date: 31/10/2016, Version: 1 | Other
V-SA Export | #R017487_012_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_SETB_MAXG_2, Effective Date: 31/10/2016, Version: 1 | Other
V-SA Export | #R017497_005_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017499_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
V-SA Export | #R017501_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017506_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017506_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
V-SA Export | #R017543_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
V-SA Export | #R017840_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 10/09/2018, Version: 1 | Other
V-SA Export | #R017950_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::S_BLKRG_MAXG_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R017950_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::S_BLKRG_MAXG_2, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Export | #R018129_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 21/11/2018, Version: 1 | Other
V-SA Export | S>>KNPW_SETB_SETB | 0.083333 | 0 | Out= Penola West-Kincraig 132 kV line (Note: with both Black Range series caps I/S or O/S), avoid O/L of either South East-Tailem Bend 275kV line on trip of other South East-Tailem Bend 275kV | Outage
V-SA Export | S>>MOTB_TBTU_TBCG | 0.083333 | 0 | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::N_BURC_S2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V::N_BURC_V2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Export | V>>V_MLSY_4BR | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, prevent overload of the Keilor A2 or A4 500/220 kV txfmr on trip of the remaining MLTS-SYTS 500 kV line, radial mode, YWG1 on 220 kV, feedback | Outage
V-SA Export | V^^S_MLSY_3 | 0.083333 | 0 | Out = One Moorabool to Sydenham 500 kV line, Emergency Moorabool Transformer Tripping (EMTT) scheme disabled, maintain adequate network voltages and reactive margins on trip of the remaining MLTS-SYTS 500 kV line | Outage
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 199.9167 | 294.0833 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
V-SA Import | S::V_TBSE_TBSE_2 | 117.4167 | 0 | Out = one Tailembend-South East 275kV line (Note: with both Black Range series caps O/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines. | Outage
V-SA Import | S:V_500_HY_TEST_DYN | 49 | 64.5 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | V>>V_ROTS_TX_2A_R | 31.75 | 2.25 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
V-SA Import | S:V_500_HY_TEST | 24.5 | 48.0833 | SA to VIC on Heywood upper transfer limit of 500 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | V>>V_ROTS_TX_2B_R | 16.75 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage
V-SA Import | V>>V_NIL_6A_R | 11 | 0 | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL
V-SA Import | S:VS_650_HY_TEST_DYN | 8.0833 | 2.9167 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade, dynamic headroom, DS formulation only. | Outage
V-SA Import | NRM_SA1_VIC1 | 7.5833 | 1.1667 | Negative Residue Management constraint for SA to VIC flow | NIL
V-SA Import | F_S++HYSE_L6_1 | 5.1667 | 38.5 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 6 sec Requirement for risk of islanding, segment1 | Outage
V-SA Import | S::V_TBSE_TBSE_1 | 4.5833 | 2.1667 | Out = one Tailembend-South East 275kV line (NOTE: with both Black Range series capacitors I/S); SA to VIC Transient Stability limit for loss of other Tailembend-South East 275kV lines | Outage
V-SA Import | S:VS_650_HY_TEST | 4.5833 | 1.0833 | SA to VIC on Heywood and Murraylink combined upper transfer limit of 650 MW, limit for testing of Heywood interconnection upgrade. | Outage
V-SA Import | F_S++HYSE_L60 | 4.25 | 23.0833 | Out = (Heywood to South East) or (Heywood transformers) or (Heywood to Mortlake) or (Heywood to Tarrone) or (Moorabool to Mortlake) or (Moorabool to Sydenham) or (Moorabool to Tarrone), SA Lower 60 sec Requirement for risk of islanding | Outage
V-SA Import | S:V_PA_SVC_420 | 1.8333 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood upper transfer limit of 420 MW | Outage
V-SA Import | V>>V_KTS_TX_A2_2A_R | 1.75 | 9.0833 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
V-SA Import | V>>V_ROTS_TX_3A_R | 1.1667 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
V-SA Import | V::N_DDSM_V2 | 1 | 4.6667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
V-SA Import | #V-SA_RAMP_I_F | 0.66667 | 0.58333 | V-SA >= MIN(-65, InitialFlow + 50) (Wt=35) | Other
V-SA Import | S_V_NIL_ROCOF | 0.66667 | 9.5 | Out = NIL, limit SA to VIC Heywood interconnection flow to prevent Rate of Change of Frequency exceeding 3 Hz/sec in SA immediately following loss of Heywood interconnector. [NOTE: Switches based on ON/OFF status of Dalry Battery in Load Mode)] | NIL
V-SA Import | #R017497_007_RAMP_F | 0.58333 | 0 | Hard Ramping constraint for constraint V>>V_MLTS_TX_2A_R, Effective Date: 27/07/2018, Version: 1 | Other
V-SA Import | V>>V_MLTS_TX_2A_R | 0.58333 | 0 | Out = Moorabool A1 or A2 500/220kV transformer, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
V-SA Import | V>>V_ROTS_TX_3B_R | 0.5 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage
V-SA Import | SA_HYSE2 | 0.41667 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS), SA to Victoria on VicSA upper limit of 0 MW | Outage
V-SA Import | #R017359_002_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint SV_250_DYN, Effective Date: 17/08/2016, Version: 1 | Other
V-SA Import | V>>V_KTS_TX_A2_2B_R | 0.33333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
V-SA Import | #R017128_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_DDSM_V1, Effective Date: 05/04/2018, Version: 1 | Other
V-SA Import | S:VS_PA_SVC_570 | 0.25 | 0 | Out= one Para SVC, Oscillatory stability limit for SA to VIC on Heywood+ Murrylink upper transfer limit of 570 MW | Outage
V-SA Import | #R017549_003_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint S:V_PA_SVC_420, Effective Date: 07/08/2018, Version: 1 | Other
V-SA Import | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
V-SA Import | V>>BABE_DDGN_N-2 | 0.16667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
V-SA Import | #R017108_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V_ML_TRMO, Effective Date: 25/07/2017, Version: 1 | Other
V-SA Import | #R017487_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint S::V_TBSE_TBSE_2, Effective Date: 11/04/2017, Version: 1 | Other
V-SA Import | #R017693_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 03/09/2018, Version: 1 | Other
V-SA Import | S>>V_MOTB_TUTB_CGTB | 0.083333 | 0 | Out=Mobilong - Tailem Bend 132kV line; avoid O/L Cherry Gardens -Tailem Bend 275kV on trip Tungkillo -Tailem Bend 275kV line, Feedback | Outage
VIC1-NSW1 Export | V::N_NILxxx | 249.1667 | 581.4167 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | NIL
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 197.3333 | 285.75 | Out = Nil, avoid pre-contingent O/L of South Morang F2 500/330kV transformer, radial mode, YWPS unit 1 on 220kV, feedback | NIL
VIC1-NSW1 Export | V^^N_NIL_1 | 72.6667 | 0 | Out = Nil, avoid voltage collapse around Murray for loss of all APD potlines | NIL
VIC1-NSW1 Export | V>>V_ROTS_TX_2A_R | 37.5 | 2.25 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | V::N_SETB_V2 | 34.9167 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>N-NIL_HA | 21.0833 | 11.0833 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | NIL
VIC1-NSW1 Export | V>>V_ROTS_TX_2B_R | 17 | 0 | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, radial mode, YWG1 on 220 kV, feedback | Outage
VIC1-NSW1 Export | V::N_SETB_S2 | 15.6667 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_SETB_V1 | 14.8333 | 0 | Out = one South East to Tailem Bend 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_NIL_6A_R | 10.8333 | 0 | Out = Nil, avoid O/L South Morang F2 500/330 kV txfmr on trip of Rowville A1 500/220 kV txfmr, Hazelwood radial mode, Yallourn W Unit 1 in 500 kV mode, feedback | NIL
VIC1-NSW1 Export | V::N_WBHO_V2 | 10.25 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_DDSM_1 | 7.0833 | 0.16667 | Out= Dederang to South Morang 330kV line, avoid O/L Ballarat to Bendigo 220kV line on trip of the remaining South Morang to Dederang 330kV line, Feedback | Outage
VIC1-NSW1 Export | N>>N-NIL__G_15M | 7 | 0 | Out= Nil, avoid O/L Upper Tumut to Yass (2) using 15 mins rating on trip of Lower Tumut to Yass (3) line, Feedback | NIL
VIC1-NSW1 Export | V>>N-NIL_HG | 7 | 0.58333 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Nil trip; Feedback | NIL
VIC1-NSW1 Export | V::N_HYSE_V2 | 6.3333 | 0 | Out = Heywood to South East 275kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_WBHO_S2 | 5.9167 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_HORC_V2 | 5.6667 | 0.58333 | Out = Horsham to Red Cliffs 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V-MSUT_1 | 5.1667 | 0 | Out= Murray-UpperTumut(65), avoid Dederang to Wodonga (DDWO) O/L on Murray-LowerTumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | V::N_HWSM_V1 | 5 | 0 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_EPMB_S2 | 3.4167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_EPMB_V2 | 2.9167 | 0 | Out = Eildon to Mt Beauty 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_JNWO_S2 | 2.9167 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | VN_1050 | 2.75 | 0 | Discretionary Vic to NSW transfer upper limit of 1050 MW | Outage
VIC1-NSW1 Export | V::N_HWSM_V2 | 2.5833 | 18.5 | Out = Hazelwood to South Morang OR Hazelwood to Rowville 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | N::V_BYGR_2 | 2.0833 | 0 | Out = Bannaby to Gullen Range(61), stability limit (Snowy-NSW) for loss of Yass-Marulan (4/5) 330kV line | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 2 | 26.5833 | Out = Nil, avoid O/L either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | N::V_CNLT_2 | 1.9167 | 0 | Out = Lower Tumut -Canberra(07), stability limit (Snowy-NSW) for fault of various location between Yass-South Morang area | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2A_R | 1.75 | 8.25 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 500 kV network, feedback | Outage
VIC1-NSW1 Export | N^^N_NIL_1 | 1.5 | 0 | Out= Nil, northerly flow on line 01,2,3 and 07 cut-set voltage stability limit, Feedback | NIL
VIC1-NSW1 Export | V::N_DDSM_V2 | 1.3333 | 4.6667 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_3A_R | 1.1667 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 500 kV, feedback | Outage
VIC1-NSW1 Export | N>>N-NIL_01N | 1.0833 | 0.083333 | Out= Nil, avoid O/L Canberra to Yass (9) on trip of Kangaroo Valley to Dapto (18) line, Feedback | NIL
VIC1-NSW1 Export | V>>V_MLTS_TX_2A_R | 0.75 | 0 | Out = Moorabool A1 or A2 500/220kV transformer, avoid pre-contingent O/L South Morang 500/330kV (F2) transformer for NIL trip, Yallourn unit 1 in 500kV mode, radial mode at Hazelwood | Outage
VIC1-NSW1 Export | V::N_WBHO_V1 | 0.66667 | 0 | Out = Waubra to Ararat or Horsham to Ararat 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>V_SMTT2_2 | 0.66667 | 0 | Out = South Morang to Thomastown No. 2 220 kV line, avoid O/L of the Thomastown to South Morang No. 1 220 kV line on trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Export | V::N_JNWG_xxx | 0.58333 | 0 | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | #R017366_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017497_007_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V>>V_MLTS_TX_2A_R, Effective Date: 27/07/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017533_004_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
VIC1-NSW1 Export | V>>V_ROTS_TX_3B_R | 0.5 | 0 | Out= Rowville A1 or A2 500/220 kV txfmr, avoid overload of the South Morang F2 500/330 kV txfmr for trip of the remaining Rowville 500/220 kV txfmr, radial mode, Yallourn W1 on 220 kV, feedback | Outage
VIC1-NSW1 Export | #R017128_016_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 09/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017255_023_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 09/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017358_007_RAMP_F | 0.41667 | 0 | Hard Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017496_007_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017525_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017533_004_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017883_005_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017148_012_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017255_023_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 09/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017278_008_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017358_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017449_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017485_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017485_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017520_004_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017525_004_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017597_007_RAMP_F | 0.33333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017818_007_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
VIC1-NSW1 Export | V::N_SM330_2B_V22 | 0.33333 | 0 | Out = South Morang No.2 330kV bus, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2B_R | 0.33333 | 0 | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, radial mode, Yallourn W Unit 1 on 220 kV network, feedback | Outage
VIC1-NSW1 Export | #R017008_023_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 09/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017148_012_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017152_017_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V>>N_SM330_2B_3, Effective Date: 26/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017152_017_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V>>N_SM330_2B_3, Effective Date: 26/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017451_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017481_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017497_002_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017512_014_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017597_007_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017818_007_RAMP_F | 0.25 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 10/09/2018, Version: 1 | Other
VIC1-NSW1 Export | V::N_MLSY_V2 | 0.25 | 0 | Out = Moorabool to Sydenham 500kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | #R017128_016_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V>>V_DDSM_1, Effective Date: 09/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017152_012_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V12, Effective Date: 05/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017278_008_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SM330_2B_S22, Effective Date: 24/05/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017366_007_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_HYSE_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017497_002_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017506_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017512_011_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017512_011_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017638_007_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_WBHO_V2, Effective Date: 27/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017677_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_SMTT_V2, Effective Date: 10/09/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017883_005_RAMP_F | 0.16667 | 0 | Hard Ramping constraint for constraint V::N_MLTX_V2, Effective Date: 10/09/2018, Version: 1 | Other
VIC1-NSW1 Export | V::N_DDSM_V1 | 0.16667 | 0 | Out = Dederang to South Morang 330kV line, prevent transient instability for fault and trip of the parallel Dederang to South Morang 330kV line, VIC accelerates, Yallourn W G1 on 220 kV. | Outage
VIC1-NSW1 Export | V::N_JNWO_V2 | 0.16667 | 0 | Out = Jindera to Wodonga 330kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_MLTX_V2 | 0.16667 | 0 | Out = Moorabool Transformer 500/200kV, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>BABE_DDGN_N-2 | 0.16667 | 0 | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of both Dederang to Glenrowan 220kV No.1 and No.3 lines, Feedback | Outage
VIC1-NSW1 Export | V>>N_SM330_2B_3 | 0.16667 | 0 | Out = South Morang F2 500/330 kV and either H1 or H2 330/220 kV txfmr, SMTS 220kV bus tied, avoid O/L Ballarat to Bendigo 220kV line on trip of South Morang H2 or H1 220/330kV transformer, Feedback | Outage
VIC1-NSW1 Export | V>>N_SMHTX_1 | 0.16667 | 0 | Out = South Morang H 330/220 kV txfmr, only one SMTS H txfmr in service, avoid O/L the remaining in service SMTS H 330/220 kV txfmr (flow 220 kV to 330 kV) for trip of the South Morang F2 500/330 kV txfmr, feedback | Outage
VIC1-NSW1 Export | V>>V_NIL1A_R | 0.16667 | 0 | Out = Nil, avoid O/L either South Morang to Dederang 330 kV line (flow North) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Export | #R017008_023_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 09/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017148_017_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V>>N_SM330_2B_3, Effective Date: 26/04/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017278_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017284_014_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_SM330_2B_V22, Effective Date: 24/05/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017449_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017451_005_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_KGRC_V2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017499_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 26/06/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017501_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_MLTX_S2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017506_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_S2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017506_014_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_BURC_V2, Effective Date: 08/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017543_004_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_WBHO_S2, Effective Date: 16/08/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017693_001_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V>>V_ROTS_TX_2A_R, Effective Date: 03/09/2018, Version: 1 | Other
VIC1-NSW1 Export | #R017840_004_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint V::N_HORC_V1, Effective Date: 10/09/2018, Version: 1 | Other
VIC1-NSW1 Export | #R018129_002_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint V::N_HORC_S2, Effective Date: 21/11/2018, Version: 1 | Other
VIC1-NSW1 Export | V::N_BURC_S2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, SA accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V::N_BURC_V2 | 0.083333 | 0 | Out = Buronga to Redcliffs (0X1) 220kV line, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Yallourn W G1 on 500 kV. | Outage
VIC1-NSW1 Export | V>>SML_NIL_8 | 0.083333 | 1.75 | Out = Nil, avoid O/L Ballarat to Bendigo 220 kV line (flow North) for loss of Shepparton to Bendigo 220 kV line, 15 minute line ratings, feedback | NIL
VIC1-NSW1 Import | N^^V_NIL_1 | 1114.4167 | 1805.6667 | Out = Nil, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | NIL
VIC1-NSW1 Import | N^^V_NIL_MAXG_PP_N-2 | 26.1667 | 0 | Out = Nil, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit + Pelican Point when they declared as single credible contingency | NIL
VIC1-NSW1 Import | N>>V-NIL_O | 20.25 | 0 | Out = Nil, avoid overloading Upper Tumut to Murray (65) using 15 mins rating line on trip of Lower Tumut to Wagga (051) + 970,990,99M (out of Yass) line, Feedback | NIL
VIC1-NSW1 Import | N^^V_CNCW_1 | 11.5833 | 0 | Out = Canberra-Capital (6) or Kangaroo Valley to Capital (3W), avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V_NIL_1A | 7.8333 | 0.25 | Out = Nil, avoid O/L Murray to Dederang No.1 330kV line (flow MSS to DDTS) for loss of the parallel No.2 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
VIC1-NSW1 Import | N^^V_DDSM1 | 6.25 | 11.9167 | Out = Dederang to South Morang 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink or the parallel Dederang to South Morang 330kV line | Outage
VIC1-NSW1 Import | N^^V_DDWG | 3.6667 | 14.5 | Out = 330 kV line between Dederang to Wodonga to Jindera to Wagga, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_MSDD2 | 2.8333 | 0 | Out = Dederang to Murray 330 kV line, avoid voltage collapse at Darlington Point for loss of the remaining Dederang to Murray 330 kV line | Outage
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 2.5 | 0 | Negative Residue Management constraint for NSW to VIC flow | NIL
VIC1-NSW1 Import | N^^V_MSUT_1 | 2.1667 | 20 | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_BUDP_1 | 1.5833 | 0 | Out = Buronga to Balranald to Darlington Pt (X5) 220 kV line, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_SMTXF2_1 | 1.3333 | 0 | Out = South Morang F2 500/330kV txfmr, avoid voltage collapse at Darlington Point for loss of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V_NIL_1B | 1.3333 | 1 | Out = Nil, avoid O/L Murray to Dederang No.2 330kV line (flow MSS to DDTS) for loss of the parallel No.1 line, DBUSS-Line control scheme enabled, 15 min line ratings, feedback | NIL
VIC1-NSW1 Import | V>>DDSH_DDGN_N-2 | 1.0833 | 1.25 | Out= Nil, avoid O/L Dederang to Shepparton 220kV line on trip of both Dederang to Glenrowan No.1 and No.3 220kV lines, Feedback | Outage
VIC1-NSW1 Import | N>>V-LTMS_5 | 0.91667 | 0 | Out= LowerTumut-Murray(66), avoid UpperTumut to Murray (65) O/L(15m rating) on LowerTumut-Wagga(051)+ 970,990,99M trips; Feedback | Outage
VIC1-NSW1 Import | #R016888_005_RAMP_F | 0.83333 | 0 | Hard Ramping constraint for constraint N^^V_MSDD2, Effective Date: 16/02/2018, Version: 1 | Other
VIC1-NSW1 Import | N>>N-X_WGYS_99M_992 | 0.58333 | 0 | Out = Out = Murrumburrah to Yass 132kV line (99M) and Burrinjuck to Tumut132 132kV line (992), avoid Lower Tumut to Wagga 330kV (051) O/L on Murray - Dederang 330kV (67 or 68) trip with DBUSS action | Outage
VIC1-NSW1 Import | #R017724_011_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R017739_011_RAMP_F | 0.5 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | N_V_HV1075 | 0.5 | 0 | Snowy abolition constraint for discretionary Snowy to Vic transfer limit of 1075 MW | Outage
VIC1-NSW1 Import | #R017935_003_RAMP_V | 0.41667 | 0 | Soft Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018053_019_RAMP_V | 0.33333 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | N::V_DDMS | 0.33333 | 1.5 | Out=Dederang to Murray (67 or 68) line, NSW to Victoria Transient stability limit. | Outage
VIC1-NSW1 Import | V>>V_NIL_3 | 0.33333 | 0 | Out = Nil, avoid O/L either Dederang to South Morang 330 kV line (flow South) for trip of the parallel line, feedback | NIL
VIC1-NSW1 Import | #R016867_006_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N>>V-LTMS_5, Effective Date: 23/02/2018, Version: 1 | Other
VIC1-NSW1 Import | #R016888_005_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_MSDD2, Effective Date: 16/02/2018, Version: 1 | Other
VIC1-NSW1 Import | #R017752_011_RAMP_V | 0.25 | 0 | Soft Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018073_019_RAMP_V | 0.16667 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | #R016774_010_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_MSUT_1, Effective Date: 16/02/2018, Version: 1 | Other
VIC1-NSW1 Import | #R016867_006_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N>>V-LTMS_5, Effective Date: 23/02/2018, Version: 1 | Other
VIC1-NSW1 Import | #R016872_006_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N>>V-LTMS_5, Effective Date: 23/02/2018, Version: 1 | Other
VIC1-NSW1 Import | #R017703_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R017719_011_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_DDSM1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R017935_003_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_SMTXF2_1, Effective Date: 06/08/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018061_019_RAMP_V | 0.083333 | 0 | Soft Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other
VIC1-NSW1 Import | #R018073_019_RAMP_F | 0.083333 | 0 | Hard Ramping constraint for constraint N^^V_CNCW_1, Effective Date: 26/10/2018, Version: 1 | Other

## Outages
Constraint Set ID | 2018 Days | 2017 Days | Description
N-MBTE_1 | 284.9201 | 278.1528 | Out= one Directlink cable
N-TAPM_964 | 185.4167 | 0 | Out = Taree to Port Macquarie (964) 132kV line
V-MTGBRAND_22WT | 126.3194 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 22
N-LS_VC1 | 110.1528 | 11.566 | Out= Lismore SVC
N-X_WGYS_99M_992 | 70.7847 | 0 | Out = Murrumburrah to Yass 132kV line (99M) and Burrinjuck to Tumut132 132kV line (992) ; Wagga-Yass 132kV network
N-X_ARKK_CH_CB892A | 61.0417 | 0 | 966 (Armidale to Koolkhan) 132kV line O/S and Coffs Harbour CB 892A opened - Arrangement 1 - see OM521
N-X_MBTE_2 | 55.7882 | 115.3889 | Out= two Directlink cables
N-STWF1_WT_MW | 48.2535 | 0 | Limit number of turbines online and upper MW for Silverton wind farm
V-MTGBRAND_11WT | 37.1771 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 11
I-ML_ZERO | 35.3646 | 4.5938 | Limit Murraylink to zero in either direction
V-ROTX_R | 33.566 | 1.6562 | Outage = Rowville 500/220kV (A) transformer, Radial
V-MTGBRAND_33WT | 31 | 0 | Limit number of turbine online for Mt Gelibrand WF to be not exceed 33
S-BRDV | 30.25 | 25.6354 | Out = Brinkworth - Davenport 275 kV line
T-HAPM_220 | 30.1111 | 0.17361 | Out = One Hadspen to Palmerston (No.1 or No.2) 220kV line
T-PMWA | 27.3924 | 4.184 | Out = Palmerston to Waddamana 110kV line; suitable for associated CBs at WA either open or close
T-FATI | 26.8299 | 30.1667 | Out=Farrell-Tribute 220KV line
Q-STBS | 26.4167 | 19.8194 | Out= 856 or 8831 H29 Stanwell to H20 Broadsound 275 kV line
S-X_BC_CP | 25.4201 | 10.1701 | Out = both Black Range series capacitors bypassed
T-PMSH | 23.0312 | 1.1354 | Out = Palmerston to Sheffield 220kV line
S-KHKN | 22.8924 | 5.5312 | Out = Keith - Kincraig 132 kV line (Note: with both Black Range series caps I/S)
Q-BCCP_CAGS_CLOSED | 21.1111 | 0.79167 | Out= Bouldercombe to Calliope River (812) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, thermal limit equations for 811, 871 and 8859.
Q-GGCP_813 | 20.8333 | 5.3229 | Out= H6 Gin Gin to H67 Calliope River (813) 275kV feeder
T-HA_TX | 20.1076 | 0.5625 | Out = one Hadspen 220/110kV transformer
Q-LCCP_CAGS_CLOSED | 19.1979 | 0 | Out= Larcom Creek to Calliope River (8859) with 7104 and/or 7105 (Callide A to Gladstone South) 132 kV lines closed, thermal limit equations for 812 and 871.
Q-GGWO | 18.9167 | 9.7014 | Out= 815 or 816 H5 Woolooga to H6 Gin Gin 275 kV feeder
S-MKRB | 18.0347 | 0.38194 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps I/S)
F-I_ML_APD | 17.4896 | 8.2674 | Out=Nil, Dymanic FCAS for APD Load Event
S-TBSE_BC-2CP | 17.0521 | 0 | Out - one South East-Tailembend 275kV line (Note: with both Black Range series caps O/S)
S-KNPW | 16.2049 | 4.3125 | Kincraig to Penola West 132kV O/S, (Note: with both Black Range series caps I/S)
V-SMTS_HTX_R | 15.5833 | 1.8299 | Outage = South Morang H 330/220 kV transformer, only one SMTS H txfmr in service, Radial
T-LIPM | 14.4757 | 9.684 | Out = Liapootah to Waddamana to Palmerston 220kV line
S-BRTW | 14.4306 | 21.3438 | Out= Brinkworth- Templers West 275kV line
V-ARHO | 14.0486 | 0 | Out = Ararat to Horsham 220kV line
Q-SMRS | 13.9583 | 3.2361 | Out = 8911 (H91 Haughton River to H13 Ross) or 879 (H35 Strathmore to H91 Haughton) or 8857 or 8858 (H35 Strathmore to H13 Ross) 275kV line, CQ-NQ limits.
S-PATW | 12.9896 | 0 | Out = Para - Templers West 275kV line
F-T-CSGO | 12.8472 | 1.1042 | Out = one Chapel St to Gordon 220kV line, FCAS Requirements
T-CSGO | 12.8472 | 1.1042 | Out = One Chapel St to Gordon 220kV line
Q-GGWU | 12.3056 | 0 | Out= 819 H40 Wurdong to H6 Gin Gin 275kV feeder, CQ-SQ voltage stability limit, 2008/2009 implementation
V-HWSM | 11.8264 | 18.6111 | Outage = Hazelwood to South Morang 500kV line
S-RBPA | 11.5694 | 3.3924 | Out= Robertstown - Para 275 kV line
N-X_MBTE_3 | 10.6215 | 9.4062 | Out= all three Directlink cables
T-PM_TX | 10.3576 | 0.62847 | Out = Palmerston 220/110kV transformer
S-MOTB | 10.2812 | 0 | Out= Mobilong - Tailem Bend 132kV line (Note: with both Black Range series caps I/S)
T-GTHA | 8.8854 | 2.2118 | Out = One George Town to Hadspen 220kV line
S-TB275_E_BUS | 7.8403 | 0 | Out = Tailem Bend 275kV East Bus WITH/WITHOUT associated bus 275kV CBs O/S (Note: or Tailembend 132/275kV TX4 transformer + associated tx 275kV CBs O/S); (Note: all other 275kV CBs & lines at Tailembend I/S), (Note: with both Black Range series caps I/S)
S-SECB6161 | 7.6215 | 0 | Out = South East 132kV CB6161 ONLY O/S
Q-GGCP_814 | 7.3056 | 7.5243 | Out= H6 Gin Gin to H67 Calliope River (814) 275kV feeder
I-NQTE_BLOCK_ECS | 7.0139 | 0 | Block Directlink ECS operation when Directlink support is required, minimum of 29MW on Directlink QLD to NSW to ensure that Directlink ECS will not operate
N-MUTW_88 | 6.3542 | 1.9271 | Out = Muswellbrook to Tamworth (88) line
F-N-MUTW_88 | 6.3542 | 1.9271 | Out = Muswellbrook to Tamworth (88) 330kV line - FCAS Requirements
N-AR_VC1 | 6.3299 | 1.8472 | Out = Armidale SVC
V-EILDON2_ZERO | 6.25 | 0 | Discretionary upper limit for Eildon Unit 2 of 0 MW
V-HORC | 5.434 | 1.2708 | Out = Horsham to Murra Warra to Redcliffs 220kV line
S-BLMK | 5.2569 | 24.0035 | Out = Belalie - Mokota 275kV line
I-CTRL_ISSUE_TE | 4.6215 | 12.9167 | DC Link Control Issue Constraint for Terranora
Q-PWSP_808 | 4.5382 | 0.15972 | Out= 808 H2 South Pine to H9 Palmwoods 275 kV feeder (132 and 110 kV parallel between South Pine and Woolooga closed)
F-T-GTTE | 4.5174 | 1.5417 | Out = one George Town to Temco 110kV line OR loss of both Georgetown to Temco 110 kV lines or all Temco load declared credible
S-DVLK | 4.3056 | 11.5382 | Out = Davenport-Mt Lock 275kV line (Note:both Black Range series capacitors I/S)
N-KKLS_967 | 4.0764 | 66.7847 | Out= Koolkhan to Lismore (967) 132kV line
S-WIMK | 3.8993 | 0 | Out= Willalow-Mokota 275kV line (Note: WITH/WITHOUT associated line CBs I/S); (Note: with both Black Range series caps I/S)
T-X_BWLF_PMWA_110 | 3.7604 | 0 | Out= Bridgewater to Lindisfarne or Bridgewater to Waddamana AND Palmerston to Waddamana 110kV lines
S-RB_TX2 | 3.3438 | 0 | Out = Robertstown #2 275/132kV Transformer, with Murraylink sever trip I/S and Murraylink Runback Scheme I/S or O/S
V-HWYP2 | 3.2743 | 6.9028 | Out = Hazelwood to Yallourn No. 2 220 kV line, radial mode
N-ARTW_85 | 3.2535 | 2.0694 | Out = Armidale to Tamworth (85) line
Q-MEWF1_ZERO | 3.184 | 0 | Mt Emerald Wind Farm upper limit of 0 MW
V-MLTX_A2_R | 3.1736 | 0 | Out= Moorabool A2 500/220kV transformer, Radial Mode
N-BAMB_132_OPEN | 2.9757 | 18.7292 | Out = Any one 132 kV line between Ballina and Mullumbimby that opens the 132 kV path.
V-KTTX_A2_OR_A4_R | 2.8958 | 9.8403 | Outage = Keilor 500/220kV A2 or A4 transformer, Radial
S-SE_VC1 | 2.8056 | 9.5521 | Out= Either one of South East SVC O/S (Note: with both Black Range series caps I/S)
V-EPMB | 2.7917 | 2.3403 | Outage = Eildon to Mt Beauty 220kV line
V-DDSM | 2.7812 | 1.4028 | Out = Dederang to South Morang (DDTS-SMTS) 330 kV line
I-MUTE_758 | 2.5764 | 8.4896 | Out= 758 T174 Terranora to H4 Mudgeeraba 110kV line
S-PW-CB6156 | 2.5694 | 0.10417 | Out= Penola West 132kV CB 6156 Or CB 6260 Or CB 6157 O/S; (Note: with Penola West 132kV CB 6158 CLOSED)
V-DDTX2 | 2.5556 | 1.066 | Outage = Dederang No.2 330/220kV transformer
S-LB2_0 | 2.5 | 0 | Discretionary upper limit for Lake Bonney 2 generation of 0 MW
S-HALWF2_0 | 2.4757 | 0.82986 | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW
N-STWF1_ZERO | 2.3264 | 0 | Silverton wind farm upper limit of 0 MW
Q-LCCP_8859 | 2.1979 | 0 | Out= Larcom Creek to Calliope River (8859), thermal limit equations for 812 and 871.
S-LB_1+2+3_190 | 2.1806 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms<= 190 MW
N-ARDM_ONE | 2.1458 | 5.8333 | Out= one Armidale to Dumaresq (8C or 8E) line
S-X_TBTU+CB_BC-2CP | 2.0729 | 0 | Out= Tailembend -Tungkillo 275kV line + associated Tailembend 275kV line CBs O/S (Note: i.e. also Tailembend CBs 6595 & 6594 O/S; (Note: with both Black Range series caps O/S)
S-X_CGTB+CB_BC-2CP | 2.0694 | 0 | Out= Cherry Gardens-Tailembend 275kV line + associated 275kV line CBs O/S (Note: i.e. also Tailembend CBs 6535 & 6536 O/S); (Note: with both Black Range series caps O/S)
N-LSTN_96L | 1.9757 | 2.0972 | Out= Lismore to Tenterfield (96L)
V-BANNERTON_ZERO | 1.9618 | 0 | Bannerton Solar Farm upper limit of 0 MW
S-SNOW_N+S_190 | 1.8472 | 0 | Discretionary upper limit for Snowtown North and South Windfarms 190 MW
S-X_BWMP+MPPA | 1.8056 | 0 | Out = Blyth West- Munno Para 275kV line and Munno Para-Para 275kV (i.e. with Blyth West CB8002 OPEN & Blyth West tripping scheme I/S)
V-MLSY_NOEMTT_R | 1.7847 | 0 | Out = One Moorabool to Sydenham 500 kV line, EMTT scheme not armed, Radial mode
V-X_SMTS_F2_H12_R | 1.7361 | 0 | Out = South Morang F2 500/330 kV txfmr and H1 or H2 330/220 kV txfmr, radial mode
N-CHLS_89 | 1.7292 | 0.79514 | Out= Coffs Harbour - Lismore (89) 330kV line
N-LDMU_83 | 1.6389 | 0.96528 | Out = Liddell to Muswellbrook (83) line
F-N-LDMU_83 | 1.6389 | 0.96528 | Out = Liddell to Muswellbrook (83) 330kV line - FCAS Requirements
N-CNLT_07 | 1.6007 | 2.4444 | Out= Canberra - Lower Tumut (07)
S-SE_TX_1 | 1.5799 | 0 | Out = One South East 275/132kV transformer (NOTE: associated CBs I/S)
V-HWRO3 | 1.566 | 0.36458 | Outage = Hazelwood to Rowville No.3 500kV line
F-N-8C_ONE | 1.5382 | 0 | Out = Armidale to Dumaresq (8C) 330kV line - FCAS Requirements
S-SESG | 1.4653 | 0 | Out = South East - Snuggery - Mayura 132kV line (including line section connecting Lake Bonney WFs O/S, Lake Bonney WFs O/S)
V-ARCW | 1.3333 | 0 | Out = Ararat to Crowlands 220kV line
S-X_RBPA+CB6574+75 | 1.3056 | 0 | Out= Robertstown-Para 275kV line and Robertstown CB6574 and CB6575
N-WRWF1_055 | 1.2604 | 2.125 | White Rock WF upper limit of 55 MW
I-JNWO_RADIAL | 1.25 | 0 | Out = Jindera to Wodonga (060) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
T-X_HATX_PMWA_110 | 1.1944 | 0 | Out = one Hadspen 220/110kV transformer and Palmerston to Waddamana 110kV line; suitable for associated CBs at WA either open or close
S-PA_VC1 | 1.1632 | 1.2014 | Out= One Para SVC , (Note: with both Black Range Series caps I/S)
T-GTSH | 1.1458 | 1.3854 | Out = One George Town to Sheffield 220kV line
S-BUPV1_0 | 1.1181 | 0 | Discretionary upper limit for Bungala Stage 1 PV generation of 0 MW
S-X_MKRB+WERB | 1.1146 | 0 | Out = Robertstown -MWP4 -Waterloo East O/S(or any line segment between Robertstown-Waterloo East 132kV line O/S) + Mokota Robertstown 132kV line (i.e. Line Only O/S, all CBs at RB I/S); (Note: with both Black Range serices caps I/S)
N-AR_CP2 | 1.1076 | 12.8646 | Out = Armidale Capacitor Bank (120 MVAr)
N-LSDU_9U6 | 1.0938 | 3.7326 | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7), avoid O/L on the remaining 132kV line, Feedback
S-X_CGTB+CB | 1.059 | 2.3611 | Out= Cherry Gardens-Tailembend 275kV line + associated 275kV line CBs O/S (Note: i.e. also Tailembend CBs 6535 & 6536 O/S); (Note: with both Black Range series caps I/S)
N-BLOWERNG_ZERO | 1.0451 | 6.6076 | Blowering generation upper limit of 0 MW
N-JNWG_RADIAL | 1.0417 | 0.70486 | Outage = Jindera - Wagga (62) line, Wagga-Yass 132kV network Split, X5 opened and with 2 Yass Transformer in service
I-VS_050 | 1.0208 | 5.4201 | Victoria to SA on VicSA upper transfer limit of 50 MW
V-KGRC | 1.0174 | 0.87847 | Outage = Kerang to Wemen or Red Cliffs to Wemen 220 kV line sections, or full Kerang to Wemen to Red Cliffs 220kV line
S-HYSE_BC-2CP | 1.0035 | 0 | Out =One Heywood-South East 275kV line O/S (Note: with both Black Range series caps O/S)
I-HYSE | 1.0035 | 0 | Outage = Heywood to South East 275kV line
S-BG_CB6246 | 0.94792 | 0 | Out = Bungama 132kV CB6246
F-T-COGT | 0.89583 | 0.125 | Out = one Comalco to George Town 220kV line OR loss of both Comalco to Georgetown 220 kV lines or all Comalco potlines declared credible
I-VS_350 | 0.88194 | 0 | Victoria to SA on VicSA upper transfer limit of 350 MW
I-VS_250 | 0.85764 | 21.9479 | Victoria to SA on VicSA upper transfer limit of 250 MW
I-BURC | 0.84375 | 0.64583 | Out = Buronga to Redcliffs (0X1) 220kV line
N-COLEASF1_ZERO | 0.82639 | 0 | Coleambally solar farm upper limit of 0 MW
I-MSUT | 0.78125 | 1.7951 | Out= Murray - Upper Tumut (65) line
S-DVEM | 0.70139 | 0 | Out = Davenport - Emeroo #1 132kV line (Note: With/Without associated line CBs)
V-CWHO | 0.67014 | 0 | Out = Crowlands to Horsham 220kV line
S-TB275_E_BUS_BC-2CP | 0.64583 | 0 | Out = Tailem Bend 275kV East Bus WITH/WITHOUT associated bus 275kV CBs O/S (Note: or Tailembend 132/275kV TX4 transformer + associated tx 275kV CBs O/S); (Note: all other 275kV CBs & lines at Tailembend I/S), (Note: with both Black Range series capsO/S)
V-SMTT2 | 0.62847 | 1.4618 | Out= South Morang to Thomastown No. 2 220 kV line
S-SNOWNTH1_ZERO | 0.60764 | 0 | Discretionary upper limit for Snowtown 2 North WF generation of 0 MW
S-SNOWSTH1_ZERO | 0.60764 | 0 | Discretionary upper limit for Snowtown 2 South WF generation of 0 MW
S-MKRB_BC-2CP | 0.60069 | 0 | Out= Mokota-Robertstown 275kV line (Note: with both Black Range series caps O/S)
S-SNOW_N+S_210 | 0.52431 | 0 | Discretionary upper limit for Snowtown North and South Windfarms 210 MW
S-MYTX1_44248OPEN | 0.52431 | 0 | Out = Mayura No.1 132/33kV transformer (with 33kV bus tie isolator 44248 open)
N-X_89_LSTX_SVC | 0.49306 | 0 | Outage of Coffs Harbour to Lismore (89) line and 330/132kV Lismore Txs O/S, and Lismore SVC in reactive power control mode
S-MHNW_1 | 0.48958 | 0 | Out = Monash to North West Bend line 1, runback On
V-ARARAT_ZERO | 0.47917 | 0.15972 | Ararat Wind Farm upper limit of 0 MW
S-LB_1+2+3_150 | 0.43403 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=150 MW
Q-CLARESF1_ZERO | 0.40278 | 0 | Clare solar farm upper limit of 0 MW
Q-KSP1_ZERO | 0.38889 | 0 | Kidston solar farm upper limit of 0 MW
V-BALDHILL_ZERO | 0.37153 | 0 | Bald Hill Windfarm upper limit of 0 MW
V-DDMS | 0.36111 | 0 | Out = One Dederang - Murray (67 or 68) 330 kV line
N-BODWF1_ZERO | 0.35417 | 0 | Bodangora wind farm upper limit of 0 MW
F-N-ARDM_ONE | 0.34028 | 5.8333 | Out = one Armidale to Dumaresq (8C or 8E) 330kV line - FCAS Requirements
F-Q_TARONG#1_ZERO | 0.33333 | 0.13542 | Tarong 1 FCAS <= 0MW
F-Q_TARONG#2_ZERO | 0.33333 | 0.13542 | Tarong 2 FCAS <= 0MW
I-LTMS | 0.32639 | 0.88542 | Out= Lower Tumut - Murray (66) line
S-LB_1+2+3_210 | 0.31944 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=210 MW
T-FAMA | 0.29861 | 0.21528 | Out=Farrel-Mackintosh 110KV line
Q-810_PARALLEL_OPEN | 0.28819 | 1.9965 | Out= 810 H9 Palmwoods to H5 Woolooga 275 kV feeder with parallel 132 kV and 110kV network open
T-FARC1 | 0.28125 | 0 | Out=Farrell-Reece 1 220KV line
N-DPWG_63_X5 | 0.27778 | 2.0312 | Out = Darlington Point to Wagga (63) 330kV line + line X5 opened
F-I-BCDM_ONE | 0.26736 | 0 | Out = one Bulli Creek to Dumaresq (8L or 8M) or Dumaresq to Sapphire (8J) line 330kV line - FCAS Requirements
S-X_DVLK_LKCN | 0.26389 | 0 | Out = Davenport-Mt Lock-Canowie 275kV line (Note:both Black Range series capacitors I/S)
S-X_CNRB+CB | 0.25694 | 6.3438 | Out = Canowie-Robertstown 275kV line + Associated line CBs 6616 & 6571 at Robertstown O/S(Note:both Black Range series capacitors I/S)
S-NW_CB6021 | 0.25 | 0 | Out= North West Bend 132kV CB6021
T-TAMAR_GCS_OUT | 0.24306 | 0 | Out = Tamar CCGT GCS (Generation Control Scheme) - Limit Tamar CCGT to 144 MW
I-VS_300 | 0.18403 | 0 | Victoria to SA on VicSA upper transfer limit of 300 MW
I-BL-FCSPS_NO_ACTION | 0.18403 | 0 | Constrains Basslink transfers to levels where no FCSPS action is required for loss of Basslink
S-BRBG | 0.16319 | 1.3993 | Out = Brinkworth to Redhill to Bungama 132kV lines (Note: outage also takes out Clements Gap Windfarm).
I-VS_400 | 0.11806 | 0 | Victoria to SA on VicSA upper transfer limit of 400 MW
I-NQTE_-070 | 0.10069 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -70 MW
I-MUTE_757 | 0.10069 | 4.9097 | Out= 757 T174 Terranora to H4 Mudgeeraba 110kV line
V-HYTR | 0.097222 | 0.80556 | Out = Heywood to Tarrone (HYTS-TRTS) No. 1 500kV line
V-MTMERCER_ZERO | 0.086806 | 2.2951 | Mt Mercer Windfarm upper limit of 0 MW
N-TW_330_BUS3 | 0.0625 | 0.20833 | Out= Tamworth No.3 330kV bus
F-STHN_ISLE | 0.055556 | 0 | Southern separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M) - FCAS Contingency Requirements
F-QLD_STHN_ISLE_REG | 0.055556 | 0 | Qld / Southern separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M) - FCAS Regulation Requirements
F-QLD_ISLE | 0.055556 | 0 | Qld separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M) - FCAS Contingency Requirements
QLD_STHN_ISLE | 0.055556 | 0 | Qld / Southern separation between Armidale and Bulli Creek (8C and 8E or 8L and 8M)
Q-RS_160 | 0.052083 | 0 | Qld, Ross cutset upper limit of 160MW (discretionary)
Q-CN540 | 0.052083 | 0 | Qld CQ-NQArea Trf<=540MW(Nebo+Dys);
N-BROKENH1_ZERO | 0.045139 | 0.38889 | Broken Hill Solar Farm upper limit of 0MW
S-LB_1+2+3_230 | 0.045139 | 0 | Discretionary upper limit for Lake Bonney 1 + 2+ 3 Windfarms <=230 MW
T-FCSPS_RAMP | 0.038194 | 0 | Ramp down Basslink for outage of FCSPS
Q-RS_200 | 0.038194 | 0 | Qld, Ross cutset upper limit of 200MW (discretionary)
T-FA_TX | 0.038194 | 0 | Out = Farrell 220/110kV transformer, West Coast 110/220 kV parallel open, Farrell Contingency Arming Scheme unavailable.
I-NQTE_-010 | 0.03125 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -10 MW
V-MACARTHUR_ZERO | 0.020833 | 0.89931 | Macarthur Wind Farm upper limit of 0 MW
I-CTRL_ISSUE_ML | 0.017361 | 0 | DC Link Control Issue Constraint for Murraylink
F-ESTN_ISLE | 0.013889 | 0 | Eastern separation between Heywood and South East (HYTS - SESS) - FCAS Requirements
F-SA_ISLE | 0.013889 | 0 | SA separation between Heywood and South East (HYTS - SESS) - FCAS Requirements
F-SA_ESTN_ISLE_REG | 0.013889 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS) - Regulation FCAS Requirements
SA_ESTN_ISLE | 0.013889 | 0 | SA / Eastern separation between Heywood and South East (HYTS - SESS)
S-SE_132KV_BUS | 0.0069444 | 0.71528 | Out = ONLY One South East 132 kV bus (i.e. either East or West 132kV bus WITH/WITHOUT associated CBs)
V-MTGELIBRAND_ZERO | 0.0069444 | 0 | Mt Gelibrand wind farm upper limit of 0 MW
Q-RS_560 | 0.0069444 | 0 | Qld, Ross cutset upper limit of 560MW (discretionary)
T-MB_ZERO | 0.0034722 | 0 | Limit Meadowbank to 0 MW for Energy and FCAS
I-NQTE_-080 | 0 | 0 | NSW to Qld on Terranora Interconnector upper transfer limit of -80 MW

## Outage stats
Column1 | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2014 | 12 | 27 | 9 | 0
2015 | 27 | 60 | 8 | 2
2016 | 24 | 36 | 7 | 1
2017 | 20 | 33 | 5 | 4
2018 | 21 | 74 | 15 | 3
ElectraNet 2014 | 93 | 311 | 571 | 108
2015 | 447 | 918 | 1003 | 231
2016 | 110 | 266 | 309 | 176
2017 | 281 | 687 | 907 | 426
2018 | 417 | 863 | 973 | 804
Essential E 2014 | 6 | 39 | 82 | 4
2015 | 0 | 17 | 59 | 0
2016 | 3 | 26 | 40 | 0
2017 | 4 | 28 | 61 | 0
2018 | 8 | 5 | 29 | 0
Powerlink 2014 | 350 | 1143 | 1993 | 15
2015 | 1076 | 3173 | 6415 | 100
2016 | 273 | 885 | 2265 | 17
2017 | 1796 | 5071 | 11266 | 195
2018 | 2020 | 5841 | 13383 | 222
AusNet 2014 | 179 | 778 | 473 | 38
2015 | 197 | 1119 | 918 | 86
2016 | 170 | 876 | 695 | 97
2017 | 316 | 1484 | 1208 | 80
2018 | 304 | 1467 | 970 | 54
TasNetworks 2014 | 33 | 125 | 130 | 73
2015 | 128 | 629 | 993 | 302
2016 | 19 | 88 | 166 | 32
2017 | 89 | 472 | 602 | 323
2018 | 171 | 577 | 637 | 238
TransGrid 2014 | 134 | 636 | 991 | 614
2015 | 161 | 678 | 1290 | 764
2016 | 116 | 472 | 973 | 506
2017 | 277 | 911 | 1365 | 856
2018 | 326 | 820 | 1730 | 522

## NEM Changes
PROJECT | DATE | REGION | NOTES
Clare Solar Farm | 14 February 2018 | Qld | New Generator
Silverton Wind Farm | 26 February 2018 | NSW | New Generator
Gannawarra Solar Farm | 20 March 2018 | Victoria | New Generator
Wilalo Substation | 27 March 2018 | SA | Willalo substation has been energised at 275 kV. Belalie – Mokota 275 kV Transmission line has now been cut to form two lines connecting to Willogoleche Windfarm substation. The new transmission line names are Belalie – Willalo 275 kV Transmission line and Willalo – Mokota 275 kV Transmission line.
George Town No.3 Capacitor Bank | 18 April 2018 | Tasmania | George Town No.3 42 MVAr 110 kV capacitor bank commissioned.
Manildra Solar Farm | 20 April 2018 | NSW | New Generator
Bungala Stage 1 Solar Pv | 1 May 2018 | SA | New Generator
Hamilton Solar Farm | 29 May 2018 | Qld | New Generator
Salt Creek Wind Farm | 29 May 2018 | Victoria | New Generator
Whitsunday Solar Farm | 29 May 2018 | Qld | New Generator
Mt Gelibrand Wind Farm | 1 June 2018 | Victoria | New Generator
Crookwell Substation | 05 June 2018 | NSW | Crookwell substation has been energised at 330 kV. Bannaby – Gullen Range 330 kV transmission line has now been cut to form two lines connecting to Crookwell Windfarm substation. The new transmission line names are Bannaby – Crookwell 330 kV transmission line and Crookwell – Gullen Range 330 kV transmission line.
Dalrymple Battery (Generation Component) | 5 June 2018 | SA | New Generator
Dalrymple Battery (Load Component) | 5 June 2018 | SA | New Generator
Ross River Solar Farm | 26 June 2018 | Qld | New Generator
Darling Downs Solar Farm | 27 June 2018 | Qld | New Generator
Bodangora Wind Farm | 10 July 2018 | NSW | New Generator
Bannerton Solar Farm | 11 July 2018 | Victoria | New Generator
Sun Metals Solar Farm | 19 July 2018 | Qld | New Generator
Willogoleche Wind Farm | 24 July 2018 | SA | New Generator
Bungala Stage 2 Solar Pv | 31 July 2018 | SA | New Generator
Collinsville Solar Farm | 31 July 2018 | Qld | New Generator
Crookwell 2 Wind Farm | 1 August 2018 | NSW | New Generator
Crush Creek to Strathmore 275 kV transmission line | 14 August 2018 | Qld | Transmission line commissioned
Mt Emerald Wind Farm | 14 August 2018 | Qld | New Generator
Mount Emerald to Walkamin Wind Farm 275 kV transmission line | 16 August 2018 | Qld | Transmission line commissioned
White Rock Solar | 21 August 2018 | NSW | New Generator
Ross to Lake Ross 132 kV transmission line and Lake Ross No.1 132/33 kV transformer | 29 August 2018 | Qld | Transmission line and transformer commissioned
Coleambally Solar Farm | 3 September 2018 | NSW | New Generator
Emerald Solar Farm | 13 September 2018 | Qld | New Generator
South Morang H3 Transformer | 15 September 2018 | Victoria | South Morang Terminal Station H3 330 kV/220 kV transformer commissioned
Crowlands No.2 220 kV Bus | 15 September 2018 | Victoria | Crowlands Terminal Station No.2 220 kV Bus Commissioned.
Daydream Solar Farm | 28 September 2018 | Qld | New Generator
Hayman Solar Farm | 28 September 2018 | Qld | New Generator
Karadoc Solar Farm | 9 October 2018 | Victoria | New Generator
Coopers Gap 275 kV substation | 17 October 2018 | QLD | A new substation cut-in between Halys and Westerndowns on the the previous 8866 275 kV line
Corraberra Hill 275 kV substation | 17 October 2018 | SA | A new substation cut-in between Cultana and Davenport. Previous Cultana to Davenport No.1 275 kV line is now Cultana to Corraberra Hill to Davenport 275 kV line
Ballarat Battery (Generation Component) | 6 November 2018 | Victoria | New Generator
Ballarat Battery (Load Component) | 6 November 2018 | Victoria | New Generator
Crowlands Wind Farm | 6 November 2018 | Victoria | New Generator
Wemen Solar Farm | 6 November 2018 | Victoria | New Generator
Gannawarra Battery (Generation Component) | 7 November 2018 | Victoria | New Generator
Gannawarra Battery (Load Component) | 7 November 2018 | Victoria | New Generator
Susan River Solar Farm | 18 December 2018 | Qld | New Generator

## Disclaimer
Disclaimer
This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. AEMO has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and
· are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.