## AEMO-use Only
AEMO-approved fields
DUID:
Wind Farm Maximum Capacity (MW):
Cluster ID(s):
Cluster Maximum Capacity (MW):
Last updated: 19/09/2022

## Submission Guideline
ECM data template submission guideline:
This guideline for the Energy Conversion Model (ECM) data for registering Semi-Scheduled Generating Units has been published under NER clause 2.1.3(b)(5).
How to use this document
Parameters that need to be supplied by the wind farm to AEMO are listed and marked as 'Mandatory'.
Sampling rates for dynamic parameters are specified. These denote the sampling intervals for data. Aggregation of this data will be done within MMS or the ECM.
Italicised terms are defined in 'Chapter 10: Glossary' of the National Electricity Rules (NER).
Who needs to submit an ECM
A generating unit intending to register as semi-scheduled must submit an ECM under the NER clause 2.2.7(c)(2).
Some Non-Scheduled generating units may be required to submit an ECM under NER clause 2.2.3(c).
NER clause 2.2.7(c2) states a person must comply with any terms and conditions imposed by AEMO as part of an approval under paragraph 2.2.7(c1).
To avoid delays, AEMO recommends that the first draft of the ECM be submitted to AEMO at least three months before applying for Registration. Note, official ECM approval can only be provided after applying for Registration otherwise only conditional ECM approval will be provided.
Document structure
The document is divided in farm level and cluster level tabs. To this end:
- The 'ECM Wind Farm' tab contains fields relating to wind farm level operation.
- The 'ECM Wind Farm Cluster' tab contains fields relating to cluster level operation. Additional Cluster tabs should be created if more than one cluster exists for the wind farm.
Facility hierarchy
There is an assumed hierarchy of sub-components that constitute a wind farm. These are illustrated in the diagram below
In the event that multiple sub-components are available, parameters applicable to these sub-components will need to be provided for each sub-component.
E.g. There are multiple clusters in a facility. Parameters that are applicable to every cluster in the 'ECM Wind Farm Cluster' tab will need to be provided
Note that one ECM is required to be submitted for every dispatchable unit (DUID) within a facility.
Additional Information
In the interest of maintaining accuracy of the wind generation forecasts, any material changes to the ECM data must be re-submitted to AEMO and at any other time on AEMO request.
Where relevant, the data entered into the ECM data template needs to be consistent with (or derived from) information and/or data provided in the: - Generator registration application documentation - Generator Performance Standard (GPS) - Power System Design Data Sheets and Generating System Setting Data Sheets or as otherwise agreed with AEMO.
Turbine
Facility
A cluster is potentially comprised of multiple turbines
A facility is potentially comprised of multiple dispatchable units
Cluster
Dispatchable Unit
A dispatchable unit is potentially comprised of multiple clusters

## Cluster Definition Guideline
Cluster Definition Guideline
A "cluster" corresponds to a group of wind turbines of identical type in the wind farm and within a reasonable geographic area. See below for more details. Participant to propose the cluster arrangement to AEMO for approval.
To define a “cluster” the ensemble of the following constraints should be satisfied:
i. no more than 7 km x 7 km (with some degree of flexibility)
ii. only identical turbines are included in a cluster
NOTE: Identical turbines means turbines supplied by same manufacturer, having the same model, hub height and characteristic power curve.
The factors that are expected to affect the definition of such clusters are :
· Important changes in the terrain complexity throughout the area covered by the wind farm
· Changes in the meteorology due to the size of the area covered (presence of local patterns)
· Physical separation of parts of the wind farm (considerable distance between groups of wind turbines)
· Different timing in the development/commissioning of parts of the wind farm
· Different types of wind turbines in the wind farm (model, hub height)
· More than one connection point to the grid
Additional Information
Wind farms with only one cluster do not require cluster level SCADA signals. Only farm level SCADA signals stated in 'ECM Wind Farm' sheet are required.

## ECM Wind Farm
Energy Conversion Model for Wind Farms: | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data Type | Valid Range | Mandatory | Interval | Value | Units | Comments | Description
Farm Level | Parameters that apply to the wind farm. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value.
Wind farm identification
Power Station name | Descriptive String | n/a | Yes | n/a |  | n/a |  | Name of the wind farm. To be same as specified in the 'Application for Registration as a Generator in the NEM' document.
Region | Descriptive String | n/a | Yes | n/a |  | n/a |  | Name of NEM region of the wind farm. To be same as specified in the 'Application for Registration as a Generator in the NEM' document.
Wind farm nominal data
Nameplate Rating | Scalar decimal number | >0 | Yes | n/a |  | MW |  | The total installed capacity of the Wind Farm (MW) as outlined in the Generator Performance Standard (GPS). This equals the sum of the nameplate rating of all turbines installed. This Item must match the nameplate rating of the dispatchable unit stated in the "Application for Registration as a Generator in the NEM" document.
Maximum Capacity | Scalar integer number | >0 | Yes | n/a |  | MW |  | Maximum generation to which the semi-scheduled generating unit may be dispatched as outlined in the Generator Performance Standard (GPS), rounded down to the nearest whole MW. This definition can be found in the "Application for Registration as a Generator in the NEM" document. The Maximum Capacity value must reference the same measurement point as the SCADA Wind Farm Active Power signal.
Wind farm location & terrain data
Latitude | Scalar decimal number | (-90,90) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Longitude | Scalar decimal number | (-180,180) | Yes | n/a |  | Decimal degrees |  | Defined at the centre of the collector area
Altitude | Scalar decimal number | (-15,2228) | Yes | n/a |  | metres ASL |  | Representative value for the wind farm altitude (given as a unique value in m ASL [meters above sea level]). It should be average of ground altitude for turbine locations.
Site Map | PDF / high resolution image | n/a | Yes | n/a |  | pdf file |  | Given as a map with marked wind turbines position (high resolution image/ PDF file). Please submit as separate pdf.
Air Density | Scalar decimal number | >0 | Yes | n/a |  | kg/m3 |  | The typical air density at the level of this Wind Farm (yearly average). In case of multiple power curves the one that corresponds to this density is considered.
Wind farm other
Number of Clusters | Scalar positive integer | >0 | Yes | n/a |  | n/a |  | Number of clusters of the facility, for cross-checking
NSP MW Control Schemes in Operation | String | n/a | Yes | n/a |  | n/a |  | Provide details of NSP MW Control Schemes used to down regulate the wind farm at wind farm and/or cluster level.
Any other restrictions | String | n/a | Yes | n/a |  | n/a |  | Provide details of any other limitations imposed on the Wind Farm. This should be consistent with information provided in Power System Design Data Sheets section 6.1.2 (tab S-6), and Data Sheets section 7.1.2 (tab: S-7).
Wind Farm SCADA to AEMO: |  | Valid range must be reflected in the corresponding SCADA signal list. |  |  | Specify if the non-mandatory signal will be provided. |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated at least every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, a maximum 15-second average update is required.
Data Parameter | Data Type | Valid Range | Mandatory | Interval | Provision - Yes/No? | Units | Comments | Description
Wind Farm Active Power | Scalar decimal number | (<0,>=0) | Yes | 4-10 secs | Yes | MW |  | Total wind farm active power. The SCADA Wind Farm Active Power measurement must reference the agreed point of dispatch.
Control System Set-Point | Scalar non-negative decimal number | (0, 2.5 x Nameplate Rating) | Yes | 4-10 secs | Yes | MW |  | MW Set-Point applied in the wind farm's control system to limit (down regulate) its output. At other times when no limit applies, the set-point to be set to above the wind farm's Nameplate Rating, but below 250% of it. SCADA MW Set-Point must reference the same measurement point as the SCADA Active Power signal.
Local Limit | Scalar non-negative decimal number | (0, Max Capacity) | Yes | 4-10 secs | Yes | MW |  | In MW, the SCADA Local Limit for a wind farm is the lower of its plant availability and all technical limits on the capacity of its connection assets to export energy. The SCADA Local Limit is used to cap the UIGF for the wind farm in the dispatch timeframe. The SCADA Local Limit excludes limits managed by AEMO through the central dispatch process (e.g. via constraints). Transmission network and distribution network limits already communicated to and managed by AEMO through the central dispatch process must be excluded from the SCADA Local Limit (to ensure AEMO’s compliance with clause 3.7B(c)(6) of the Rules). Limits already communicated in the SCADA Turbines Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits not intended to apply at the end of the next dispatch interval may be excluded from the SCADA Local Limit, unless otherwise agreed with AEMO. The SCADA Local Limit should not exceed the Maximum Capacity of the wind farm. SCADA Local Limit must reference the same measurement point as the SCADA Wind Farm Active Power signal.
Possible Power | Scalar non-negative decimal number | (0, Max Capacity) | No | 4-10 secs |  | MW |  | SCADA Possible Power is the Generator’s estimate in MW of current unconstrained intermittent generation, subject only to technical factors affecting operation of its generation and connection assets. SCADA Possible Power is used to assess the performance of unconstrained intermittent generation forecasts. SCADA Possible Power must be calculated assuming limits managed by AEMO through the central dispatch process do not apply. SCADA Possible Power must reflect any Local Limits at the wind farm, unless agreed with AEMO. The SCADA Possible Power must not exceed the Maximum Capacity of the wind farm. SCADA Possible Power must reference the same measurement point as the SCADA Wind Farm Active Power signal.
Number of Wind Turbines Available for Generation | Scalar integer number | >=0 | Yes | 4-10 secs | Yes | no. |  | Number of turbines available for generation. This definition is the summation of: • Turbines operating • Turbines available to operate, but not operating due to ambient wind conditions (very low / high wind speeds, extreme direction change) • Turbines available to operate, but paused due to down regulation. This definition excludes all the following cases: • Turbines under maintenance or repair • Turbines with a fault or damage • Turbines not yet built or still being commissioned and not released for operation • Turbines that cannot operate because connection to networks still being commissioned If agreed with AEMO, turbines paused due to ambient temperature may be counted as available in this signal.
Number of Wind Turbines Operating / Actively Generating | Scalar integer number | >=0 | Yes | 4-10 secs | Yes | no. |  | Number of turbines actively generating power
Wind Turbines Extreme Wind Cut-out | Scalar integer number | >=0 | No | 4-10 secs |  | no. |  | Number of turbines counted in the Turbines Available signal that are currently in cut-out mode due to extreme high wind speed or extreme wind direction change. If agreed with AEMO, extreme wind direction change may be excluded.
Wind Speed | Scalar decimal number | >=0 | Yes | 4-10 secs | Yes | m/s |  | SCADA Wind Speed – Farm level is a single wind speed measurement, which must be representative of wind conditions across the site for calculation of dispatch UIGF. This is an average of all turbine nacelle wind speed measurements. The measurement is considered representative if, on the advice of the AWEFS vendor, the wind speed measurement is sufficiently stable and there is adequate correlation between the wind speed measurement and the farm’s active power output when not downregulated.
Wind Direction | Scalar decimal number (bearing) | (0,360) | Yes | 4-10 secs | Yes | º |  | SCADA Wind direction – Farm level is a single wind direction measurement which must be an average of all turbine nacelle wind direction measurements. This requires proper directional averaging (x-y decomposition). Example: https://en.wikipedia.org/wiki/Mean_of_circular_quantities https://www.itron.com/blog/forecasting/computing-a-weighted-average-wind-speed-and-wind-direction-across-multiple-weather-stations
Ambient Temperature | Scalar decimal number | (-50,100) | Yes | 4-10 secs | Yes | ºC |  | To be representative of the wind farm. Also provide the height at which this is measured.
Barometric Pressure | Scalar decimal number | (0,1100) | No | 4-10 secs |  | hPa |  | To be representative of the wind farm. Also provide the height at which this is measured.
Ends

## ECM Wind Farm Cluster 1
Energy Conversion Model for Wind Farms: | [7 empty] | Please submit completed ECM to op.forecasting@aemo.com.au
Data Parameter | Data Type | Valid Range | Mandatory | Interval | Value | Units | Comments | Description
Cluster Level | Parameters that apply to a cluster Please copy this sheet into a separate tab for each additional cluster. |  |  |  | Specify one distinct value per cell. If variants or a range exists, specify the most relevant value. |  |  | A "cluster" corresponds to a group of wind turbines of similar type in the wind farm and within a reasonable geographic area. Please see the ‘Cluster definition guideline’ for more details. Participant to propose the cluster arrangement to AEMO for approval. If there are more than one such clusters, please repeat the following table in a separate tab.
Cluster identification
Cluster Reference | Descriptive String | n/a | Yes | n/a |  | n/a |  | Unique reference for this cluster. Note, following ECM submission, AEMO will allocate a unique cluster identification to each of your clusters.
Cluster characteristics
Number of Wind Turbines in this Cluster | Scalar integer | >0 | Yes | n/a |  | no. |  | Number of identical machines proposed in this cluster. This should be consistent with information provided in Power System Design Data Sheets section 7 (tab S-7).
Turbine Manufacturer & Model ID | Descriptive string | n/a | Yes | n/a |  | n/a |  | Type of the wind turbines proposed in the cluster. Mark the commercial wind turbine reference example - VESTAS V66 1.75 MW. This should be consistent with information provided in Power System Design Data Sheets section 7 (tab S-7).
Hub height of wind turbines in this Cluster | Scalar decimal number | >0 | Yes | n/a |  | m |  | The hub height of this type of wind turbines
Rotor diameter | Scalar decimal number | >0 | Yes | n/a |  | m |  | Rotor Diameter of the turbine
Manufacturers' power vs wind speed characteristic curve | Complete turbines curve table | n/a | Yes | n/a | See 'Turbine Curves Table' tab | n/a |  | Provide the characteristic curve of the type of wind turbines in this cluster using the turbine curves table attached. This is the basic power curve provided by the manufacturer.
Turbine Nameplate Rating | Scalar decimal number | >0 | Yes | n/a |  | kW |  | The nameplate rating of that type of turbine (kW) as defined in the National Electricity Rules. This should be consistent with information provided in Power System Design Data Sheets section 7.1.1 (tab S-7).
Turbine Temperature Rating | 2-vector (min, max) | n/a | Yes | n/a |  | min ºC |  | Temperature Range of turbine operation, example -20 to 40 degrees C.
max ºC
Wind Turbine Cut-out Temperature / Automatic Stop limit due to high temperature | Scalar decimal number | n/a | Yes | n/a |  | ºC |  | For cases where the wind turbine need to be stopped during certain high temperatures. This should be consistent with information provided in Power System Design Data Sheets section 7.1.1 (tab S-7). Temperature threshold and associated time delay also to be provided, if available in technical specification of the Turbine.
Wind Turbine Cut-in Temperature / Automatic re-enter in operation after cut-out due to high temperatures | Scalar decimal number | n/a | Yes | n/a |  | ºC |  | Temperature where the wind turbine gets back in operation after a cut-off due to high temperature.
Wind Turbine Cut-out Temperature / Automatic Stop limit due to very low negative temperatures | Scalar decimal number | n/a | Yes | n/a |  | ºC |  | For cases where the wind turbine need to be stopped during certain low negative temperatures
Wind Turbine Cut-in Temperature / Automatic re-enter in operation after cut-out due to very low negative temperatures | Scalar decimal number | n/a | Yes | n/a |  | ºC |  | Temperature where the wind turbine gets back in operation after a cut-off due to low negative temperatures.
Rated Speed | Scalar decimal number | >0 | Yes | n/a |  | m/s |  | The rated speed (m/s) of that type of turbine, i.e. the wind speed at which full power is attained. This should be consistent with information provided in Power System Design Data Sheets section 12.4.1 (tab S-12.4) - "wind speed at which full power is attained".
Cut-in Speed | Scalar decimal number | >0 | Yes | n/a |  | m/s |  | Minimum wind speed at which the wind turbine starts to produce power. This should be consistent with information provided in Power System Design Data Sheets section 12.4.1 (tab S-12.4).
Cut-out Speed | Scalar decimal number | >0 | Yes | n/a |  | m/s |  | Minimum wind speed at which the wind turbine is stopped to avoid damage at high wind speeds. This should be consistent with information provided in Power System Design Data Sheets section 12.4.1 (tab S-12.4).
Restart after cut-out Wind Speed | Scalar decimal number | >0 | Yes | n/a |  | m/s |  | Maximum wind speed at which the wind turbine can re-enter operation after being cut-out due to too high wind speeds.
Cluster characteristics
Imposed noise level restrictions | Descriptive String | n/a | Yes. If any. | n/a |  | DB |  | For cases where wind turbines should operate at a specific noise mode. The appropriate power curve is then selected.
Manufacturers' power vs wind speed characteristic curve as a function of noise level | Duplicate the turbines curve table for each noise level. | n/a | Yes. If applicable. | n/a |  | n/a |  | If restrictions apply due to noise, the manufacturer's characteristic wind speed vs power curves of the wind turbines for different noise levels should be provided using the table provided for each noise level.
Legal start night time | Time | hh24:mi | Yes. If applicable. | n/a |  | Time |  | For cases where wind turbines stop or run on a special power curve (indicate curve) during night hours for noise reduction or other reasons.
Legal ending night time | Time | hh24:mi | Yes. If applicable. | n/a |  | Time |  | For cases where wind turbines stop or run on a special power curve (indicate curve) during night hours for noise reduction or other reasons.
Cluster SCADA (Not required for wind farms with only one cluster) |  | Valid range must be reflected in the corresponding SCADA signal list. |  |  | Specify if the non-mandatory signal will be provided. |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required.
Data Parameter | Data Type | Valid Range | Mandatory | Interval | Provision - Yes/No? | Units | Comments | Description
Cluster Active Power | Scalar decimal number | >0 | Yes | 4-10 secs |  | MW |  | Total cluster active power. This measurement must reference the generator terminals in this cluster.
Cluster Number of Wind Turbines Available for Generation | Scalar integer | >=0 | Yes | 4-10 secs |  | No. |  | Number of turbines available for generation. This definition is the summation of: • Turbines operating • Turbines available to operate, but not operating due to ambient wind conditions (very low / high wind speeds, extreme direction change) • Turbines available to operate, but paused due to down regulation. This definition excludes all the following cases: • Turbines under maintenance or repair • Turbines with a fault or damage • Turbines not yet built or still being commissioned and not released for operation • Turbines that cannot operate because connection to networks still being commissioned If agreed with AEMO, turbines paused due to ambient temperature may be counted as available in this signal.
Cluster Number of Wind Turbines Operating / Actively Generating | Scalar integer | >=0 | Yes | 4-10 secs |  | No. |  | As number of turbines actively generating power.
Cluster Turbines Extreme Wind Cut-out | Scalar integer | >=0 | No | 4-10 secs |  | No. |  | Number of turbines counted in the Turbines Available signal that are currently in cut-out mode due to extreme high wind speed or extreme wind direction change. If agreed with AEMO, extreme wind direction change may be excluded.
Cluster Wind Speed | Scalar decimal number | >=0 | Yes | 4-10 secs |  | m/s |  | SCADA Wind Speed – Cluster level is a single wind speed measurement, which must be representative of wind conditions across the cluster. This is an average is of all turbine nacelle wind speed measurements within the cluster. The measurement is considered representative if, on the advice of the AWEFS vendor, the wind speed measurement is sufficiently stable and there is adequate correlation between the wind speed measurement and the cluster's active power output when not downregulated.
Cluster Wind Direction | Scalar decimal number | (0,360) | Yes | 4-10 secs |  | º |  | SCADA Wind direction - Cluster level is a single wind direction measurement, which must be an average of all turbine measurements within the cluster. This requires proper directional averaging (x-y decomposition). Example: https://en.wikipedia.org/wiki/Mean_of_circular_quantities https://www.itron.com/blog/forecasting/computing-a-weighted-average-wind-speed-and-wind-direction-across-multiple-weather-stations
Wind turbines location
Data Parameter | Data Type | Valid Range | Mandatory | Latitude | Longitude | Units | Comments | Description
Geographical coordinates of Wind Turbine #1 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #2 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #3 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #4 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #5 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #6 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #7 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #8 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #9 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #10 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #11 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #12 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #13 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #14 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #15 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #16 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #17 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #18 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #19 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Geographical coordinates of Wind Turbine #20 | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Add more if required | 2x Scalar decimal number | (-90,90), (-180,180) | Yes |  |  | Decimal degrees |  | Coordinates in Latitude/ Longitude
Ends

## Turbine Curves Table
Wind Turbine Characteristic Curves
Please repeat the following table for each type of wind turbines.
Repeat the table if for a wind turbine type a different characteristic curve is available for different values of air density and/or for operation at different noise modes (in case that noise restrictions apply).
The wind speed increment must be in the order of 0.5 m/s up to the cut-out speed.
Type of wind turbine:
Air density (kg/m3):
Noise mode dB (A):
| Speed (m/s) | Power (kW)
0
0.5
1
1.5
2
2.5
3
3.5
4
4.5
5
5.5
6
6.5
7
7.5
8
8.5
9
9.5
10
10.5
11
11.5
12
12.5
13
13.5
14
14.5
15
15.5
16
16.5
17
17.5
18
18.5
19
19.5
20
20.5
21
21.5
22
22.5
23
23.5
24
24.5
25
…
…