## Submission Guideline
ECM data template submission guideline:
This guideline for the Energy Conversion Model (ECM) data for registering Semi-Scheduled Generators has been published as prescribed in the Central Dispatch and Integration of Wind and Other Intermittent Generation Rule 2008 under clause 2.2.7(d).
Generator intending to register as semi-scheduled must provide a completed Energy Conversion Model (ECM) data template to AEMO 3 months before participation in the market.
In the interest of maintaining accuracy of the wind generation forecasts, any material changes to the ECM data must be re-submitted to AEMO and at any other time on AEMO request.
Where relevant, the data entered into the ECM data template needs to be consistent with, or derived from, data in the Generating System Design Data Sheets and Generating System Setting Data Sheets, or as otherwise agreed with AEMO.

## Cluster Definition Guideline
A "cluster" corresponds to a group of wind turbines of similar type in the wind farm and within a reasonable geographic area. Please see the ‘Cluster definition guideline’ for more details. Participant to propose the cluster arrangement to AEMO for approval.
Cluster definition guideline
To define a “cluster” the ensemble of the following constraints should be roughly satisfied :
i. no more than 7 km x 7 km (with some degree of flexibility)
ii. only identical turbines are included in a cluster
NOTE: Identical turbines means turbines supplied by same manufacturer, having the same model, hub height and characteristic power curve.
The factors that are expected to affect the definition of such clusters are :
· Important changes in the terrain complexity throughout the area covered by the wind farm
· Changes in the meteorology due to the size of the area covered (presence of local patterns)
· Physical separation of parts of the wind farm (considerable distance between groups of wind turbines)
· Different timing in the development/commissioning of parts of the wind farm
· Different types of wind turbines in the wind farm (model, hub height)
· More than one connection points to the grid

## ECM Data Template
Energy Conversion Model for Wind Farms: |  |  |  |  | Please submit completed ECM to op.forecasting@aemo.com.au
Data Type | Units | Required | Value | Comments | Description
Wind farm identification
Name | n/a | Yes |  |  | Name of the wind farm. To be same as specified in the Registration process.
DUID | n/a | Yes |  |  | DUID of the wind farm to be proposed by the participant. Maximum 8 characters allowed. Example - SYDNWIND. NOTE: DUID to be same as specified in the Registration process.
Region | n/a | Yes |  |  | Name of the Region where the wind farm is installed. Needs to be the same as specified in the Registration process.
Wind farm Status
Status of the wind farm | n/a | Yes |  |  | New future wind farm or extension of an existing wind farm?
From which date is or will the wind farm be fully operational? | Date | Yes |  |  | Provide the plan for progressive commissioning of the wind farm with expected dates of commissioning per wind turbine - as per Rules Cl 5.8.4
From which date will the wind farm be first connected to the grid or energised? | Date | Yes |  |  | Provide the date when the wind farm is expected to commence generation.
Wind farm nominal data
Nameplate Rating | MW | Yes |  |  | The total installed capacity of the Wind Farm (MW). This equals turbine nameplate rating x total number of turbines installed. This Item corresponds to "Nameplate Rating" in Sections C and I.5 of "Application for Registration as a Generator in the NEM."
Maximum Capacity | MW | Yes |  |  | Maximum generation to which the semi-scheduled generating unit may be dispatched. This definition can be found in sections C, I.4 and I.5 of "Application for Registration as a Generator in the NEM",
Wind farm location & terrain data
Geographical coordinates (UTM WGS-84) | n/a | No |  |  | Geographical coordinates of a representative point of the wind farm, example: UTM WGS84 Z55 E304898 N5489758
Geographical coordinates | Decimal Degrees Lat/Lon | Yes |  |  | Geographical coordinates of a representative point of the wind farm, example: -40.72067 / 144.68691
Wind farm altitude | m ASL | Yes |  |  | Representative value for the wind farm altitude (given as a unique value in m ASL [meters above sea level]). It should be average of ground altitude for turbine locations.
Wind farm geometry | map | Yes |  |  | Given as a map with marked wind turbines position (high resolution image/ PDF file)
Orography information | map | No |  |  | Given as a map of the wind farm area in numerical format with the highest available spatial resolution (recommended not inferior than 200 m) (e.g. WASP [Wind Atlas Analysis and Application Program] format)
Mesoscale roughness coefficient | m | Yes |  |  | Given as a unique representative value for the mesoscale roughness coefficient of the wind farm (meso z0)
Roughness of surrounding area | map | No |  |  | Given as a map in numerical format (e.g. WASP format) with the highest available spatial resolution (recommended not inferior than 200 m) or paper format (1:50000)
Met mast measuring height | m AGL | Yes |  |  | Description: If a met mast available, indicate the measuring height(s) above ground level. Example - Met mast (SCADA wind speed data) height: = met mast A=80m, met mast B=85m, met mast C=92m.
Met mast Geographical coordinates | Decimal Degrees Lat/Lon | Yes |  |  | Description: If a met mast available, indicate the geographical coordinates. Example - Met mast (SCADA wind speed data) coordinates = met mast A: (- 81.15611,122.47823) met mast B: (-81.15984,122.47159)
Air density | kg/m^3 | Yes |  |  | The typical air density at the level of this Wind Farm (yearly average). In case of multiple power curves the one that corresponds to this density is considered.
Wind Farm SCADA to AEMO: |  |  |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated at least every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, a maximum 15-second average update is required.
Wind farm active power | MW | Yes |  |  | Total wind farm active power.
Number of wind turbines available for generation data | no. | Yes |  |  | Number of turbines available for generation. This definition is the summation of: • Turbines operating • Turbines available to operate, but not operating due to ambient wind conditions (very low / high wind speeds, extreme direction change) • Turbines available to operate, but paused due to down regulation. This definition excludes all the following cases: • Turbines under maintenance or repair • Turbines with a fault or damage • Turbines not yet built • Transmission/distribution network not available If agreed with AEMO, turbines paused due to ambient temperature may be counted as available in this signal.
Number of wind turbines actively generating | no. | Yes |  |  | Number of turbines actively generating power
Local Limit | MW | Yes, unless otherwise agreed by AEMO |  |  | In MW, the SCADA Local Limit for a wind farm is the lower of its plant availability and all technical limits on the capacity of its connection assets to export energy. When implemented in AWEFS, the SCADA Local Limit is used to cap the UIGF for the wind farm in the dispatch timeframe. The SCADA Local Limit excludes limits on a transmission network and distribution network (to ensure AEMO’s compliance with clause 3.7B(c)(6) of the Rules), and may exclude other limits managed by AEMO through the central dispatch process. Limits already communicated in the SCADA Turbines Available signal may be excluded from the SCADA Local Limit. Manually-applied transient limits not intended to apply at the end of the next dispatch interval may be excluded from the SCADA Local Limit. The SCADA Local Limit should not exceed the higher of the nameplate rating and the Maximum Capacity of the wind farm.
Estimated Power | MW | No |  |  | SCADA Estimated Power is the Generator’s forecast in MW of active power at the end of the next dispatch interval, subject only to technical factors affecting operation of its generation and connection assets. SCADA Estimated Power should be calculated assuming that no distribution or transmission network constraints apply to the next dispatch interval, and may assume that other limits managed by AEMO through the central dispatch process do not apply to the next dispatch interval. The SCADA Estimated Power should not exceed the higher of the nameplate rating and the Maximum Capacity of the wind farm. Implementation of this parameter is dependent on AEMO being satisfied that its accuracy and implementation concerns are addressed. AEMO will then issue a market notice to this effect and post it on its website. After implementation, AEMO will retain discretion to reject data that does not pass its initial and ongoing validation and accuracy assessment.
Wind speed data | m/s | Yes |  |  | Measurements from turbine nacelle anemometers are much preferred over measurements from meteorological mast(s). SCADA Wind Speed – Farm level is a single wind speed measurement, which must be representative of wind conditions across the site for calculation of dispatch UIGF. For large wind farms, an average of several turbine nacelle wind speed measurements may be used to achieve this. Ideally this average is of all turbine nacelles, or of several geographically-distributed meteorological masts. The measurement is considered representative if, on the advice of the AWEFS vendor, the wind speed measurement is sufficiently stable and there is adequate correlation between the wind speed measurement and the farm’s active power output when not downregulated.
Wind direction data | º | Yes |  |  | Wind direction measurements from turbine nacelle anemometers much preferred over measurements from meteorological mast(s). Wind direction from selected single representative nacelle (no averaging for direction).
Temperature data | ºC | Yes |  |  | Ambient temperature. Also provide the height at which this is measured.
Wind Farm Control System Set-Point | MW | Yes |  |  | MW set-point applied in the wind farm's control system to limit (down regulate) its output. At other times when no limit applies, the set-point to be set to above the wind farm's Nameplate Rating, but below 250% of it.
Pressure or humidity data | hPa, %RH | No |  |  | Also provide the height at which this is measured.
SCADA data available from this wind farm | n/a | Yes |  |  | SCADA readings not listed above, if any, to be provided as per National Electricity Rules S5.2.6.
Provide historical SCADA measurements since the beginning of operation of the wind farm | n/a | Yes |  |  | Only applicable if an operational wind farm is registered as a scheduled or semi-scheduled generator or a Non-scheduled generating unit expanding to >= 30MW Nameplate Rating and thereby creating a need for their output to be forecast. Time resolution should be same as current SCADA, If this time resolution is not availabe, 1 minute averages will suffice.
Ends

## ECM Data Template Cluster
Energy Conversion Model for Wind Farms: |  |  |  |  | Please submit completed ECM to op.forecasting@aemo.com.au
Data Type | Units | Required | Value | Comments | Description
Cluster Standing Data: | Parameters that apply to a cluster Please copy this section of the sheet for each cluster |  |  |  | A "cluster" corresponds to a group of wind turbines of similar type in the wind farm and within a reasonable geographic area. Please see the ‘Cluster definition guideline’ for more details. Participant to propose the cluster arrangement to AEMO for approval. If there are more than one such clusters, please repeat the following table in a seperate tab.
Cluster identification
ID of this Wind Turbines Cluster | n/a | Yes |  |  | Unique ID of the cluster of wind turbines in the farm to be provided by the participant. Maximum 10 characters allowed. Example- SYDWND_CL1. Cluster ID to be same as specified in the Registration process.
Cluster characteristics
Number of Wind Turbines in the Cluster | no. | Yes |  |  | Number of identical machines proposed in the cluster. This should be consistent with information provided in Generating System Design Data Sheets section 7, page 21
Type of Turbines in the Cluster | n/a | Yes |  |  | Type of the wind turbines proposed in the cluster. Mark the commercial wind turbine reference example - VESTAS V66 1.75 MW. This should be consistent with information provided in Generating System Design Data Sheets section 7, page 21
Hub height of wind turbines in the Cluster | m | Yes |  |  | The hub height of this type of wind turbines
Rotor diameter | m | Yes |  |  | Rotor Diameter of the turbine
Manufacturers' power vs wind speed characteristic curve | n/a | Yes |  |  | Provide the characteristic curve of the type of wind turbines in this cluster using the turbine curves table attached. This is the basic power curve provided by the manufacturer.
Directional power curves | n/a | No |  |  | These are characteristic curves that give the power output of the wind farm cluster as a function of wind speed and wind direction. Such curves are dependent on the specific wind farm cluster as they account for wake effects. Please provide in separate file (e.g. WASP format). This should be consistent with information provided in Generating System Design Data Sheets section 12.4.1 page 58 - power curve
Manufacturer's thrust coefficient vs wind speed characteristic curve | n/a | Yes |  |  | Provide the characteristic curve of the thrust coefficient of each type of wind turbines in this cluster using the turbine curves table attached. This parameter is used to calculate wake effects in some physical forecasting models.
Turbine Nameplate Rating | kW | Yes |  |  | The nameplate rating of that type of turbine (kW). This should be consistent with information provided in Generating System Design Data Sheets section 7.1.1, page 21
Maximum Power | kW | Yes |  |  | The maximum power a turbine of that type can produce (kW). This should be consistent with information provided in Generating System Design Data Sheets section 7.1.1, page 21
Operation in ambient temperature range | ºC | Yes |  |  | Temperature Range of turbine operation, example -20 to 40 degree C
Wind Turbine Cut-out Temperature / Automatic Stop limit due to high temperature | ºC | Yes |  |  | For cases where the wind turbine need to be stopped during certain high temperatures. This should be consistent with information provided in Generating System Design Data Sheets section 7.1.1, page 21. Temperature threshold and associated time delay also to be provided, if available in technical specification of the Turbine.
Wind Turbine Cut-in Temperature / Automatic re-enter in operation after cut-out due to high temperatures | ºC | Yes |  |  | Temperature where the wind turbine gets back in operation after a cut-off due to high temperature.
Wind Turbine Cut-out Temperature / Automatic Stop limit due to very low negative temperatures | ºC | Yes |  |  | For cases where the wind turbine need to be stopped during certain low negative temperatures
Wind Turbine Cut-in Temperature / Automatic re-enter in operation after cut-out due to very low negative temperatures | ºC | Yes |  |  | Temperature where the wind turbine gets back in operation after a cut-off due to low negative temperatures.
Rated Speed | m/s | Yes |  |  | The rated speed (m/sec) of that type of turbine, i.e. the wind speed at which full power is attained. This should be consistent with information provided in Generating System Design Data Sheets section 12.4.1, page 57 - "speed at which full power is attained"
Cut-in Speed | m/s | Yes |  |  | Minimum wind speed at which the wind turbine starts to produce power. This should be consistent with information provided in Generating System Design Data Sheets section 12.4.1, page 57
Cut-out Speed | m/s | Yes |  |  | Minimum wind speed at which the wind turbine is stopped to avoid damage at high wind speeds. This should be consistent with information provided in Generating System Design Data Sheets section 12.4.1, page 57
Cut-out Speed - other measurements | m/s | No |  |  | Type of wind speed measurement on which cut-out is triggered (e.g. 2 min, 10 min, gusting average wind speeds). Repeat if several measurements available.
Restart after cut-out Wind Speed | m/s | Yes |  |  | Maximum wind speed at which the wind turbine can re-enter operation after being cut-out due to too high wind speeds.
Restart after cut-out Wind Speed - other measurements | n/a | No |  |  | Type of maximum wind speed measurement on which wind turbine can re-enter operation after cut-out due to too high wind speeds (e.g. 2 min, 10 min, gusting average wind speeds). Repeat if several measurements available.
Cluster characteristics
Imposed noise level restrictions | DB | No |  |  | For cases where Wind Turbines should operate at a specific noise mode. The appropriate power curve is then selected.
Manufacturers' power vs wind speed characteristic curve as a function of noise level | n/a | No |  |  | If restrictions apply due to noise, the manufacturer's characteristic wind speed vs power curves of the wind turbines for different noise levels should be provided using the table provided for each noise level.
Legal start night time | Time | No |  |  | For cases where Wind Turbines stop or run on a special power curve (indicate curve) during night hours for noise reduction or other reasons.
Legal ending night time | Time | No |  |  | For cases where Wind Turbines stop or run on a special power curve (indicate curve) during night hours for noise reduction or other reasons.
NSP MW Control Schemes in operation | n/a | Yes |  |  | Provide details of NSP MW Control Schemes used to down regulate the wind farm at wind farm and/or cluster level.
Any other restrictions | n/a | Yes |  |  | Provide details of any other limitations imposed on the Wind Farm. This should be consistent with information provided in Generating System Design Data Sheets section 6.1.2, page 20, and Data Sheets section 7.1.2, page 22
Cluster SCADA |  |  |  |  | Instantaneous measurements are required, unless otherwise agreed by AEMO. Instantaneous means values updated every 4-10 seconds, with 4 seconds or faster preferred. If only averages are available, maximum 15-second average update is required.
Cluster active power | MW | Yes |  |  | Total cluster active power
Number of wind turbines available for generation data | No. | Yes |  |  | Number of turbines available for generation. This definition is the summation of: • Turbines operating • Turbines available to operate, but not operating due to ambient wind conditions (very low / high wind speeds, extreme direction change) • Turbines available to operate, but paused due to down regulation. This definition excludes all the following cases: • Turbines under maintenance or repair • Turbines with a fault or damage • Turbines not yet built • Transmission/distribution network not available If agreed with AEMO, turbines paused due to ambient temperature may be counted as available in this signal.
Number of wind turbines actively generating | No. | Yes |  |  | As number of turbines actively generating power.
Turbines Extreme Wind Cut-out | No. | Yes, unless otherwise agreed by AEMO. |  |  | This is the number of turbines counted in the Turbines Available signal that are currently in cut-out mode due to extreme high wind speed or extreme wind direction change. If agreed with AEMO, this signal may be provided at a farm level. If agreed with AEMO, extreme wind direction change may be excluded.
Wind speed data | m/s | Yes |  |  | Measurements from turbine nacelle anemometers much preferred over measurements from meteorological mast(s). Also provide the height at which this is measured.
Wind direction data | º | Yes |  |  | Wind direction measurements from turbine nacelle anemometers much preferred over measurements from meteorological mast(s) Also provide the height at which this is measured.
Wind turbines location
Geographical coordinates of Wind Turbine #1 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #2 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #3 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #4 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #5 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #6 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #7 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #8 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #9 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #10 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #11 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #12 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #13 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #14 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #15 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #16 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #17 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #18 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #19 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Geographical coordinates of Wind Turbine #20 | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Add more if required | Coordinates in UTM WGS-84 or Latitude/ Longitude | Yes
Ends

## Turbine Curves Table
Wind Turbine Characteristic Curves
Please repeat the following table for each type of wind turbines.
Repeat the table if for a wind turbine type a different characteristic curve is available for different values of air density and/or for operation at different noise modes (in case that noise restrictions apply).
The wind speed increment should be in the order of 0.5-1.0 m/s
Type of wind turbine:
Air density (kg/m3):?
Noise mode dB (A): ?
| Speed (m/s) | Power (kW) | Speed (m/s) | Thrust coeff. Ct