## Queensland Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer on the 'Disclaimer' tab of this workbook.
Queensland Summary
Committed project developments
Kogan Creek Solar Boost: CS Energy advises that the Kogan Creek Solar Boost project (44 MW) is now a committed project and due to be completed in July 2015. Note that the 44 MW capacity is not additional to the 730/744 MW summer/winter capacities of Kogan Creek, rather it is a contribution towards the total generation.
Plant retirements
Collinsville Power Station: Ratch Australia advised that Collinsville power station will be retired in June 2016.
Mackay GT Power Station: Stanwell Corporation advised that Mackay GT will be retired at the end of 2016.
Daandine Power Station: Energy infrastructure Investments Pty Ltd advised that Daandine power station will be retired in June 2022.
Mt Stuart Power Station: Origin Energy Mt Stuart advised that Mt Stuart power station will be retired at the end of 2023.
Changes since the 2013 ESOO (existing generation)
Swanbank E Gas Power Station: Stanwell Corporation advises that the existing scheduled Swanbank E Gas Power Station (385 MW combined cycle gas turbine) will be placed in cold storage from December 2014.
Tarong Power Station: Stanwell Corporation advises that the Tarong station will revise its available capacity from 700 MW to 1050 MW (+350 MW) in summer 2014, due to the return of service of Unit 4 (DUID TARONG#4) in July 2014. The avaible capacity will be revised to 1400 MW (+350 MW) in summer 2015, due to the return of service of Unit 2 (DUID TARONG#2) in June 2015.
Plant limitations
AEMO has not been advised of any plant limitations in Queensland for the 10-year planning outlook.
Queensland existing and potential new developments by generation type (MW) data
Status / Type | Coal | CCGT | OCGT | Gas other | Solar | Wind | Water | Biomass | Geo-thermal | Other
Existing | 7866 | 1242 | 1103 | 30 | 0.4 | 12 | 664 | 364 | 0 | 879
Committed | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
Publicly announced | 0 | 0 | 2545 | 0 | 679 | 1999 | 200 | 158 | 0 | 0
Withdrawn | 540 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queensland existing and potential new developments by generation type (MW)

## Change Log
Queensland Change Log
Lists all key updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Solar Dawn Project: Areva and the Solar Dawn Consortium advised it would no longer develop the proposed 250 MW solar thermal power facility in South-West Queensland.
Tarong Power Station: Stanwell Corporation advises that the Tarong plant has revised its available capacity from 1,400 MW to 700 MW (-700 MW) in summer and winter, due to the withdrawal of service of Unit 2 (DUID TARONG#2) in October 2012 and Unit 4 (DUID TARONG#4) in December 2012, both for a period of at least two years or until wholesale electricity demand improves.
Collinsville Power Station: Ratch Australia advises that the Collinsville plant has revised its available capacity from 190 MW to 0 MW (-190 MW) in summer and winter, due to the withdrawal of service of all generation units from 31 December 2012, until wholesale electricity demand improves.
Publication Date: | 2013-02-22
Millmerran Power Station: Millmerran Power Partners advises that the Millmerran plant has revised its available capacity from 856 MW to 760 MW (-96 MW) in summer, based on operating experience on higher temperature days.
Braemar Power Station: Alinta Energy advises that Braemar's available capacity has been revised from 435 MW to 480 MW (+45 MW) in summer, due to use of Evaporative Cooling and Peak Firing of the units.
Publication Date: | 2013-06-30
Braemar Power Station: Alinta Energy advises that Braemar's available capacity has been revised from 435 MW to 465 MW (+30 MW) in summer (an increase from last years ESOO), due to the regular use of Evaporative Cooling and Peak Firing of the units. These modes of operation result in the units achieving higher levels of output than would be typically expected during periods of high temperature.
Darling Downs Power Station: Alinta Energy advises that Darling Downs available capacity has been revised from 605 MW to 580 MW (-25 MW) in summer, reflecting capability at higher temperatures.
Kogan Creek Solar Boost: CS Energy advises that the Kogan Creek Solar Boost project is now a committed project and due to be completed in Jan 2014.
Publication Date: | 2013-11-15
Westlink Power Project: Westlink Pty Ltd as trustee for Westlink Industrial Trust advised that Westlink Power Project (Stage 1-3 up to 1000 MW), has revised construction start estimates by 1 year – from 2015 to 2016 for stage 1, from 2017 to 2018 for stage 2 and from 2019 to 2020 for stage 3. This remains a publicly announced project only.
Publication Date: | 2014-02-28
Swanbank E Gas Power Station: Stanwell Corporation advises that the existing scheduled Swanbank E Gas Power Station (385 MW combined cycle gas turbine) will withdraw from service for up to three years from 1 October 2014.
Publication Date: | 2014-05-30
Collinsville Power Station: Ratch Australia advised that Collinsville power station will be retired in June 2016.
Daandine Power Station: Energy infrastructure Investments Pty Ltd advised that Daandine power station will be retired in June 2022.
Mt Stuart Power Station: Origin Energy Mt Stuart advised that Mt Stuart power station will be retired in July 2023.
Swanbank E Gas Power Station: Stanwell Corporation advises that the existing scheduled Swanbank E Gas Power Station (385 MW combined cycle gas turbine) will be placed in cold storage from October 2014.
Tarong Power Station: Stanwell Corporation advises that the Tarong station will revise its available capacity from 700 MW to 1050 MW (+350 MW) in summer 2014, due to the return of service of Unit 4 (DUID TARONG#4) in July 2014. The avaible capacity will be revised to 1400 MW (+350 MW) in summer 2015, due to the return of service of Unit 2 (DUID TARONG#2) in June 2015.
Kogan Creek Solar Boost: CS Energy advises that the Kogan Creek Solar Boost project (44 MW) is now a committed project and due to be completed in July 2015. Note that the 44 MW capacity is not additional to the 730/744 MW summer/winter capacities of Kogan Creek, rather it is a contribution towards the total generation.
Publication Date: | 2014-08-07
Kidston Pumped Storage Hydro Project: Genex Power announces the Kidston Pumped Hydo Storage (200 MW) project in far north Queensland.
Cook Shire Solar Project: Lyon Infrastructure announces the Cook Shire Solar (26 MW) project in far north Queensland. Construction is to commence in December 2014 and commissioning is planned for July 2015.
Publication Date: | 2014-12-10
Swanbank E Gas Power Station: Stanwell Corporation advises that the existing scheduled Swanbank E Gas Power Station (385 MW combined cycle gas turbine) will be placed in cold storage from December 2014.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Barcaldine Power Station | Ergon Energy Queensland Pty Ltd | 1 x 37 1 x 18 | 55 | CCGT | Natural Gas Pipeline | S
Barron Gorge | Stanwell Corporation Limited | 2 x 33 | 66 | Run of River | Water | S
Braemar | Braemar Power Project Pty Ltd | 3 x 168 | 504 | OCGT | Coal Seam Methane | S
Braemar 2 | NewGen Braemar 2 Partnership | 3 x 173 | 519 | OCGT | Coal Seam Methane | S
Callide B | CS Energy | 2 x 350 | 700 | Steam Sub Critical | Black Coal | S
Callide C | Callide Power Management | 2 x 450 | 900 | Steam Super Critical | Black Coal | S
Collinsville | Ratch Australia | 2 x 31.5 2 x 30.5 1 x 66 | 190 | Steam Sub Critical | Black Coal | S
Condamine A | QGC | 1 x 144 | 144 | CCGT | Coal Seam Methane | S
Darling Downs | Origin Energy Power Limited | 1 x 280 3 x 121.5 | 644.5 | CCGT | Coal Seam Methane | S
Gladstone | Gladstone Power Station Participants | 6 x 280 | 1680 | Steam Sub Critical | Black Coal | S
Kareeya | Stanwell Corporation Limited | 4 x 21.6 | 86.4 | Run of River | Water | S
Kogan Creek | CS Energy | 1 x 744 | 744 | Steam Super Critical | Black Coal | S
Mackay GT | Stanwell Corporation Limited | 1 x 34 | 34 | OCGT | Diesel | S
Millmerran | Millmerran Power Partners | 2 x 426 | 852 | Steam Super Critical | Black Coal | S
Mt Stuart | Origin Energy Mt Stuart | 2 x 146 1 x 131.5 | 423.5 | OCGT | Kerosene Aviation fuel used for stationary energy | S
Oakey | Oakey Power Holdings | 2 x 140.9 | 281.8 | OCGT | Diesel | S
Roma | Origin Energy Power Limited | 2 x 40 | 80 | OCGT | Natural Gas Pipeline | S
Stanwell | Stanwell Corporation Limited | 4 x 365 | 1460 | Steam Sub Critical | Black Coal | S
Swanbank E GT | Stanwell Corporation Limited | 1 x 385 | 385 | CCGT | Coal Seam Methane | S
Tarong | Stanwell Corporation Limited | 4 x 350 | 1400 | Steam Sub Critical | Black Coal | S
Tarong North | Stanwell Corporation Limited | 1 x 450 | 450 | Steam Super Critical | Black Coal | S
Wivenhoe | CS Energy | 2 x 250 | 500 | Pump Storage | Water | S
Townsville Power Station | Ratch Australia | 1 x 160 1 x 84 | 244 | CCGT | Coal Seam Methane | S
Total |  |  | 12343.2

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – Queensland (MW)
Power Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Barcaldine | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | S
Barcaldine Power Station | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | S
Barron Gorge | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | S
Braemar | 465 | 465 | 465 | 465 | 465 | 465 | 465 | 465 | 465 | 465 | S
Braemar 2 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | 495 | S
Callide B | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | S
Callide C | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | S
Collinsville | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Condamine A | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Darling Downs | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | S
Gladstone | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | S
Kareeya | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | S
Kogan Creek | 720 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | S
Mackay GT | 34 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Millmerran | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760 | S
Mt Stuart | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | 379.2 | S
Oakey | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | 281.8 | S
Roma | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | S
Stanwell | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | S
Swanbank E GT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tarong | 1050 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Tarong North | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | S
Townsville Power Station | 235 | 234 | 234 | 233 | 233 | 233 | 232 | 232 | 232 | 232 | S
Wivenhoe | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | S
Total | 11067.4 | 11426.4 | 11426.4 | 11391.4 | 11391.4 | 11391.4 | 11390.4 | 11390.4 | 11390.4 | 11390.4

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation – Queensland (MW)
Project Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Barcaldine Power Station | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | S
Barron Gorge | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | S
Braemar | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | 504 | S
Braemar 2 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | 519 | S
Callide B | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | S
Callide C | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | S
Collinsville | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Condamine A | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Darling Downs | 633 | 633 | 633 | 633 | 633 | 633 | 633 | 633 | 633 | 633 | S
Gladstone | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | 1680 | S
Kareeya | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | 86.4 | S
Kogan Creek | 744 | 744 | 744 | 744 | 744 | 744 | 744 | 744 | 744 | 744 | S
Mackay GT | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Millmerran | 852 | 852 | 852 | 852 | 852 | 852 | 852 | 852 | 852 | 852 | S
Mt Stuart | 419 | 419 | 419 | 419 | 419 | 419 | 419 | 419 | 419 | 419 | S
Oakey | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | S
Roma | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | S
Stanwell | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | 1460 | S
Swanbank E GT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Tarong | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Tarong North | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | S
Townsville Power Station | 243 | 243 | 243 | 243 | 243 | 243 | 242 | 242 | 242 | 242 | S
Wivenhoe | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | S
Total | 11772.4 | 11772.4 | 11738.4 | 11738.4 | 11738.4 | 11738.4 | 11737.4 | 11737.4 | 11737.4 | 11737.4

## New Developments
Projects under development – Queensland
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW)a | Dispatch Type | Commissioning Start Date
Archer Point | Wind Power Queensland Pty Ltd | 1-60 | Wind | Wind - Onshore | [5 empty] | Pub An | 120 | SS | 2016-12-31
Bowen | Ratch Australia | 1-60/80 | Wind | Wind - Onshore | [5 empty] | Pub An | 120-240 | SS | TBA
Braemar 3 | ERM Power Limited | 1-2 | Coal Seam Methane | OCGT | ü |  |  |  |  | Pub An | 550 | S | TBA
Braemar 4 | ERM Power Limited | 1-3 | Coal Seam Methane | OCGT | ü |  |  |  |  | Pub An | 495 | S | TBA
Cloncurry Solar Farm | Infigen Energy | 1 | Solar | PV panels | [5 empty] | Pub An | 3-6 | NS | TBA
Collinsville PV | Ratch Australia | All Units | Solar | PV panels | ü |  | ü |  |  | Pub An | 23 | NS | 2015-12-31
Cook Shire Solar Project | Lyon Infrastructure | 1 | Solar | PV panels | [5 empty] | Pub An | 26 | NS | 2015-07-01
Coopers Gap | Coopers Gap Wind Farm Pty Ltd | 1 - 115 | Wind | Wind - Onshore | [5 empty] | Pub An | 350 | SS | TBA
Crediton | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 40-90 | SS | TBA
Crows Nest | AGL Energy | 1-67 | Wind | Wind - Onshore | [5 empty] | Pub An | 200 | SS | TBA
Darling Downs 2 | Origin Energy | 1-4 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 500 | S | TBA
Forsayth Wind Farm | Infigen Energy | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 75 | SS | TBA
High Road | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 34 | SS | 2018-04-01
Kennedy Wind Farm | Windlab Developments | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | 650 | SS | TBA
|  | All Units | Solar | PV panels | [5 empty] | Pub An | 650 | SS | TBA
Kidston Pumped Storage Hydro Project | Genex Power | 1 | Water | Pump Storage | [5 empty] | Pub An | 200 | S | TBA
Kogan Creek | CS Energy | 1 | Solar | Solar Thermal | ü | ü | ü | ü | ü | Com | 44 | S | 2015-07-01
Mt Cotton Biomass Cogeneration Power Station | Darwalla Milling Co Pty Ltd | 1 | Wood Waste | Steam Sub Critical | ü |  |  |  |  | Pub An | 7.6 | S | TBA
Mt Emerald | Ratch Australia | Units 1-70 | Wind | Wind - Onshore | [5 empty] | Pub An | 210 | SS | 2018-03-31
North Qld Bio-Energy Plant | North Queensland Bio-Energy Corporation Limited | 1-3 | Bagasse | Steam Sub Critical |  |  |  |  | ü | Pub An | 120 to 150 | S | 2017-09-01
Westlink Power Project | Westlink Pty Ltd as trustee for Westlink Industrial Trust | 1-2 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | Up to 1000 developed over three stages | S | 2018-06-30
|  | 3-4 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | Up to 1000 developed over three stages | S | 2020-06-30
|  | 5-6 | Natural Gas Pipeline | OCGT | ü |  |  |  |  | Pub An | Up to 1000 developed over three stages | S | 2022-06-30
Windy Hill II | Ratch Australia | Station | Wind | Wind - Onshore | [5 empty] | Pub An | 10-30 | NS | 2019-09-01
a. Where the proponent has provided a range of nameplate capacities, the upper bound has been used in any total calculations

## Existing NS Generation
Existing non-scheduled generation – Queensland
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type
Birkdale | LMS ENERGY Pty Ltd | 0.75 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Browns Plains | EDL LFG Qld Pty Ltd | 2.18 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Callide A | Oxyfuel Technologies Pty Ltd | 30 | Steam Sub Critical | Black Coal
Daandine | Energy infrastructure Investments Pty Ltd | 30 | Compression Reciprocating Engine | Coal Seam Methane
FPC Green Energy | FPC 30 Limited as Trustee for FPC Green Fund Trust | 30 | Steam Sub Critical | Green and air dried wood
Fraser Coast Community Solar Farm | Wide Bay Water Corporation | 0.401 | PV panels | Solar
German Creek | EDL CSM Qld Pty Ltd | 45.01 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas
Inkerman Mill | Pioneer Sugar Mills P/L | 10.5 | Steam Sub Critical | Bagasse
Invicta Mill | The Haughton Sugar Company P/L | 50.3 | Steam Sub Critical | Bagasse
ISIS Central Sugar Mill Co-generation Plant | AGL Energy | 25 | Steam Sub Critical | Bagasse
Kalamia Mill | Wilmar Sugar P/L | 9 | Steam Sub Critical | Bagasse
Kareeya 5 | Stanwell Corporation Limited | 7 | Hydro - Gravity | Water
Macknade Mill | Wilmar Sugar P/L | 8 | Steam Sub Critical | Bagasse
Maryborough | MSF Sugar | 7.5 | Steam Super Critical | Bagasse
Moranbah Generation Project | AGL | 12.56 | Compression Reciprocating Engine | Waste Coal Mine Gas
Moranbah North | EDL Projects Australia Pty Ltd | 45.6 | Spark Ignition Reciprocating Engine | Waste Coal Mine Gas
Mulgrave | MSF Sugar | 13 | Steam Super Critical | Bagasse
Oaky Creek | Envirogen Oaky Pty Ltd | 20.84 | Compression Reciprocating Engine | Waste Coal Mine Gas
Pioneer Sugar Mill | Pioneer Sugar Mills P/L | 67.8 | Steam Sub Critical | Bagasse
Plane Creek Mill | Wilmar Sugar Plane Creek P/L | 14 | Steam Sub Critical | Bagasse
Proserpine | Wimar Sugar Proserpine Pty Ltd | 17 | Steam Sub Critical | Bagasse
Racecourse Mill | Mackay Sugar Ltd | 48 | Steam Sub Critical | Bagasse
Rochedale Renewable Energy Facility | LMS Generation | 4.158 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Roghan Road | EDL LFG Qld Pty Ltd | 1.15 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
South Johnstone | MSF Sugar | 19.3 | Steam Sub Critical | Bagasse
Southbank Institute of Technology Unit 1 Plant | Southbank Institute of Technology | 1 | Compression Reciprocating Engine | Diesel
Suncoast Gold Macadamias | AGL | 0 | Steam Sub Critical | Macadamia Nut Shells
Swanbank JV | LMS ENERGY Pty Ltd | 1.123 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Tableland | MSF Sugar | 7 | Steam Super Critical | Bagasse
Tarong GT | Stanwell Corporation Limited | 15 | OCGT | Fuel Oil
Ti Tree Bioenergy | Ti Tree Bioenergy | 3.3 | Compression Reciprocating Engine | Landfill Methane / Landfill Gas
Victoria Mill | Wilmar Sugar Herbert P/L | 24 | Steam Sub Critical | Bagasse
Whitwood Road | LMS Energy Pty Ltd | 1.123 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Windy Hill | Ratch Australia | 12 | Wind - Onshore | Wind
Wivenhoe Small Hydro | Stanwell Corporation Limited | 4.5 | Hydro - Gravity | Water
Yarwun 1 | RTA Yarwun Pty Ltd | 154 | CCGT | Natural Gas Pipeline
Total |  | 742.095

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless classified as semi-scheduled, or AEMO is permitted to classify it as non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW and equal to or greater than 5 MW.
Generating systems greater than 30 MW may be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating less than 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.

## Disclaimer
Important Notice
Purpose
The purpose of this publication is to provide technical, market data and information regarding opportunities in the National Electricity Market.
AEMO publishes the Electricity Statement of Opportunities in accordance with clause 3.13.3(q) of the National Electricity Rules (Rules). This publication has been prepared by AEMO using information available at 31 July 2014, unless otherwise specified. Information made available after 31 July 2014 may have been included in this publication where practical.
Disclaimer
AEMO has made every effort to ensure the quality of the information in this publication but cannot guarantee that information, forecasts and assumptions are accurate, complete or appropriate for your circumstances. This publication does not include all of the information that an investor, participant or potential participant in the National Electricity Market might require, and does not amount to a recommendation of any investment.
Anyone proposing to use the information in this publication (including information and reports from third parties) should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this publication:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this publication; and
· are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this publication.
Acknowledgement
AEMO acknowledges the support, co-operation and contribution of all participants in providing data and information used in this publication.
Copyright
© 2014 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.