## Tasmania Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer on the 'Disclaimer' tab of this workbook.
Tasmania Summary
Committed project developments
AEMO has not been advised of any committed projects in Tasmania within the 10-year planning outlook.
Plant retirements
AEMO has not been advised of any planned plant retirements in Tasmania within the 10-year planning outlook.
Changes since the 2012 ESOO (existing generation)*
Musselroe Wind Farm: Hydro Tasmania Wind Operations Pty Ltd advises that Musselroe (168 MW) project was completed in June 2013.
Poatina Power Station: Hydro-Electric Corporation advises that Poatina station available capacity changed from 300 MW to 342 MW (+42 MW) to be consistent with MTPASA values rather than registered nameplate capacity.
* Note that the Tungatinah upgrades reported in the change log do not impact available capacity.
Plant limitations
Bastyan Power Station: Hydro-Electric Corporation advises that Bastyan's available capacity will be (zero) 0 MW during summer 2019-20.
Catagunyah/Liapootah/Wayatinah Power Station: Hydro-Electric Corporation advises that Catagunyah/Liapootah/Wayatinah stations will undergo the following outages:
· Liapootah Unit 1 will be unavailable during:
- summer 2017–18
· Liapootah Unit 2 will be unavailable during:
- summer 2018–19
· Liapootah Unit 3 will be unavailable during:
- summer 2016–17
· Wayatinah Unit 1 will be unavailable during:
- summer 2013–14
· Wayatinah Unit 2 will be unavailable during:
- summer 2013–14
- summer 2017–18
· Wayatinah Unit 3 will be unavailable during:
- summer 2013–14
- summer 2017–18
· Catagunya Unit 1 will be unavailable during:
- summer 2013–14
- summer 2017–18
· Catagunya Unit 2 will be unavailable during:
- summer 2018–19
Cethana Power Station: Hydro-Electric Corporation advises that Cethana’s available capacity will be (zero) 0 MW during summer 2014-15.
Devils Gate Power Station: Hydro-Electric Corporation advises that Devils Gate’s available capacity will be (zero) 0 MW during summer 2017-18.
Fisher Power Station: Hydro-Electric Corporation advises that Fisher’s available capacity will be (zero) 0 MW during summer 2016-17.
Gordon Power Station: Hydro-Electric Corporation advises that Gordon's available capacity will be limited to 288 MW, due to an outage to unit 3 during summer 2016-17.
Lake Echo Power Station: Hydro-Electric Corporation advises that Lake Echo's available capacity will be (zero) 0 MW during winter 2019.
Lemonthyme/Wilmot Power Station: Hydro-Electric Corporation advises that Lemonthyme/Wilmot's available capacity will be during summer 2018-19.
Mackintosh Power Station: Hydro-Electric Corporation advises that Mackintosh's available capacity will be (zero) 0 MW during summer 2020-21.
Meadowbank Power Station: Hydro-Electric Corporation advises that Meadowbank's available capacity will be (zero) 0 MW during winter 2014.
Tarraleah Power Station: Hydro-Electric Corporation advises that Tarraleah’s available capacity will be:
• 75 MW during summer 2013–14 due to outages of Unit 1.
• 45 MW during summer 2017–18 due to outages of Units 4-6.
Trevallyn Power Station: Hydro-Electric Corporation advises that Trevallyn’s available capacity will be:
• 82 MW during summer 2018–19 due to outages of Unit 1.
• 82 MW during summer 2019–20 due to outages of Unit 2.
Tungatinah Power Station: Hydro-Electric Corporation advises that Tungatinah’s available capacity will be:
• 75 MW during summer 2013–14 due to outages of Units 4-5.
• 100 MW during summer 2015–16 due to outages of Unit 3.
• 100 MW during summer 201–17 due to outages of Unit 4.
• 100 MW during winter 2017 due to outages of Unit 4.
Tasmania existing and potential new developments by generation type (MW) data
Project type | CCGT | OCGT | Gas other | Coal | Biomass | Geothermal | Water | Solar | Wind | Other
Publically Announced | 0 | 0 | 0 | 0 | 273 | 0 | 302 | 0 | 1319.7 | 0
Advanced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Committed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Existing | 208 | 178 | 4.936 | 0 | 0 | 0 | 2280.8 | 0 | 308 | 0
Tasmania existing and potential new developments by generation type (MW)

## Change Log
Tasmania Change Log
Lists all updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Tungatinah (Upgrade): Hydro-Electric Corporation advises the upgrade to Unit 1 is committed and scheduled to return to service in December 2012.
Publication Date: | 2013-02-22
Poatina Power Station: Hydro Tasmania advises that the Poatina plant has revised its available capacity from 300 MW to 342 MW (+42 MW) in summer and winter, based on operating experience.
Musselroe Wind Farm: Hydro Tasmania Wind Operations Pty Ltd advises that Musselroe (168 MW) is now a committed project. Construction is expected be completed around June 2013.
Publication Date: | 2013-06-30
Tungatinah (Upgrade): Hydro-Electric Corporation advises the upgrade to Unit 1 was completed and returned back to service on February 2013. The upgrade was a revamp of the unit where some efficiency gains are expected.
Tungatinah (Upgrade): Hydro-Electric Corporation advises an upgrade to Unit 2, a revamp of the existing unit where some efficiency gains are expected. The upgrade to be completed in November 2013.
Publication Date: | 2013-11-15
Musselroe Wind Farm: Hydro Tasmania Wind Operations Pty Ltd advises that Musselroe (168 MW) project was completed in June 2013.
TasWind (King Island): Hydro Tasmania advises that the TasWind (King Island) project is publically anounced.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Bastyan | Hydro-Electric Corporation | 1 x 79.9 | 79.9 | Hydro - Gravity | Water | S
Bell Bay Three | Aurora Energy Tamar Valley Pty Ltd | 3 x 40 | 120 | OCGT | Natural Gas Pipeline | S
Catagunya / Liapootah / Wayatinah | Hydro-Electric Corporation | 2 x 24 3 x 27.9 3 x 12.8 | 170.1 | Hydro - Gravity | Water | S
Cethana | Hydro-Electric Corporation | 1 x 85 | 85 | Hydro - Gravity | Water | S
Devils Gate | Hydro-Electric Corporation | 1 x 60 | 60 | Hydro - Gravity | Water | S
Fisher | Hydro-Electric Corporation | 1 x 43.2 | 43.2 | Hydro - Gravity | Water | S
Gordon | Hydro-Electric Corporation | 3 x 144 | 432 | Hydro - Gravity | Water | S
John Butters | Hydro-Electric Corporation | 1 x 144 | 144 | Hydro - Gravity | Water | S
Lake Echo | Hydro-Electric Corporation | 1 x 32.4 | 32.4 | Hydro - Gravity | Water | S
Lemonthyme / Wilmot | Hydro-Electric Corporation | 1 x 51 1 x 30.6 | 81.6 | Hydro - Gravity | Water | S
Mackintosh | Hydro-Electric Corporation | 1 x 79.9 | 79.9 | Hydro - Gravity | Water | S
Meadowbank | Hydro-Electric Corporation | 1 x 40 | 40 | Hydro - Gravity | Water | S
Musselroe | Woolnorth Wind Farm Holding Pty Ltd | 56 x 3 | 168 | Wind - Onshore | Wind | SS
Poatina | Hydro-Electric Corporation | 6 x 50 | 300 | Hydro - Gravity | Water | S
Reece | Hydro-Electric Corporation | 2 x 115.6 | 231.2 | Hydro - Gravity | Water | S
Tamar Valley Combined Cycle | Aurora Energy Tamar Valley Pty Ltd | 1 x 140 1 x 68 | 208 | CCGT | Natural Gas Pipeline | S
Tamar Valley Peaking | Aurora Energy Tamar Valley Pty Ltd | 1 x 58 | 58 | OCGT | Natural Gas Pipeline | S
Tarraleah | Hydro-Electric Corporation | 6 x 15 | 90 | Hydro - Gravity | Water | S
Trevallyn | Hydro-Electric Corporation | 2 x 20 2 x 26.5 | 93 | Hydro - Gravity | Water | S
Tribute | Hydro-Electric Corporation | 1 x 82.8 | 82.8 | Hydro - Gravity | Water | S
Tungatinah | Hydro-Electric Corporation | 5 x 25 | 125 | Hydro - Gravity | Water | S
Total |  |  | 2724.1

## Existing Wind Generation
Existing & committed wind generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Installed | Plant Type | Fuel | Dispatch Type
Capacity (MW)
Woolnorth Studland Bay / Bluff Point | Woolnorth Wind Farm Holding Pty Ltd | 25 x 3 37 x 1.75 | 140 | Wind - Onshore | Wind | NS
Musselroe | Woolnorth Wind Farm Holding Pty Ltd | 56 x 3 | 168 | Wind - Onshore | Wind | SS
Total |  |  | 308

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – Tasmania (MW)
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 20212 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Bastyan | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 0 | 79.9 | 79.9 | 79.9 | S
Bell Bay Three | 120.1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | S
Catagunya / Liapootah / Wayatinah | 112 | 179 | 179 | 150 | 111 | 111 | 179 | 179 | 179 | 179 | S
Cethana | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | S
Devils Gate | 62 | 62 | 62 | 62 | 0 | 62 | 62 | 62 | 62 | 62 | S
Fisher | 45 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | S
Gordon | 444 | 444 | 444 | 296 | 444 | 444 | 444 | 444 | 444 | 444 | S
John Butters | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Lake Echo | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | S
Lemonthyme / Wilmot | 86 | 86 | 86 | 86 | 86 | 0 | 86 | 86 | 86 | 86 | S
Mackintosh | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 0 | 83 | 83 | S
Meadowbank | 42 | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | S
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS
Poatina | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | S
Reece | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | S
Tamar Valley Combined Cycle | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 75 | 90 | 90 | 90 | 45 | 90 | 90 | 90 | 90 | 90 | S
Trevallyn | 103 | 103 | 103 | 103 | 103 | 82 | 82 | 103 | 103 | 103 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | S
Tungatinah | 75 | 125 | 100 | 100 | 125 | 125 | 125 | 125 | 125 | 125 | S
Total | 2698 | 2644.9 | 2804.9 | 2627.9 | 2654.9 | 2654.9 | 2729 | 2746.9 | 2829.9 | 2829.9
The table above lists the latest summer capacities for Tasmanian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2013–14 these figures have been updated to 4.2% of the installed capacity during summer, and 2.5% during winter compared to the 2011–12 contribution factors.
The two tables below have been included to better represent supply availability in South Australia, by taking into account the firm contribution by wind. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Summer total available semi-scheduled capacity by power station table lists the total available capacity for semi-scheduled wind generation for the summer period. The total available refers to the maximum amount that the wind farms can generate at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation – Tasmania (MW)
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 20212 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Bastyan | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 0 | 79.9 | 79.9 | 79.9 | S
Bell Bay Three | 120.1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | S
Catagunya / Liapootah / Wayatinah | 112 | 179 | 179 | 150 | 111 | 111 | 179 | 179 | 179 | 179 | S
Cethana | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | S
Devils Gate | 62 | 62 | 62 | 62 | 0 | 62 | 62 | 62 | 62 | 62 | S
Fisher | 45 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | S
Gordon | 444 | 444 | 444 | 296 | 444 | 444 | 444 | 444 | 444 | 444 | S
John Butters | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Lake Echo | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | S
Lemonthyme / Wilmot | 86 | 86 | 86 | 86 | 86 | 0 | 86 | 86 | 86 | 86 | S
Mackintosh | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 0 | 83 | 83 | S
Meadowbank | 42 | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | S
Poatina | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | S
Reece | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | S
Tamar Valley Combined Cycle | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 75 | 90 | 90 | 90 | 45 | 90 | 90 | 90 | 90 | 90 | S
Trevallyn | 103 | 103 | 103 | 103 | 103 | 82 | 82 | 103 | 103 | 103 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | S
Tungatinah | 75 | 125 | 100 | 100 | 125 | 125 | 125 | 125 | 125 | 125 | S
Firm Wind Capacity | 0.7056 | 0.7056 | 0.7056 | 0.7056 | 0.7056 | 0.7056 | 0.7056 | 0.7056 | 0.7056 | 0.7056 | SS
Total | 2530.7056 | 2477.6056 | 2637.6056 | 2460.6056 | 2487.6056 | 2487.6056 | 2561.7056 | 2579.6056 | 2662.6056 | 2662.6056
Summer aggregate available semi-scheduled generation
Power Station | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 20212 | Dispatch Type
Barcaldine | –14 | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | S
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS

## Winter Scheduled Capacities
Winter aggregate available scheduled and semi-scheduled generation – Tasmania (MW)
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Bastyan | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | S
Bell Bay Three | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | S
Catagunya / Liapootah / Wayatinah | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | S
Cethana | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | S
Devils Gate | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Fisher | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | S
Gordon | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | S
John Butters | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Lake Echo | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 32 | 32 | 32 | S
Lemonthyme / Wilmot | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | S
Mackintosh | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | S
Meadowbank | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | S
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS
Poatina | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | S
Reece | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | S
Tamar Valley Combined Cycle | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 75 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Trevallyn | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | S
Tungatinah | 125 | 125 | 125 | 100 | 125 | 125 | 125 | 125 | 125 | 125 | S
Total | 2772.9 | 2731.9 | 2829.9 | 2804.9 | 2829.9 | 2797.9 | 2829.9 | 2829.9 | 2829.9 | 2829.9
The table above lists the latest winter capacities for Tasmanian generation. Winter conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2013–14 these figures have been updated to 4.2% of the installed capacity during summer, and 2.5% during winter compared to the 2011–12 contribution factors.
The two tables below have been included to better represent supply availability in South Australia, by taking into account the firm contribution by wind. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Summer total available semi-scheduled capacity by power station table lists the total available capacity for semi-scheduled wind generation for the summer period. The total available refers to the maximum amount that the wind farms can generate at the summer reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation – Tasmania (MW)
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Bastyan | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | S
Bell Bay Three | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | S
Catagunya / Liapootah / Wayatinah | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | S
Cethana | 98 | 0 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | S
Devils Gate | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Fisher | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | S
Gordon | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | 444 | S
John Butters | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | S
Lake Echo | 32 | 32 | 32 | 32 | 32 | 0 | 32 | 32 | 32 | 32 | S
Lemonthyme / Wilmot | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | S
Mackintosh | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | S
Meadowbank | 0 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | S
Poatina | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | 342 | S
Reece | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | S
Tamar Valley Combined Cycle | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | S
Tamar Valley Peaking | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | S
Tarraleah | 75 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | S
Trevallyn | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | S
Tribute | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | S
Tungatinah | 125 | 125 | 125 | 100 | 125 | 125 | 125 | 125 | 125 | 125 | S
Firm Wind Capacity | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | S
Total | 2605.32 | 2564.32 | 2662.32 | 2637.32 | 2662.32 | 2630.32 | 2662.32 | 2662.32 | 2662.32 | 2662.32
Winter aggregate available semi-scheduled generation
Project Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Musselroe | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | SS

## New Developments
Projects under development – Tasmania
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Commissioning Start Date
Banks Strait Tidal Energy Facility | Tenax Engery | 1 | Water | Wave | [5 empty] | Pub An | 302 | NS | TBA
Bell Bay Pulp Mill Project | Southern Star Corporation | 1 | Wood Waste | Steam Sub Critical | ü | ü |  |  |  | Pub An | 213 | S | TBA
|  | 2 | Wood Waste | Steam Sub Critical | ü |  |  |  |  | Pub An | 60 | S | TBA
Cattle Hill Wind Farm | Cattle Hill Wind Farm Pty Ltd | Unit 1-80 | Wind | Wind - Onshore | [5 empty] | Pub An | 240 | SS | TBA
Granville Harbour Windfarm | Westcoast Wind Pty Ltd | All Units | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
Low Head Wind Farm | Low Head Wind Farm Pty Ltd | ECO122 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 29.7 | NS | TBA
TasWind (King Island) | Hydro Tasmania | 1-200 | Wind | Wind - Onshore | [5 empty] | Pub An | 600 | SS | TBA
White Rock | Eureka Funds Management | Vestas V90 | Wind | Wind - Onshore | [5 empty] | Pub An | 450 | SS | TBA

## Existing NS Generation
Existing non-scheduled generation – Tasmania
Power Station | Owner | Fuel Type | Technology Type | Nameplate Capacity (MW)
Butlers Gorge | Hydro-Electric Corporation | Water | Hydro - Gravity | 14.4
Cluny | Hydro-Electric Corporation | Water | Hydro - Gravity | 17
Glenorchy | AGL | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 1.69
Hobart | AGL | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 1
Lake Margaret | Hydro-Electric Corporation | Water | Hydro - Gravity | 8.4
Lower Lake Margaret | Hydro-Electric Corporation | Water | Hydro - Gravity | 3.2
Paloona | Hydro-Electric Corporation | Water | Hydro - Gravity | 28
Remount | LMS Energy Pty Ltd | Landfill Methane / Landfill Gas | Spark Ignition Reciprocating Engine | 2.246
Repulse | Hydro-Electric Corporation | Water | Hydro - Gravity | 28
Rowallan | Hydro-Electric Corporation | Water | Hydro - Gravity | 10.5
Tods Corner | Hydro-Electric Corporation | Water | Pump Storage | 1.2
Woolnorth Studland Bay / Bluff Point | Woolnorth Wind Farm Holding Pty Ltd | Wind | Wind - Onshore | 140
Total |  |  |  | 255.636

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless classified as semi-scheduled, or AEMO is permitted to classify it as non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW and equal to or greater than 5 MW.
Generating systems greater than 30 MW may be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating less than 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.

## Disclaimer
Important Notice
Purpose
The purpose of this publication is to provide technical, market data and information regarding opportunities in the National Electricity Market.
AEMO publishes the Electricity Statement of Opportunities in accordance with clause 3.13.3(q) of the National Electricity Rules (Rules). This publication has been prepared by AEMO using information available at 31 July 2013, unless otherwise specified. Information made available after 31 July 2013 may have been included in this publication where practical.
Disclaimer
AEMO has made every effort to ensure the quality of the information in this publication but cannot guarantee that information, forecasts and assumptions are accurate, complete or appropriate for your circumstances. This publication does not include all of the information that an investor, participant or potential participant in the National Electricity Market might require, and does not amount to a recommendation of any investment.
Anyone proposing to use the information in this publication (including information and reports from third parties) should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this publication:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this publication; and
· are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this publication.
Acknowledgement
AEMO acknowledges the support, co-operation and contribution of all participants in providing data and information used in this publication.
Copyright
© 2013 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.