## Victoria Summary
Disclaimer
This document is subject to an important disclaimer that limits or excludes AEMO's liability.
Please read the full disclaimer on the 'Disclaimer' tab of this workbook.
Victoria Summary
Committed project developments
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm is a committed project. The 131.2 MW wind farm expected commissioning is July 2014.
Bald Hill Wind Farm (Phase 1): Mitsui and Co. Australia Ltd advises that Bald Hill wind farm is a committed project. The 106.6 MW wind farm expected commissioning is May 2015.
Portland Stage 4 Cape Nelson North and Cape Sir William Grant: Pacific Hydro Portland Wind Farm Pty Ltd advises that Portland Stage 4 Cape Nelson North and Cape Sir William Grant wind farm is a committed project. The 47.15 MW wind farm expected commissioning is May 2015.
Plant retirements
AEMO has not been advised of any plant retirements in Victoria within the 10-year planning outlook.
Changes since the 2013 ESOO (existing generation)
Loy Yang A: AGL Energy advises Loy Yang A Power Station has revised its available capacity to 2100 MW (-90 MW) in summer due to operational experience in ambient conditions.
Macarthur: AGL Energy advises Macarthur Power Station has revised its available capacity to 315 MW (-105 MW) in summer to reflect the actual behaviour of the wind generation assets during high temperature days.
Morwell/Energy Brix: Energy Brix Australia Corporation Pty Ltd advises Morwell/Energy Brix Power Station has revised its available capacity to 65 MW (-10 MW) in summer due to the Morwell mine fire destroying conveyors, thus restricting coal supply.
Plant limitations
Laverton North Power Station: Snowy Hydro advises that Laverton North will be limited to 170 MW during winter 2017 due to rescheduled maintenance.
Murray 1 Power Station: Snowy Hydro advises that Murray 1 will undergo the following limitations:
· 855 MW during winter 2016 due to an outage of Unit 3
· 855 MW during winter 2017 due to an outage of Unit 8
· 855 MW during winter 2018 due to an outage of Unit 9
· 855 MW during winter 2019 due to an outage of Unit 5
· 855 MW during winter 2020 due to an outage of Unit 6
· 855 MW during winter 2021 due to an outage of Unit 4
· 855 MW during winter 2022 due to an outage of Unit 10.
Victoria existing and potential new developments by generation type (MW) data
Status / Type | Coal | CCGT | OCGT | Gas other | Solar | Wind | Water | Biomass | Geo-thermal | Other
Existing | 6599 | 21 | 1904 | 516 | 1.5 | 939 | 2296 | 53 | 0 | 0.78
Committed | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0
Publicly announced | 0 | 500 | 1150 | 0 | 100 | 3287 | 97 | 0 | 0 | 0
Withdrawn | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria existing and potential new developments by generation type (MW)

## Change Log
Victoria Change Log
Lists all key updates to new development projects and existing generation information between publication dates since the 2012 ESOO.
Publication Date: | 2012-12-20
Morwell Power Station: Energy Brix Australia Corporation Pty Ltd advises that the Morwell plant has revised its available capacity from 104 MW to 75 MW (-29 MW) in summer and winter, due to generation units with DUID MOR1 in operation and generation unit with DUID MOR2 operational when generation unit with DUID MOR1 is under maintenance. Generation unit with DUID MOR3 will be available on a 30 day recall.
Qenos Cogeneration Facility: AGL Energy advises that Qenos Cogeneration Facility is a committed project. The 21 MW combined-cycle gas turbine (CCGT) construction completion acheived in October 2012 and full commisioning at the end of March 2013.
Publication Date: | 2013-06-30
Macarthur Wind Farm: AGL Energy advises that the 420 MW Macarthur wind farm project was completed in January 2013.
Mortons Lane Wind Farm: Mortons Lane WindFarm Pty Ltd advises that the 19.5 MW Mortons Lane wind farm project was completed in December 2012.
Qenos Cogeneration Facility: AGL Energy advises that 21 MW Qenos Cogeneration Facility project was completed in March 2013.
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm is a committed project. The 131.2 MW wind farm expected commissioning is January 2015.
Mildura Power Station: Solar Systems advises that Mildura Power Station demonstation facility is a committed project. The 1.5 MW solar plant is under construction and expected completion is July 2013.
Hallam Road Power Station: LMS Energy advises that the upgrades to Unit 7 was completed in June 2012 and Unit 8 in November 2012 increasing the capacity by 2.2 MW.
Publication Date: | 2013-08-13
Mildura Power Station: Solar Systems advises that Mildura Power Station Stage 2 of the project is to be 100 MW of capacity.
Publication Date: | 2013-11-15
Mildura Power Station: Solar Systems advises that Mildura Power Station demonstation facility (1.5 MW) project was completed in July 2013.
Portland Stage 4 Cape Nelson North and Cape Sir William Grant: Pacific Hydro Australia advises that Portland Stage 4 Cape Nelson North and Cape Sir William Grant (47.15 MW) construction at the site is to commence in September 2013, with full commissioning planned for September 2015.
Publication Date: | 2014-05-30
Loy Yang A: AGL Energy advises Loy Yang A Power Station has revised its available capacity to 2100 MW (-90 MW) in summer due to operational experience in ambient conditions.
Macarthur: AGL Energy advises Macarthur Power Station has revised its available capacity to 315 MW (-105 MW) in summer to reflect the actual behaviour of the wind generation assets during high temperature days.
Morwell/Energy Brix: Energy Brix Australia Corporation Pty Ltd advises Morwell/Energy Brix Power Station has revised its available capacity to 65 MW (-10 MW) in summer due to the Morwell mine fire destroying conveyors, thus restricting coal supply.
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm is a committed project. The 131.2 MW wind farm expected commissioning is July 2014.
Bald Hill Wind Farm (Phase 1): Mitsui and Co. Australia Ltd advises that Bald Hill wind farm is a committed project. The 106.6 MW wind farm expected commissioning is May 2015.
Portland Stage 4 Cape Nelson North and Cape Sir William Grant: Pacific Hydro Portland Wind Farm Pty Ltd advises that Portland Stage 4 Cape Nelson North and Cape Sir William Grant wind farm is a committed project. The 47.15 MW wind farm expected commissioning is May 2015.
Publication Date: | 2014-08-07
Mt Mercer Wind Farm: Mt Mercer Wind Farm Pty Ltd advises that Mt Mercer wind farm has been in full production since July 2014. The commissioning date has been revised to February 2015.
Anglesea Power Station: Alcoa of Australia Limited advises that Anglesea Power Station is changed its registration classification from Non-Scheduled to a Scheduled generator.

## Existing S & SS Generation
Existing & committed scheduled and semi-scheduled generation
Power Station | Owner | Unit Numbers and Nameplate Capacity (MW) | Nameplate Capacity (MW) | Technology Type | Fuel Type | Dispatch Type
Anglesea Power Station | Alcoa of Australia Limited | 1 x 150 | 150 | Steam Sub Critical | Brown Coal | S
Bairnsdale | Alinta DEBO | 2 x 47 | 94 | OCGT | Natural Gas Pipeline | S
Bogong / Mackay | AGL | 2 x 80 6 x 25 | 310 | Hydro - Gravity | Water | S
Dartmouth | AGL | 1 x 185 | 185 | Hydro - Gravity | Water | S
Eildon | AGL | 2 x 60 2 x 7.5 | 135 | Hydro - Gravity | Water | S
Hazelwood | Hazelwood Power | 8 x 200 | 1600 | Steam Sub Critical | Brown Coal | S
Hume VIC | Green State Power Pty Ltd | 1 x 29 | 29 | Hydro - Gravity | Water | S
Jeeralang A | Industry Funds Management Nominees Ltd | 4 x 53 | 212 | OCGT | Natural Gas Pipeline | S
Jeeralang B | Industry Funds Management Nominees Ltd | 3 x 76 | 228 | OCGT | Natural Gas Pipeline | S
Laverton North | Snowy Hydro Ltd | 2 x 156 | 312 | OCGT | Natural Gas Pipeline | S
Loy Yang A | AGL Energy | 3 x 560 1 x 500 | 2180 | Steam Sub Critical | Brown Coal | S
Loy Yang B | IPM Australia Limited | 2 x 500 | 1000 | Steam Sub Critical | Brown Coal | S
Macarthur | Macarthur Wind Farm Pty Ltd and Meridian Wind Macarthur Pty Ltd | 140 x 3 | 420 | Wind - Onshore | Wind | SS
Mildura Power Station | Solar Systems Pty Ltd | 1 X 1.5 | 1.5 | PV-Concentrator | Solar | SS
Mortlake | Origin Energy Power Limited | 2 x 283 | 566 | OCGT | Natural Gas Pipeline | S
Morwell/Energy Brix | Energy Brix Australia Corporation Pty Ltd | 1 x 84 1 x 30 1 x 75 | 189 | Steam Sub Critical | Brown Coal | S
Murray 1 | Snowy Hydro Ltd | 10 x 95 | 950 | Hydro - Gravity | Water | S
Murray 2 | Snowy Hydro Ltd | 4 x 138 | 552 | Hydro - Gravity | Water | S
Newport | Industry Funds Manaegment Nominees Ltd | 1 x 510 | 510 | Steam Sub Critical | Natural Gas Pipeline | S
Oaklands Hill | Oaklands Hill Wind farm pty ltd | 32 x 2.1 | 67.2 | Wind - Onshore | Wind | SS
Somerton | AGL Energy | 4 x 40 | 160 | OCGT | Natural Gas Pipeline | S
Valley Power | Snowy Hydro Ltd | 6 x 50 | 300 | OCGT | Natural Gas Pipeline | S
West Kiewa | AGL | 4 x 15 | 60 | Hydro - Gravity | Water | S
Yallourn W | EnergyAustralia Holdings Pty Ltd | 2 x 380 2 x 360 | 1480 | Steam Sub Critical | Brown Coal | S
Committed
Bald Hills p1 | Mitsui and Co. Australia Ltd | 52 X 2.05 | 106.6 | Wind - Onshore | Wind | SS
Mt Mercer | Mt Mercer Wind Farm Pty Ltd | 64 x 2.05 | 131.2 | Wind - Onshore | Wind | SS
Total |  |  | 11928.5

## Summer Scheduled Capacities
Summer aggregate available scheduled and semi-scheduled generation – Victoria (MW)
Power Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Barcaldine | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | S
Anglesea Power Station | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | S
Bairnsdale | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | S
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | S
Hume VIC | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Jeeralang A | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | S
Jeeralang B | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | S
Laverton North | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Loy Yang A | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | S
Loy Yang B | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | S
Macarthur | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | SS
Mortlake | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | S
Morwell/Energy Brix | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | S
Murray 1 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | S
Murray 2 | 562.5 | 562.5 | 562.5 | 562.5 | 562.5 | 575 | 587.5 | 600 | 600 | 600 | S
Newport | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | S
Oaklands Hill | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | SS
Somerton | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | S
Valley Power | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | S
West Kiewa | 53 | 57 | 57 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Committed Projects
Bald Hills p1 | 0 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Total | 11132.5 | 11243.1 | 11243.1 | 11248.1 | 11248.1 | 11260.6 | 11273.1 | 11285.6 | 11285.6 | 11285.6
The table above lists the latest summer capacities for Victorian generation. Summer conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2014–15 these figures are 6.7% of the installed capacity during summer, and 5.9% during winter, based on the contribution factors published by AEMO in the 2014 NEM Historical Market Information Report.
The two tables below have been included to better represent the supply availability in Victoria, by taking into account the firm contribution by wind. The Summer aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Summer aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled wind generation for the summer period. The total refers to the maximum amount that the wind farms can be generated from the wind farms at the summer reference temperatures.
Summer aggregate scheduled and firm semi-scheduled generation – Victoria (MW)
Power Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Barcaldine | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | S
Anglesea Power Station | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | S
Bairnsdale | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | S
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | S
Hume VIC | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | S
Jeeralang A | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | S
Jeeralang B | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | S
Laverton North | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Loy Yang A | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | S
Loy Yang B | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | 965 | S
Mortlake | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | 518 | S
Morwell/Energy Brix | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | S
Murray 1 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | 950 | S
Murray 2 | 562.5 | 562.5 | 562.5 | 562.5 | 562.5 | 575 | 587.5 | 600 | 600 | 600 | S
Newport | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | S
Somerton | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | 133.5 | S
Valley Power | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | S
West Kiewa | 53 | 57 | 57 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | S
Firm Wind Capacity | 33.0645 | 40.2067 | 40.2067 | 40.2067 | 40.2067 | 40.2067 | 40.2067 | 40.2067 | 40.2067 | 40.2067 | SS
Total | 10672.0645 | 10683.2067 | 10683.2067 | 10688.2067 | 10688.2067 | 10700.7067 | 10713.2067 | 10725.7067 | 10725.7067 | 10725.7067
Summer aggregate available semi-scheduled generation
Power Station | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | Dispatch Type
Barcaldine | –15 | –16 | –17 | –18 | –19 | –20 | –21 | -22 | -23 | -24 | S
Macarthur | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | SS
Oaklands Hill | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | SS
Committed Projects
Bald Hills p1 | 0 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Total | 493.5 | 600.1 | 600.1 | 600.1 | 600.1 | 600.1 | 600.1 | 600.1 | 600.1 | 600.1

## Winter Scheduled Capacities
Winter aggregate scheduled and semi-scheduled generation – Victoria (MW)
Project Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Anglesea Power Station | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | S
Bairnsdale | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | S
Hume VIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Jeeralang A | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | S
Jeeralang B | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | S
Laverton North | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | S
Loy Yang A | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | S
Loy Yang B | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | S
Macarthur | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | SS
Mortlake | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | S
Morwell/Energy Brix | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | S
Murray 1 | 950 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 950 | 950 | S
Murray 2 | 562.5 | 562.5 | 562.5 | 562.5 | 575 | 587.5 | 600 | 600 | 600 | 600 | S
Newport | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | S
Oaklands Hill | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | SS
Somerton | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | S
Valley Power | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | S
West Kiewa | 53 | 57 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | S
Committed Projects
Bald Hills p1 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Total | 11992.8 | 11901.8 | 11906.8 | 11906.8 | 11919.3 | 11931.8 | 11944.3 | 11944.3 | 12039.3 | 12039.3
The table above lists the latest winter capacities for Victorian generation. Winter conditions relate to statistically predicted contribution under 10% POE maximum demand conditions.
Due to the intermittent nature of wind, wind generation capacities are de-rated to account for the output most likely to be available during times of maximum demand. AEMO refers to this as the "firm contribution" from wind generators during peak periods. For 2014–15 these figures are 6.7% of the installed capacity during summer, and 5.9% during winter, based on the contribution factors published by AEMO in the 2014 NEM Historical Market Information Report.
The two tables below have been included to better represent the supply availability in Victoria, by taking into account the firm contribution by wind. The Winter aggregate scheduled and firm semi-scheduled generation table presents scheduled generation and aggregated firm wind generation. The Winter aggregate available semi-scheduled generation table lists the total available capacity for semi-scheduled wind generation for the winter period. The total refers to the maximum amount that the wind farms can be generated from the wind farms at the winter reference temperatures.
Winter aggregate scheduled and firm semi-scheduled generation – Victoria (MW)
Project Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Anglesea Power Station | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | S
Bairnsdale | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | S
Bogong / Mackay | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | S
Dartmouth | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | S
Eildon | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | S
Hazelwood | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | S
Hume VIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | S
Jeeralang A | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | S
Jeeralang B | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | S
Laverton North | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | S
Loy Yang A | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | 2270 | S
Loy Yang B | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | S
Mortlake | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | S
Morwell/Energy Brix | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | S
Murray 1 | 950 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 950 | 950 | S
Murray 2 | 562.5 | 562.5 | 562.5 | 562.5 | 575 | 587.5 | 600 | 600 | 600 | 600 | S
Newport | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | S
Somerton | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | 161.5 | S
Valley Power | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | S
West Kiewa | 53 | 57 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | S
Yallourn W | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | 1504 | S
Firm Wind Capacity | 42.5272 | 42.5272 | 42.5272 | 42.5272 | 42.5272 | 42.5272 | 42.5272 | 42.5272 | 42.5272 | 42.5272 | SS
Total | 11314.5272 | 11223.5272 | 11228.5272 | 11228.5272 | 11241.0272 | 11253.5272 | 11266.0272 | 11266.0272 | 11361.0272 | 11361.0272
Winter aggregate available semi-scheduled generation
Project Station | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Dispatch Type
Macarthur | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | SS
Oaklands Hill | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | SS
Committed Projects
Bald Hills p1 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | SS
Mt Mercer | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | SS
Total | 720.8 | 720.8 | 720.8 | 720.8 | 720.8 | 720.8 | 720.8 | 720.8 | 720.8 | 720.8

## New Developments
Projects under development – Victoria
Project | Owner | Unit ID | Fuel Type | Generation Type | Land | Equip | Plan | Finance | Date | Unit Status | Nameplate Capacity (MW) | Dispatch Type | Commissioning Start Date
Ararat | Ararat Wind Farm Pty Ltd | 1-75 | Wind | Wind - Onshore | [5 empty] | Pub An | 240 | SS | 2015-10-31
Bald Hills p1 | Mitsui and Co. Australia Ltd | 1-52 | Wind | Wind - Onshore | ü | ü | ü | ü | ü | Com | 106.6 | SS | 2015-05-05
Ben More | Ratch Australia | 1-50/70 | Wind | Wind - Onshore | [5 empty] | Pub An | 50-70 | SS | TBA
Berrimal | ACCIONA Energy | 1-24 | Wind | Wind - Onshore | [5 empty] | Pub An | 24-66 | SS | TBA
Berrybank Wind Farm | Berrybank Development Pty Ltd | Units 1-89 | Wind | Wind - Onshore | [5 empty] | Pub An | 178 | SS | 2017-05-01
Chepstowe WF | Future Energy Pty Ltd | 1-3 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 6 | NS | 2015-06-01
Cherry Tree Wind Farm | Infigen Energy | Units 1-16 | Wind | Wind - Onshore | [5 empty] | Pub An | 48 | SS | TBA
Coonooer Bridge | Windlab Systems Pty Ltd | 6 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 18 | SS | 2015-01-01
Crowlands | Energy Pacific Vic Pty Ltd | 1-41 | Wind | Wind - Onshore | [5 empty] | Pub An | 82 | SS | TBA
Darlington Wind Farm | Union Fenosa Wind Australia Pty Ltd | Units 1-80 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 360 | SS | TBA
Dundonnell | TrustPower | 1-104 | Wind | Wind - Onshore | [5 empty] | Pub An | 312 | SS | 2017-12-18
Hawkesdale Wind Farm | Ryan Corner Development Pty Ltd | Units 1-31 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 62 | SS | TBA
Lal Lal elaine end | Elaine Wind Farm Pty Ltd | 41-64 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 48-78 | SS | 2015-12-31
Lal Lal yendon end | Yendon Wind Farm Pty Ltd | 1-40 | Wind | Wind - Onshore | ü |  |  |  | ü | Pub An | 80-136 | SS | 2015-12-31
Mildura Power Station | Solar Systems Pty Ltd | Stage 2 | Solar | PV-Concentrator | ü |  |  |  |  | Pub An | 100 | SS | TBA
Moorabool | Moorabool Wind Farm Pty Ltd | 1-107 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 214-342 | SS | 2017-06-30
Mortlake South | ACCIONA Energy | 1-51 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 76.5 | SS | 2016-10-01
Mortlake Stage 2 | Origin Energy | Mortlake 21-22 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 550 | S | TBA
Mt Gellibrand | ACCIONA Energy | 1-63 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 189 | SS | TBA
Mt Mercer | Mt Mercer Wind Farm Pty Ltd | WTG 1-64 | Wind | Wind - Onshore | ü | ü | ü | ü | ü | Com | 131.2 | SS | 2014-09-01
Penshurst | RES Australia Pty Ltd | 1-134 | Wind | Wind - Onshore | [5 empty] | Pub An | 442.2 | SS | TBA
Port Phillip Heads Tidal Energy Project | Tenax Energy | 1 | Water | Tidal | [5 empty] | Pub An | 34 | NS | TBA
Portland Stage 4 Cape Nelson North and Cape Sir William Grant | Pacific Hydro Portland Wind Farm Pty Ltd | 1-27 | Wind | Wind - Onshore | ü | ü | ü | ü | ü | Com | 47.15 | NS | 2015-05-26
Victorian Wave Power Project | Victorian Wave Partners Ltd | Stage 1-3 | Water | Wave | [5 empty] | Pub An | 62.5 | NS | TBA
Ryan Corner Wind Farm | Ryan Corner Development Pty Ltd | Units 1-67 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 134 | SS | TBA
Salt Creek | TrustPower | 1-15 | Wind | Wind - Onshore | [5 empty] | Pub An | 30 | NS | TBA
Shaw River Power Station | Santos TGR Pty Ltd | Shaw River 1 | Natural Gas Pipeline | CCGT | [5 empty] | Pub An | 500 | S | TBA
Stockyard Hill | Origin Energy | 1-157 | Wind | Wind - Onshore | [5 empty] | Pub An | TBA | SS | TBA
Tarrone GT | AGL Energy Limited | 1-2 | Natural Gas Pipeline | OCGT | [5 empty] | Pub An | 500-600 | S | TBA
Tarrone Wind Farm | Union Fenosa Wind Australia Pty Ltd | Units 1-17 | Wind | Wind - Onshore | ü |  |  |  |  | Pub An | 54 | SS | TBA
Willatook | Wind Prospect WA Pty Ltd | 1-145 | Wind | Wind - Onshore | [5 empty] | Pub An | 261 | SS | TBA
Winchelsea | - | 1-14 | Wind | Wind - Onshore | [5 empty] | Pub An | 28 | SS | TBA
Woolsthorpe | Woolsthorpe Wind Farm Pty Ltd | 1-20 | Wind | Wind - Onshore | [5 empty] | Pub An | 46 approx | SS | 2016-03-15
Yaloak South | Energy Pacific Vic Pty Ltd | 1-14 | Wind | Wind - Onshore | [5 empty] | Pub An | 28.7 | NS | TBA
a. Where the proponent has provided a range of nameplate capacities, the upper bound has been used in any total calculations

## Existing NS Generation
Existing non-scheduled generation – Victoria
Power Station | Owner | Nameplate Capacity (MW) | Technology Type | Fuel Type
200 Victoria Street | Cogent Energy | 0.4 | Compression Reciprocating Engine | Natural Gas Pipeline
321 Exhibition Street Trigen | Cogent Energy | 1.2 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline
990 Latrobe St | Cogent Energy | 0.4 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline
Ballarat | LMS ENERGY Pty Ltd | 0.5 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Ballarat Base Hospital | Ballarat Base Hospital | 2.04 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline
Banimboola | AGL | 12.2 | Hydro - Gravity | Water
Bendigo | LMS ENERGY Pty Ltd | 0.78 | Spark Ignition Reciprocating Engine | Biomass recycled municipal and industrial material
Berwick | EDL LFG Vic Pty Ltd | 4.57 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Broadmeadows | EDL LFG Vic Pty Ltd | 6.18 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Brooklyn | EDL LFG Vic Pty Ltd | 2.83 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Challicum Hills | Pacific Hydro Challicum Hills Pty Ltd | 52.5 | Wind - Onshore | Wind
Clayton | EDL LFG Vic Pty Ltd | 12 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Clover | AGL | 29 | Hydro - Gravity | Water
Codrington | Energy Pacific Vic Pty Ltd | 18.2 | Wind - Onshore | Wind
Corio | EDL LFG Vic Pty Ltd | 1 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Dandenong PEP | Cogent Energy | 2 | Spark Ignition Reciprocating Engine | Natural Gas Pipeline
Diamond Energy Shepparton | Diamond Energy Pty Ltd | 1.1 | Spark Ignition Reciprocating Engine | Sewerage / Waste Water
Diamond Energy Tatura | Diamond Energy Pty Ltd | 1.1 | Spark Ignition Reciprocating Engine | Sewerage / Waste Water
Eildon Small Hydro | Pacific Hydro Investments Pty Ltd | 4.5 | Hydro - Gravity | Water
Glenmaggie Hydro | Pacific Hydro Investments Pty Ltd | 3.8 | Hydro - Gravity | Water
Hallam Road | LMS Energy Pty Ltd | 8.984 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Leonards Hill | Hepburn Community Wind Park Co-operative Limited | 4.1 | Wind - Onshore | Wind
Longford | Longford Gas Plant | 31.8 | OCGT | Natural Gas Pipeline
Mornington Waste Disposal Facility | LMS Generation Pty Ltd | 0.77 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Mortons Lane Wind Farm | Mortons Lane WindFarm Pty Ltd | 19.5 | Wind - Onshore | Wind
Portland Stage 2-3 Cape Bridgewater and Cape Nelson South | Pacific Hydro Portland Wind Farm Pty Ltd | 102 | Wind - Onshore | Wind
Qenos Cogeneration Facility | AGL | 21 | CCGT | Natural Gas Pipeline
Rubicon Mountain Streams | AGL | 13.5 | Hydro - Gravity | Water
Shepparton | LMS ENERGY Pty Ltd | 0.78 | Spark Ignition Reciprocating Engine | Non-biomass recycled municipal and industrial mate
South East Water - Hallam Plant | South East Water | 0.25 | Hydro - Gravity | Water
Springvale | EDL LFG Vic Pty Ltd | 4.2 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Toora | Ratch Australia | 21 | Wind - Onshore | Wind
Waubra | Pyrenees Wind Energy Developments | 192 | Wind - Onshore | Wind
William Hovel | Pacific Hydro Investments Pty Ltd | 1.8 | Hydro - Gravity | Water
Wollert | LMS Energy Pty Ltd | 6.738 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Wonthaggi | Regional Wind Farms | 12 | Wind - Onshore | Wind
Wyndham Renewable Energy Facility | LMS Energy Pty Ltd | 1.903 | Spark Ignition Reciprocating Engine | Landfill Methane / Landfill Gas
Yambuk | Energy Pacific Vic Pty Ltd | 30 | Wind - Onshore | Wind
Yarrawonga | AGL | 9.5 | Hydro - Gravity | Water
Total |  | 638.125

## Background Information
Generation capacity in the NEM
Any person who owns, controls, or operates a generating system connected to a transmission or distribution network must register as a generator. A generating system’s registered capacity is the nominal megawatt (MW) capacity registered with AEMO.
The registered capacity is often the same as a generating system’s nameplate capacity. Nameplate capacity represents the maximum continuous output or consumption in MW, as specified by the manufacturer, or as subsequently modified. Nameplate capacity can change for a number of reasons, such as upgrade projects, age or a review of performance.
Under the National Electricity Rules (NER), generating systems are classified as scheduled, semi-scheduled, or non-scheduled.
Scheduled (S) generation refers to any generating system with an aggregate nameplate capacity of 30 MW or more, unless classified as semi-scheduled, or AEMO is permitted to classify it as non-scheduled.
Semi-scheduled (SS) generation refers to any generating system with intermittent output (such as wind or run-of-river hydro) with an aggregate nameplate capacity of 30 MW or more. A semi-scheduled classification gives AEMO the power to limit generation output that may exceed network capabilities, but reduces the participating generator’s requirement to provide information.
Non-scheduled (NS) generation refers to generating systems with an aggregate nameplate capacity of less than 30 MW and equal to or greater than 5 MW.
Generating systems greater than 30 MW may be classified as non-scheduled if:
· the primary purpose of the generating unit is for local use and the aggregate sent-out generation rarely exceeds 30 MW, or
· it is not practicable for the generating unit to participate in central dispatch.
A generating unit with a nameplate rating less than 30 MW may also be exempted by AEMO if it exports less than 20 GWh into the grid in a year or extenuating circumstances apply.
Measuring generation capacity
Generation capacity can be measured as either:
· as-generated capacity, representing the output measured at a generating unit’s terminals, or
· sent-out capacity, representing the output after allowing for energy consumption by auxiliary equipment (used to help produce and transmit the electricity).
For the purposes of the ESOO, and consistent with market systems, AEMO measures scheduled and semi-scheduled generation capacity on an as-generated basis. Non-scheduled generation is measured as sent-out because it can include co-generation plants (that usually produce both heat and electricity), where the bulk of the capacity is consumed locally.
Temperature effects on generation
The actual level of generation available at any particular time will depend on the condition of the generating plant. This includes factors such as age, outages, and wear. Another important factor with respect to output is the reduction in thermal efficiency as the temperature increases.
Because temperature can affect plant generation capacities in different ways, basing generation capacities on region-specific reference temperatures facilitates more effective assessment of available generation capacity under weather conditions frequently associated with high demand.
To produce the supply-demand outlook, AEMO — in consultation with the Jurisdictional Planning Bodies (JPBs) — undertakes the following:
· Uses historical data to estimate typical weather conditions, and to determine reference temperatures frequently associated with times of 10% probability of exceedence (POE) maximum demand in the major load centres for each region.
· Asks generators to provide generating unit capacities for summer and winter using these common reference temperatures. The table below lists the common reference temperatures AEMO applies for each region. In general, annual maximum demands occur during summer; the exception is Tasmania, where maximum demand occurs during winter. Summer maximum demand in Tasmania occurs during colder temperatures, resulting in a relatively low summer reference temperature.
Generation capacity reference temperatures
Region | Summer (°C) | Winter (°C)
Queensland | 37 | 15
New South Wales | 42 | 9
Victoria | 41 | 8
South Australia | 43 | 11
Tasmania | 7.7 | 1.2
Maximum capacity
Some thermal (generation that burns fuel) and non-thermal (renewable generation) generating systems can provide additional, short-term capacity that exceeds the registered capacity. This is known as maximum capacity.
Proposed generation in the NEM
In addition to capacity forecasts, generation plant owners advise AEMO about the status of generation projects currently under development in each region.
Proposed projects can be at different stages of development, and are categorised as follows:
· Committed projects, representing generation that is considered to be proceeding.
· Proposed projects, which are further identified as either:
- Advanced proposals, representing generation at an intermediate stage of development, or
- Publicly announced proposals, representing generation at an early stage of development.
Projects are categorised based on AEMO’s commitment criteria, which cover site acquisition, contracts for major components, planning approval, financing, and the date set for construction. Committed projects meet all five of the commitment criteria, advanced proposals meet at least three, and publicly announced proposals meet less than three.
Generation project commitment criteria
Category | Criteria
Site | The project proponent has purchased/settled/acquired (or commenced legal proceedings to purchase/settle/acquire) land for the construction of the project.
Major components | Contracts for the supply and construction of major plant or equipment components (such as generating units, turbines, boilers, transmission towers, conductors, and terminal station equipment) have been finalised and executed, including any provisions for cancellation payments.
Planning consents/construction approvals/EIS | The proponent has obtained all required planning consents, construction approvals, and licences, including completion and acceptance of any necessary environmental impact statements.
Finance | The financing arrangements for the proposal, including any debt plans, must have been concluded and contracts executed.
Final construction date set | Construction of the proposal must either have commenced or a firm commencement date must have been set.

## Disclaimer
Important Notice
Purpose
The purpose of this publication is to provide technical, market data and information regarding opportunities in the National Electricity Market.
AEMO publishes the Electricity Statement of Opportunities in accordance with clause 3.13.3(q) of the National Electricity Rules (Rules). This publication has been prepared by AEMO using information available at 31 July 2014, unless otherwise specified. Information made available after 31 July 2014 may have been included in this publication where practical.
Disclaimer
AEMO has made every effort to ensure the quality of the information in this publication but cannot guarantee that information, forecasts and assumptions are accurate, complete or appropriate for your circumstances. This publication does not include all of the information that an investor, participant or potential participant in the National Electricity Market might require, and does not amount to a recommendation of any investment.
Anyone proposing to use the information in this publication (including information and reports from third parties) should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this publication:
· make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this publication; and
· are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this publication.
Acknowledgement
AEMO acknowledges the support, co-operation and contribution of all participants in providing data and information used in this publication.
Copyright
© 2014 Australian Energy Market Operator Limited. The material in this publication may be used in accordance with the copyright permissions on AEMO’s website.