## Notes
Notes:
1. All costs should be provided in real 1 July 2019 $AUD
2. All costs should be appropriate for generation technologies to be operated in Australian conditions
3. All cost components exposed to foreign exchange need to be separately identified
4. Where costs are materially different between Australian regions (within regions of the National Electricity Market (NEM)) then the Consultant will clearly identify the regional cost differences.
5. Data produced must be expressed: • On an as-generated basis with auxiliary assumptions listed. • Using metric units. • For current costs (i.e. installation on 1 July 2019) in 1 July 2019 real Australian dollars. • Exclusive of GST. • With formulas for any calculated fields.
6. Data is required for all regions of the NEM.

## Glossary
Glossary
Acronym | Definition
MW | MegaWatt
MWh | MegaWatt Hour
GW | GigaWatt
GWh | GigaWatt Hour
GJ | Giga Joule
CCS | Carbon Capture and Storage
CCGT | Combined Cycle Gas Turbine
OCGT | Open Cycle Gas Turbine
HHV | Higher Heating Value
CO2e | Carbon Dioxide Equivalent
kg | Kilogram
CAPEX | Capital Expenditure
OPEX | Operational Expenditure
PC | Pulverised Coal
Summer | December to March
Not Summer | April to November

## Assumptions Summary
Gen Cost 2019
This file presents tables of input data for AEMO's modelling studies and publications.
Version History
Version Number | Date | Description
1 | 2019-07-25 | First release template to consultant
2 | 2019-12-10 | Release with 2019 Cost and Technical Parameter Review report by Aurecon
3 | 2020-03-04 | Updates to BESS costs following consultation process
Worksheet Descriptions
Worksheet | Assumptions Grouping | Description | Source
Renewable Energy Zones | REZs | Renewable Energy Zones and Regional definitions | AEMO
WP1 - New Costs | Work Package 1 | New entrant developments costs | Consultant
WP1 - New Parameters |  | New entrant technical parameters | Consultant
WP1 - Capacity Factors |  | New entrant solar and wind farm capacity factor improvements | Consultant
Supporting Materials
For further details on input assumptions and sources visit: | http://aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Inputs-Assumptions-and-Methodologies
Source | Materials
GHD, 2018 AEMO costs and technical parameter review | AEMO costs and technical parameter review report, available at: http://aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/9110715-REP-A-Cost-and-Technical-Parameter-Review---Rev-4-Final.pdf AEMO costs and technical parameter review databook, available at: http://aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/GHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb
CSIRO, 2018, GenCost 2018; Updated projections of electricity generation technology costs | https://publications.csiro.au/rpr/download?pid=csiro:EP189502&dsid=DS1
Generator information (2019 January release, May update) | https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information

## Renewable Energy Zones
Renewable Energy Zones |  |  |  | Renewable Energy Zone Map
List of Renewable Energy Zones (REZs) by NEM region and zone
# | Name | NEM Region | NEM Zone
Q1 | Far North QLD | QLD | NQ
Q2 | North Qld Clean Energy Hub | QLD | NQ
Q3 | Northern Qld | QLD | NQ
Q4 | Isaac | QLD | NQ
Q5 | Barcaldine | QLD | CQ
Q6 | Fitzroy | QLD | CQ
Q7 | Wide Bay | QLD | CQ
Q8 | Darling Downs | QLD | SWQ
N1 | North West NSW | NSW | NNS
N2 | New England | NSW | NNS
N3 | Central West NSW | NSW | NCEN
N4 | Southern NSW Tablelands | NSW | CAN
N5 | Broken Hill | NSW | SWNSW
N6 | South West NSW | NSW | SWNSW
N7 | Wagga Wagga | NSW | SWNSW
N8 | Tumut | NSW | CAN
N9 | Cooma-Monaro | NSW | CAN
V1 | Ovens Murray | VIC | NVIC
V2 | Murray River | VIC | NVIC
V3 | Western Victoria | VIC | CVIC
V4 | Moyne | VIC | MEL
V5 | Gippsland | VIC | LV
V6 | Central North Vic | VIC | NVIC
S1 | South East SA | SA | SESA
S2 | Riverland | SA | NSA
S3 | Mid-North SA | SA | NSA
S4 | Yorke Peninsula | SA | NSA
S5 | Northern SA | SA | NSA
S6 | Leigh Creek | SA | NSA
S7 | Roxby Downs | SA | NSA
S8 | Eastern Eyre Peninsula | SA | NSA
S9 | Western Eyre Peninsula | SA | NSA
T1 | North East Tasmania | TAS | TAS
T2 | North West Tasmania | TAS | TAS
T3 | Tasmania Midlands | TAS | TAS

## WP1 - New Costs
Technical parameters and operating costs for new technologies
General Details
Technology | Assumed unit size (MW) (Gross) @ 25oC, 110 metres, 60%RH | Seasonal Ratings: Summer (MW) (Net) | Seasonal Ratings: Not summer (MW) (Net) | Generation Type | Fuel Type | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs | Carbon Capture equipment and installation costs (separate from the generation plant) | Carbon storage costs (separate from capture costs) ($/t CO2) | Carbon transportation costs ($/t CO2) | Disposal costs
CCGT - With CCS |  |  |  | Thermal | Natural Gas
CCGT - Without CCS | 380 | 348 | 389 | Thermal | Natural Gas | 401100000 | $20M +$1.5M/km | 51570000 | 171900000
OCGT - Without CCS | 258 | 227 | 272 | Thermal | Natural Gas | 221812500 | $20M +$1.5M/km | 28500000 | 95062500
Reciprocating Engine | 211.2 | 209.1 | 209.1 | Thermal | Natural Gas/Diesel | 169371000 | $20M +$1.5M/km | 25400000 | 112914000
Fuel cells | 0.25 | 0.25 | 0.25 | Storage | N/A | 464000 | Excluded | 116000 | 116000
Large Scale Battery Storage (1hr) | 25 | 24.46 | 24.46 | Storage | N/A | 15900000 | N/A | 4800000 | 4000000
Large Scale Battery Storage (2hr) | 25 | 23.97 | 23.97 | Storage | N/A | 21000000 | N/A | 4800000 | 5300000
Large Scale Battery Storage (4hr) | 25 | 23 | 23 | Storage | N/A | 35400000 | N/A | 4800000 | 8900000
Large Scale Battery Storage (8hr) | 25 | 21.06 | 21.06 | Storage | N/A | 67400000 | N/A | 4800000 | 16900000
Flow Battery Storage (8hr)
Electrolysers | 50 | N/A | N/A | Storage | N/A | 72000000 | Excluded | 7200000 | 18000000
Solar PV - Single axis tracking | 100 | 97.1 | 97.1 | Renewable | N/A | 82800000 | N/A | 8292000 | 55200000
Solar Thermal Central Receiver with storage | 150 | 135 | 135 | Renewable | N/A | 721500000 | N/A | 38480000 | 240500000
Solar Thermal Central Receiver without storage
Wind - onshore | 210 | 194 | 210 | Renewable | N/A | 226800000 | N/A | 22680000 | 151200000
Wind - offshore | 1045 | 1003 | 1003 | Renewable | N/A | 4353020000 | N/A | 124372000 | 1865580000
Technology | Cost of energy storage ($/MWh) | Cost of storage capacity ($/MW)
Fuel cells | Excluded
Large Scale Battery Storage (1hr) | $0.57 / MWh storage | $0.23 / MW installed
Large Scale Battery Storage (2hr) | $0.42 / MWh storage | $0.21 / MW installed
Large Scale Battery Storage (4hr) | $0.39 / MWh storage | $0.21 / MW installed
Large Scale Battery Storage (8hr) | $0.39 / MWh storage | $0.21 / MW installed
Flow Battery Storage (8hr)
Electrolysers | Excluded
Solar Thermal Central Receiver with storage | N/A

## WP1 - New Parameters
Technical parameters and operating costs for new technologies
General Details
Technology | Generation Type | Fuel Type | First Year Assumed Commercially Viable for construction | Assumed unit size (MW) (Gross) @ 25oC, 110 metres, 60%RH | Seasonal Ratings: Summer (MW) (Net) | Seasonal Ratings: Not summer (MW) (Net) | Economic Life (Design Life) (yrs) | Technical Life (Operational Life)(yrs) | Time for development (includes pre/feasibilty, design, approvals and so on) (yrs) | Construction time (weeks) | Total Lead Time (years) | Min Stable Generation (% of installed capacity) | Auxiliary load (% of installed capacity) | Auxiliary load for Generators operating in Synchronous Condenser mode (% of installed capacity) | Forced outage rate (full forced outages) % | Frequency of full forced outage per annum | Full outage Mean time to repair (h) | Partial Forced outage rate (partial forced outages) | Frequency of partial forced outages | Partial Outage derating factor (% lost during partial outage) | Partial outage Mean time to repair (h) | Equivalent forced outage rate (%) | Minimum Load required for Synchronous Condensers (MW) | Ramp Up Rate (MW/h) - standard operation | Ramp Down Rate (MW/h) - standard operation | Heat rate at minimum operation (GJ/MWh) HHV Net | Heat rate at maximum operation (GJ/MWh) HHV Net | Thermal Efficiency (%, HHV, Net) MCR | Maintenance Frequency (no of maintenance events per year) | Average Planned Maintenance (no of days/year) | Hydro units: Pumping Efficiency (MWh pumped per MWh generated) - within 24 hours | Pump load (MW) | Battery storage: Charge efficiency | Battery storage: Discharge efficiency | Battery Storage: Allowable max State of Charge (%) | Battery Storage: Allowable min State of Charge (%) | Battery Storage: maximum number of Cycles | Battery storage: Depth of Discharge (DoD) | Fixed Operating Cost ($/MW Net/year) | Variable Op Cost ($/MWh Net) | Variable Operating Cost for Carbon Capture and Storage (CCS) costs ($/MWh as gen) | Cost to operate in Synchronous condenser mode ($/MWh as gen) | Cold Start-up Notification Time (Hr) | Warm Start-up Notification Time (Hr) | Hot Start-up Notification Time (Hr) | Cold Start-up Costs ($/MW as gen) | Warm Start-up Costs ($/MW as gen) | Hot Start-up Costs ($/MW as gen) | Combustion Emissions (kg CO2-e/GJ of fuel) | Fugitive Emissions (kg CO2-e/GJ of fuel)
CCGT - With CCS | Thermal | Natural Gas
CCGT - Without CCS | Thermal | Natural Gas | 2019 | 380 | 348 | 389 | 25 | 40 | 2 | 95 | 0.66 | 46% | 2.5% |  | included in EFOR |  |  | included in EFOR |  |  |  | 3.5% |  | 1320 | 1320 | 7.863 | 7.068 | 50.9% |  | 12.8 | [8 empty] | 10900 | 3.7
OCGT - Without CCS | Thermal | Natural Gas | 2019 | 258 | 227 | 272 | 25 | 40 | 2 | 70 | 0.66 | 50% | 2% |  | included in EFOR |  |  | included in EFOR |  |  |  | 2% |  | 18000 | 18000 | 11.51 | 10.051 | 35.82% |  | 3 | [8 empty] | 12600 | 4.1
Reciprocating Engine | Thermal | Natural Gas/Diesel | 2019 | 211.2 | 209.1 | 209.1 | 25 | 40 | 2 | 43.33 | 0.83 | 40% | 1% |  | included in EFOR |  |  | included in EFOR |  |  |  | 2% |  | 2160 | 2160 | 11356 | 8790 | 40.9% |  | 2.7 | [8 empty] | 24100 | 7.6
Fuel cells | Storage | N/A | 2019 | 0.25 | 0.25 | 0.25 | 8 | 20 | < 1 | 26 | 0.5 | 2% | 2% |  | included in EFOR |  |  | included in EFOR |  |  |  | 2% |  | 2.1 | 2.1 | N/A | N/A | N/A |  | - | [8 empty] | 116000 | -
Large Scale Battery Storage (1hr) | Storage | N/A | 2019 | 25 | 24.46 | 24.46 | 10 | 20 | 1 | 8 | 0.5 | Near 0 | 2.16% |  | included in EFOR |  |  | included in EFOR |  |  |  | 1.5 - 3% |  | 10,000+ | 10,000+ | N/A | N/A | N/A |  | - |  |  | 91.5% | 91.5% | 0% | 100% | 3650 | 100% | 4833 | -
Large Scale Battery Storage (2hr) | Storage | N/A | 2019 | 25 | 23.97 | 23.97 | 10 | 20 | 1 | 8 | 0.6 | Near 0 | 4.12% |  | included in EFOR |  |  | included in EFOR |  |  |  | 1.5 - 3% |  | 10,000+ | 10,000+ | N/A | N/A | N/A |  | - |  |  | 92.5% | 92.5% | 0% | 100% | 3650 | 100% | 9717 | -
Large Scale Battery Storage (4hr) | Storage | N/A | 2019 | 25 | 23 | 23 | 10 | 20 | 1 | 12 | 0.75 | Near 0 | 8% |  | included in EFOR |  |  | included in EFOR |  |  |  | 1.5 - 3% |  | 10,000+ | 10,000+ | N/A | N/A | N/A |  | - |  |  | 93.5% | 93.5% | 0% | 100% | 3650 | 100% | 19239 | -
Large Scale Battery Storage (8hr) | Storage | N/A | 2019 | 25 | 21.06 | 21.06 | 10 | 20 | 1 | 12 | 0.75 | Near 0 | 15.76% |  | included in EFOR |  |  | included in EFOR |  |  |  | 1.5 - 3% |  | 10,000+ | 10,000+ | N/A | N/A | N/A |  | - |  |  | 95% | 95% | 0% | 100% | 3650 | 100% | 39314 | -
Flow Battery Storage (8hr) | Storage | N/A
Electrolysers | Storage | N/A | 2019 | 50 | N/A | N/A | 8 | 20 | 2 | 26 | 1.5 | 10% | N/A |  | included in EFOR |  |  | included in EFOR |  |  |  | 3% |  | N/A | N/A | N/A | N/A | N/A |  | 15 | [8 empty] | 54000 | -
Solar PV - Single axis tracking | Renewable | N/A | 2019 | 100 | 97.1 | 97.1 | 25 | 30 | 2 – 3 | 21 | 0.75 | Near 0 | 2.9% |  | included in EFOR |  |  | included in EFOR |  |  |  | 1.5% |  | Resource dependant | Resource dependant | N/A | N/A | N/A |  | - | [8 empty] | 16990 | -
Solar Thermal Central Receiver with storage | Renewable | N/A | 2019 | 150 | 135 | 135 | 25 | 40 | 2 – 3 | 78 | 1.5 | 20% | 10% |  | included in EFOR |  |  | included in EFOR |  |  |  | 3% |  | 6 | 6 | N/A | N/A | N/A |  | 7 | [8 empty] | 142500 | -
Solar Thermal Central Receiver without storage | Renewable | N/A
Wind - onshore | Renewable | N/A | 2019 | 210 | 194 | 210 | 25 | 30 | 3 – 5 | 52 | 1 | Near 0 | 3% |  | included in EFOR |  |  | included in EFOR |  |  |  | 3% |  | Resource dependent | Resource dependent | N/A | N/A | N/A |  | - | [8 empty] | 21930 | -
Wind - offshore | Renewable | N/A | 2019 | 1045 | 1003 | 1003 | 25 | 35 | 4 – 5 | 156 | 2 | Near 0 | 4% |  | included in EFOR |  |  | included in EFOR |  |  |  | 5% |  | Resource dependant | Resource dependant | N/A | N/A | N/A |  | - | [8 empty] | 157680 | -

## WP1 - Capacity Factors
Capacity Factors for new solar and wind generators
Approximate future capacity factors of renewable resources.
| 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Solar PV - Single axis tracking | 29 | 29.15 | 29.3 | 29.45 | 29.6 | 29.75 | 29.9 | 30.05 | 30.2 | 30.35 | 30.5 | 30.65 | 30.8 | 30.95 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
Wind - onshore | 40 | 40.3 | 40.6 | 40.9 | 41.2 | 41.5 | 41.8 | 42.1 | 42.4 | 42.7 | 43 | 43.3 | 43.6 | 43.9 | 44.2 | 44.5 | 44.8 | 45.1 | 45.4 | 45.7 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
Wind - offshore | 45 | 45.6 | 46.2 | 46.8 | 47.4 | 48 | 48.6 | 49.2 | 49.8 | 50.4 | 51 | 51.6 | 52.2 | 52.8 | 53.4 | 54 | 54.6 | 55.2 | 55.8 | 56.4 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57