## Disclaimer
Disclaimer
This transmission outlook workbook contains data provided by or collected from third parties, and conclusions, opinions, assumptions or forecasts that are based on that data. AEMO has made every effort to ensure the quality of the information in this workbook but cannot guarantee that the information and assumptions in it are accurate, complete or appropriate for your circumstances. This workbook does not include all of the information that an investor, participant or potential participant in the electricity or gas market might require, and does not amount to a recommendation of any investment. Anyone proposing to use the information in this workbook should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts. This dataset or the information in it may be subsequently updated or amended. This work does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed legal advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
• | make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this workbook; and
• | are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this workbook.

## NSW
New South Wales - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependant on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
QNI Minor | Uprate Liddell-Tamworth 330 kV line Uprate Liddell-Muswellbrook 330 kV line | Increase transfer between Queensland and New South Wales | ✓ | ✓ | ✓ | ✓ | ✓ | 150 (NSW to QLD) / 165-215 (QLD to NSW) | 122-228
| Uprate Liddell-Muswellbrook-Tamworth 330 kV line |  | ✓ | ✓ | ✓ | ✓ | ✓
| Install 330 kV capacitor banks at Armidale, Dumaresq and Tamworth |  | ✓ | ✓ | ✓ | ✓ | ✓
| Install dynamic reactive plant at Tamworth and Dumaresq |  | ✓ | ✓ | ✓ | ✓ | ✓
QNI Medium | New 500 kV Substations at Gunnedah/Narrabri, west of Dumaresq, Bulli Creek and Western Downs. | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 2E - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 885 (NSW to QLD) / 760 (QLD to NSW) / 2,000 (Note 1) | 1,040 - 1,925
| A 500 kV line from Wollar to Gunnedah/Narrabri to west of Dumaresq to Bulli Creek to Western Downs. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x 500/275 kV 1,500 MVA transformers at Western Downs |  | ✓ | ✓ | ✓ | ✓ | ✓
| 1 x 500/330 kV 1,500 MVA transformer at each Narrabri/Gunnedah, west of Dumaresq and Bulli Creek |  | ✓ | ✓ | ✓ | ✓ | ✓
| A 330 kV line from Gunnedah/Narrabri to Armidale/Uralla; A 330 kV line from west of Dumaresq to Dumaresq |  | ✓ | ✓ | ✓ | ✓ | ✓
| Static and dynamic reactive compensation at Wollar, Gunnedah/Narrabri, West Dumaresq, Bulli Creek and/or Western Downs |  | ✓ | ✓ | ✓ | ✓ | ✓
QNI Large | A second 500 kV circuit Wollar-Gunnedah/Narrabri-west of Dumaresq-Bulli Creek-Western Downs | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 3E - Input and Assumptions workbook) | ✓ | x | x | x | x | 885 (NSW to QLD) / 760 (QLD to NSW) / 2,000 (Note 2) | 675 - 1,250
VNI minor upgrade | Installation of a new 500/330 kV 1,000 MVA transformer at South Morang | Increase export from VIC to NSW. (VNI Option 1 - Input and Assumptions workbook)) | ✓ | ✓ | ✓ | ✓ | ✓ | 170 (VIC to NSW) | 56 - 105
| Uprate the South Morang-Dederang 330 kV lines and series capacitor; |  | ✓ | ✓ | ✓ | ✓ | ✓
| Install modular power flow controllers on both the Upper Tumut-Canberra 300 kV line and the Upper Tumut-Yass 330 kV line. |  | ✓ | ✓ | ✓ | ✓ | ✓
Humelink | Establish a new 500/330 kV substation in the Snowy Area (Maragle) Cut-in Lower Tumut-Upper Tumut 330 kV line into Maragle 3x500/330 1,500 MVA transformers | Increased renewable generation in Southern NSW Tablelands and Wagga REZs / Snowy 2.0 | ✓ | ✓ | ✓ | ✓ | ✓ | 2,040/1,000 (Note 3) | 945-1,755
| 1x500 kV line between Maragle and Bannaby 1x500 kV line between Wagga and Bannaby 1x500 kV line between Maragle and Wagga |  | ✓ | ✓ | ✓ | ✓ | ✓
| Establish 500 kV substation at Wagga 2x500/330 kV 1500 MVA transformers at Wagga |  | ✓ | ✓ | ✓ | ✓ | ✓
| Power flow controller on the Bannaby-Sydney West 330 kV line (Line #39) to limit power flow |  | ✓ | ✓ | ✓ | ✓ | ✓
VNI West | VNI Option 7: 2x500 kV lines from North Ballarat to Bendigo to Kerang to Darlington Point to Wagga; 2x500/220 kV transformers at Bendigo and Kerang and 2x500/330 kV transformers at Darlington Point 1x500/330 kV transformer at Wagga Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at Bendigo, Kerang, Darlington Point and Wagga Wagga | Increase transfers between Victoria and New South Wales; Increased renewable generation in Murray, Western Victoria and South West New South Wales REZs. (VNI Option 7 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | x | 1,930 (VIC to NSW) / 1,800 (NSW to VIC) / 4,000 (Note 4) | 1,300 - 2,410
| VNI Option 6 (an alternative to VNI Option 7): 2x500 kV lines from North Ballarat to Shepparton to Wagga; 2x500/220 kV transformers at Shepparton. 1x500/330 kV transformer at Wagga Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at North Ballarat, Shepparton, and Wagga Wagga | Increase transfers between Victoria and New South Wales; Increased renewable generation in Western Victoria, Central North Victoria and Wagga Wagga REZs. (VNI Option 6 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | x | 1,930 (VIC to NSW) / 1,800 (NSW to VIC) / 3,000 (Note 5) | 940 - 1,730
Project EnergyConnect | A new double circuit Robertstown-Buronga-Darlington Point 330 kV line | Increase transfers between South Australia and New South Wales. Increased renewable generation in Riverland, South West NSW and Murray River (EnergyConnect - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 800 (NSW to SA) / 800 (SA to NSW) / 1,980 (Note 6) | 1,530 (Note 7)
| An additional 330 kV single circuit from Darlington Point to Wagga. |  | ✓ | ✓ | ✓ | ✓ | ✓
| A new double circuit 220 kV line (conductor strung on one side and operated as a single circuit) from Buronga to Red Cliffs. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 275/330 kV transformers at Robertstown. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 3 x 330 kV phase shift transformers at Buronga. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x 330/220 kV transformers at Buronga |  | ✓ | ✓ | ✓ | ✓ | ✓
| Turn Robertstown-Para 275 kV line into Tungkillo |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x +100/-100 MVAr synchronous condensers at Buronga 330 kV |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x +100/-100 MVAr synchronous condensers at Darlington Point 330kV |  | ✓ | ✓ | ✓ | ✓ | ✓
| Shunt capacitor banks at Robertstown, Buronga and Darlington Point substations |  | ✓ | ✓ | ✓ | ✓ | ✓
| Shunt line reactors at Robertstown, Buronga and Darlington Point (on the Robertstown-Buronga-Darlington Point 330 kV lines |  | ✓ | ✓ | ✓ | ✓ | ✓
| Special protection scheme to detect and manage loss of either interconnection of VIC-SA or NSW-SA |  | ✓ | ✓ | ✓ | ✓ | ✓
Northern NSW | A new second 500 kV circuit Wollar-Gunnedah/Narrabri | Increase in generation in North West NSW | x | ✓ | ✓ | ✓ | x | 1000 | 200-370
| Two 500/330 kV 1,500 MVA transformers at Gunnedah/Narrabri | Increase in generation in North West NSW | ✓ | ✓ | ✓ | ✓ | x | 5000 | 820-1,520
| A new double circuit Gunnedah-Narrabri 330 kV line (dependant on connection interest in the area) | Increase in generation in North West NSW | • | ✓ | ✓ | • | x
| Establish a new Uralla 500/330 kV substation | Increase in generation in New England | ✓ | ✓ | ✓ | ✓ | x
| Turn both Armidale–Tamworth 330 kV lines 85 and 86 into Uralla | Increase in generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| A new double circuit Uralla–Bayswater 500 kV line, string one side (route passing nearby Walcha) | Increased in renewable generation in New England | ✓ | ✓ | ✓ | ✓ | x
| Power flow controllers on the Uralla–Tamworth 330 kV line | Increased in renewable generation in New England | ✓ | ✓ | ✓ | ✓ | x
| A new single circuit Uralla–Gunnedah/Narrabri 500 kV line | Increased in renewable generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| Two 500/330 kV 1,500 MVA Uralla transformers | Increased in renewable generation in New England | ✓ | ✓ | ✓ | ✓ | x
| One 500/330 kV 1,500 MVA Bayswater transformer | Increased in renewable generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| Additional reactive support | Increased in renewable generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| Third single circuit Gunnedah/Narrabri–Bayswater/Wollar 500 kV line | Increase generation in North West NSW | ✓ | ✓ | ✓ | ✓ | x | 3000 | 290-535
| String vacant circuit on Bayswater–Uralla 500 kV line | Increased in renewable generation in New England | ✓ | ✓ | ✓ | x | x
| Two 500/330 kV transformers at Gunnedah/Narrabri | Increased in renewable generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| A new Walcha 500/330 kV Substation, turn Bayswater - Uralla into Walcha (dependant on connection interest in the area). | Increased in renewable generation in New England | • | ✓ | • | x | x |  |  | done
| Two 500/330 kV 1,500 MVA Walcha transformers | Increased in renewable generation in New England | • | ✓ | • | x | x
Central NSW | 1x 500/330 kV transformer at Wollar (second) and 330 kV switchgear | Increased in renewable generation in Central West NSW REZ | ✓ | ✓ | ✓ | ✓ | x | 700 | 35
| Establish a new 330 kV substation Central West Hub |  | ✓ | ✓ | ✓ | x | x | 1000 | 430
| A new double circuit Central West Hub - Wollar 330 kV line |  | ✓ | ✓ | ✓ | x | x
| A new single circuit Central West Hub - Wellington 330 kV line |  | ✓ | ✓ | ✓ | x | x
| Third Mount Piper-Wallerawang 330 kV line | Coal retirement within NSW (timing is indicative). The sequence of works and the timing is highly influenced load distribution, battery storage locations, and potential line upratings within Sydney/Wollongong/Newcastle load centre | ✓ | ✓ | ✓ | ✓ | ✓ | 2,000-2,500 | 375 - 700
| Third Bayswater-Liddell 330 kV line |  | ✓ | ✓ | ✓ | ✓ | ✓
| Establish 500/330 kV substation at South Creek |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2x500 kV line from Bannaby to South Creek Cut-in both Eraring-Kemps Creek 500 kV lines at South Creek |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2x500/330 kV transformers at South Creek 1x500/330 kV transformer at Bannaby |  | ✓ | ✓ | ✓ | ✓ | ✓
| 1x330 kV line from South Creek to Sydney West |  | ✓ | ✓ | ✓ | ✓ | ✓
| Cut-in Bayswater-Sydney West line at South Creek Cut-in Regentville-Sydney West 330 kV line at South Creek |  | ✓ | ✓ | ✓ | ✓ | ✓
| Two 500 kV lines from Bayswater to Eraring |  | ✓ | ✓ | ✓ | ✓ | ✓ | 2,000-2,500 | 290 - 540
Note 1 | Increase in transfer is in addition to QNI minor. Network capacity for additional generation is ~1,000 MW in Queensland and ~1,000 MW in New South Wales
Note 2 | Increase in transfer is in addition to QNI minor and QNI medium. Network capacity for additional generation additional to QNI 2E ~1,000 MW in Queensland and ~1,000 MW in New South Wales
Note 3 | Increase in REZ by 1000 MW between Southern New South Wales Tablelands and Wagga Wagg REZ. Increase for Snowy 2.0 of 2040 MW
Note 4 | Network capacity for additional generation ~4,000 MW of which ~1,000 MW is in NSW within South West NSW
Note 5 | Network capacity for additional generation ~3,000 MW in Victoria
Note 6 | Project EnergyConnect allows for additional generation of 1,980 MW, of which 600 MW is within NSW
Note 7 | Cost estimates are consistent with ElectraNet's South Australia Energy Transformation RIT-T (i.e. Project EnergyConnect).

## QLD
Queensland - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
QNI Minor | Uprate Liddell-Tamworth 330 kV line Uprate Liddell-Muswellbrook 330 kV line | Increase transfer between Queensland and New South Wales | ✓ | ✓ | ✓ | ✓ | ✓ | 150 (NSW to QLD) / 165-215 (QLD to NSW) | 122-228
| Uprate Liddell-Muswellbrook-Tamworth 330 kV line |  | ✓ | ✓ | ✓ | ✓ | ✓
| Install 330 kV capacitor banks at Armidale, Dumaresq and Tamworth |  | ✓ | ✓ | ✓ | ✓ | ✓
| Install dynamic reactive plant at Tamworth and Dumaresq |  | ✓ | ✓ | ✓ | ✓ | ✓
QNI Medium | New 500 kV substations at Gunnedah/Narrabri, west of Dumaresq, Bulli Creek and Western Downs | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 2E - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 885 (NSW to QLD) / 760 (QLD to NSW) / 2,000 (Note 1) | 1,040 - 1,925
| A 500 kV line from Wollar to Gunnedah/Narrabri to west of Dumaresq to Bulli Creek to Western Downs |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x 500/275 kV 1500 MVA transformers at Western Downs |  | ✓ | ✓ | ✓ | ✓ | ✓
| 1 x 500/330 kV 1500 MVA transformer at each Narrabri/Gunnedah, west of Dumaresq and Bulli Creek |  | ✓ | ✓ | ✓ | ✓ | ✓
| A 330 kV line from Gunnedah/Narrabri to Armidale/Uralla; A 330 kV line from west of Dumaresq to Dumaresq |  | ✓ | ✓ | ✓ | ✓ | ✓
| Static and dynamic reactive compensation at Wollar, Gunnedah/Narrabri, West Dumaresq, Bulli Creek and/or Western Downs |  | ✓ | ✓ | ✓ | ✓ | ✓
QNI Large | A second 500 kV circuit Wollar-Gunnedah/Narrabri-west of Dumaresq-Bulli Creek-Western Downs | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 3E - Input and Assumptions workbook) | ✓ | x | x | x | x | 885 (NSW to QLD) / 760 (QLD to NSW) / 2,000 (Note 2) | 675 - 1,250
Far North Queensland | Rebuild the Ross- Chalumbin 275 kV double circuit line to a higher capacity. | Increased in wind generation in Far North Queensland Assets renewal - timing could be brought forward and capacity increased | ✓ | ✓ | ✓ | ✓ | x | 600 | Assets renewal (200-325)
| Additional single circuit Ross-Chalumbin 275 kV line | Increased in wind generation in Far North Queensland | ✓ | ✓ | ✓ | ✓ | x | 500-800 | 195-350
| Increase rating on lower rated Ross-Strathmore 275 kV line |  | ✓ | ✓ | ✓ | ✓ | x |  | 10.5-19.5
| A new single circuit from Chalumbin-Walkamin-Lakeland |  | • | • | • | • | x | - | 231-429
| A new Chalumbin - Millstream 275 kV line, turn Chalumbin - Woree 275 kV line into Millstream (Note 4) |  | • | • | • | • | x | - | 45-85
Gladstone Grid section | A new double circuit Calvale-Larcom Creek 275 kV line | Retirement of Gladstone generation and increased renewable generation in Northern QLD | ✓ | ✓ | ✓ | ✓ | ✓ | 1200 | 67-124
| An additional 275/132 kV transformer at Calliope River (third) |  | ✓ | ✓ | ✓ | ✓ | ✓ |  | 10.5-19.5
| Rebuild the Bouldercombe-Calliope River 275 kV line as Bouldercombe-Larcom Creek-Calliope River 275 kV line with high thermal capacity; and | Asset renewal, Gladstone retirement and increase in high VRE in Northern QLD Timing could be brought forward with retirement of Gladstone generation. | ✓ | ✓ | ✓ | ✓ | ✓ |  | Asset Renewal (98-182)
Central to Southern Queensland | A new double Calvale-Wandoan South 275 kV line | Increased in renewable generation in Central and Northern Queensland | ✓ | ✓ | ✓ | ✓ | x | 900 | 226-420
South West Queensland | Additional infrastructure to be determined to incorporate projected wind and solar resources (Note 5) | Increased in renewable generation within Darling Downs REZ | x | ✓ | ✓ | x | x | 4,000-8,000 | Note 3
Note 1 | Increase in transfer is in addition to QNI minor. Network capacity for additional generation is ~1,000 MW in Queensland and ~1,000 MW in New South Wales.
Note 2 | Increase in transfer is in addition to QNI minor and QNI medium. Network capacity for additional generation additional to QNI 2E ~1,000 MW in Queensland and ~1,000 MW in New South Wales.
Note 3 | Transmission network augmentation and possible storage for Darling Downs under the step and fast change scenario is to be investigated for the final 2020 ISP.

## SA
South Australia - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
Mid North SA | Rebuild of Davenport-Brinkworth-Templers West-Para 275 kV line | Increased renewable generation. Timing is also influenced by the retirement of gas generation within South Australia | ✓ | ✓ | ✓ | ✓ | x | 1000 | 265-475
South East SA | String vacant circuit between Tailem Bend and Tungkillo Install reactive compensation. Where necessary manage generation with control schemes such as runback schemes. | Increased renewable generation with South East South Australia | ✓ | ✓ | ✓ | ✓ | ✓ | 400-600 (Note 1) | 20-80
Project EnergyConnect | A new double circuit Robertstown-Buronga-Darlington Point 330 kV line | Increase transfers between South Australia and New South Wales. Increased renewable generation in Riverland, South West NSW and Murray River. (EnergyConnect - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 800 (NSW to SA) / 800 (SA to NSW) / 1,980 (Note 2) | 1,530 (Note 3)
| An additional 330 kV single circuit from Darlington Point to Wagga. |  | ✓ | ✓ | ✓ | ✓ | ✓
| A new double circuit 220 kV line (conductor strung on one side and operated as a single circuit) from Buronga to Red Cliffs. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 275/330 kV transformers at Robertstown. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 3 x 330 kV phase shift transformers at Buronga. |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x 330/220 kV transformers at Buronga |  | ✓ | ✓ | ✓ | ✓ | ✓
| Turn Robertstown-Para 275 kV line into Tungkillo |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x +100/-100 MVAr synchronous condensers at Buronga 330 kV |  | ✓ | ✓ | ✓ | ✓ | ✓
| 2 x +100/-100 MVAr synchronous condensers at Darlington Point 330 kV |  | ✓ | ✓ | ✓ | ✓ | ✓
| Shunt capacitor banks at Robertstown, Buronga and Darlington Point substations |  | ✓ | ✓ | ✓ | ✓ | ✓
| Shunt line reactors at Robertstown, Buronga and Darlington Point (on the Robertstown-Buronga-Darlington Point 330 kV lines |  | ✓ | ✓ | ✓ | ✓ | ✓
| Special protection scheme to detect and manage loss of either interconnection of VIC-SA or NSW-SA |  | ✓ | ✓ | ✓ | ✓ | ✓
Roxby Downs | Establish 275/132 kV connection point at Mount Gunson South. A new Davenport-Mount Gunson South 275 kV line | Committed project | ✓ | ✓ | ✓ | ✓ | ✓ | 450-650 | -
Eyre Peninsula | A double circuit Cultana - Yadnarie 275 kV line energised at 132 kV A double circuit Yadnarie-Port Lincoln 132 kV line | Committed project - End of life replacements and improved reliability of supply | ✓ | ✓ | ✓ | ✓ | ✓ | 470 | 240 (Note 4)
Note 1 | Runback schemes can further increase capacity.
Note 2 | Project EnergyConnect allows for additional generation of 1,980 MW - Including Riverland, Murray River and South West NSW REZs.
Note 3 | Cost estimates aligned with SAET PACR.
Note 4 | Cost estimates aligned with Eyre Peninsula Electricity Supply Options PACR.

## TAS
Tasmania - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
Marinus Link | 1x750 MW HVDC link between Burnie area in Tasmania and Latrobe Valley in Victoria | Marinus Link 750 MW option 3 | ✓ | x | ✓ | ✓ | x | 750 (TAS to VIC) / 500 (VIC to TAS) / 1,140 (Note 1) | 1,150 - 2,130
| A new 220 kV switching station in the Burnie area adjacent to the converter station. A new double-circuit 220 kV transmission line from Burnie to Sheffield and decommissioning of the existing 220 kV single-circuit transmission line in this corridor. A new double-circuit 220 kV transmission line from Palmerston to Sheffield. | Marinus Link option 3 and/or Wind generation in NWTAS | ✓ | x | ✓ | ✓ | x
| First 750 MW HVDC link between Burnie area in Tasmania and Latrobe Valley in Victoria | Marinus Link option 4 and/or Wind generation in NWTAS (Note 3) | x | ✓ | x | x | x | 1,500 (TAS to VIC) / 1,250 (VIC to TAS) (Note 2) | 1,935-3,590
| A new 220 kV switching station in the Burnie area adjacent to the converter station. A new double-circuit 220 kV transmission line from Burnie to Sheffield and decommissioning of the existing 220 kV single-circuit transmission line in this corridor. A new double-circuit 220 kV transmission line from Palmerston to Sheffield. |  | x | ✓ | x | x | x
| Second 750 MW HVDC link between Burnie area in Tasmania and Latrobe Valley in Victoria |  | x | ✓ | x | x | x
| A new double-circuit 220 kV transmission line from Burnie to Staverton via Hampshire. A new 220 kV switching station at Staverton. |  | x | ✓ | x | x | x
Midlands | A new double circuit Palmerston - Sheffield 220 kV line A new double circuit Palmerston - Waddamana 220 kV line | Increased renewable generation in Tasmania Midlands | x | ✓(Note 3) | x | x | x | 800 | 140-260
Note 1 | Network capacity for additional generation is ~1,140 MW.
Note 2 | Network capacity for additional generation within REZs in Tasmania will be further investigated for the final 2020 ISP.
Note 3 | Additional build may still be required under the step change scenario. This requirement may change, if additional new generation were to be located in North West Tasmania. This will be investigated for the final 2020 ISP.

## VIC
Victoria - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
VNI minor upgrade | Installation of a new 500/330 kV 1,000 MVA transformer at South Morang | Increase export from VIC to NSW. (VNI Option 1 - Input and Assumptions workbook)) | ✓ | ✓ | ✓ | ✓ | ✓ | 170 (VIC to NSW) | 56 - 105
| Uprate the South Morang-Dederang 330 kV lines and series capacitor; |  | ✓ | ✓ | ✓ | ✓ | ✓
| Install modular power flow controllers on both the Upper Tumut-Canberra 300 kV line and the Upper Tumut-Yass 330 kV line. |  | ✓ | ✓ | ✓ | ✓ | ✓
VNI West | VNI Option 7: 2x500 kV lines from North Ballarat to Bendigo to Kerang to Darlington Point to Wagga; 2x500/220 kV transformers at Bendigo and Kerang and 2x500/330 kV transformers at Darlington Point 1x500/330 kV transformer at Wagga Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at Bendigo, Kerang, Darlington Point and Wagga Wagga | Increase transfers between Victoria and New South Wales; Increased renewable generation in Murray, Western Victoria and South West New South Wales REZs. (VNI Option 7 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | x | 1,930 (VIC to NSW) / 1,800 (NSW to VIC) / 4,000 (Note 1) | 1,300 - 2,410
| VNI Option 6 (an alternative to VNI Option 7): 2x500 kV lines from North Ballarat to Shepparton to Wagga; 2x500/220 kV transformers at Shepparton. 1x500/330 kV transformer at Wagga Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at North Ballarat, Shepparton, and Wagga Wagga | Increase transfers between Victoria and New South Wales; Increased renewable generation in Western Victoria, Central North Victoria and Wagga Wagga REZs. (VNI Option 6 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | x | 1,930 (VIC to NSW) / 1,800 (NSW to VIC) / 3,000 (Note 2) | 940 - 1,730
Latrobe Valley (LV) | Reconfigure Hazelwood 220 kV switchyard to utilise Hazelwood/Yallourn-Rowville 220 kV lines | Retirement of Yallourn power station | ✓ | ✓ | ✓ | ✓ | ✓ | 1,100-1,400 | TBA (Note 3)
Central VIC | Installation of wind monitoring equipment and the upgrade of station limiting on: - Red Cliffs–Wemen 220 kV line - Wemen–Kerang 220 kV line - Kerang–Bendigo 220 kV line - Moorabool–Terang 220 kV line - Ballarat–Terang 220 kV line | Increased renewable generation in Western Victoria and Murray REZs | ✓ | ✓ | ✓ | ✓ | ✓ | 450 (Note 4) | 5.5 (Note 5)
| A new terminal station at North Ballarat A new 500 kV double circuit transmission line from Sydenham to North Ballarat 2 x 500/220 kV transformers at North Ballarat. |  | ✓ | ✓ | ✓ | ✓ | ✓ |  | 473 (Note 5)
| A new 220 kV double circuit transmission line form North Ballarat to Bulgana (via Waubra) |  | ✓ | ✓ | ✓ | ✓ | ✓
| Move the Waubra Terminal Station connection from the existing Ballarat–Ararat 220 kV line to one of the North Ballarat–Bulgana 220 kV lines. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Cut-in the existing Ballarat–Bendigo 220 kV line at North Ballarat. Cut-in the existing Moorabool–Ballarat No.2 220 kV at Elaine Terminal Station |  | ✓ | ✓ | ✓ | ✓ | ✓
| Additional 3rd Red Cliffs-Buronga 220 kV line (Note 6) |  | ✓ | ✓ | ✓ | ✓ | x | 400 | 5.6-10.4 (Note 7)
South West Victoria | Moorabool - Mortlake 500 kV line | Increased renewable generation in South West Victoria (Note 6) | x | ✓ | ✓ | x | x | 2000 | 175-325
| Additional Moorabool 500/220 kV Moorabool transformer |  | x | ✓ | ✓ | x | x | 1000 | 18-33
Note 1 | Network capacity for additional generation ~4,000 MW of which ~3,000 MW is in Victoria. Additional generation of 2,000 MW for Murray REZ and 1,000 MW for Western Victoria REZ.
Note 2 | Network capacity for additional generation ~3,000 MW. Additional generation of 2,000 MW for Shepparton REZ, 1,000 MW for Western Victoria REZ.
Note 3 | Mainly switching reconfiguration of the existing assets.
Note 4 | In addition to the existing and committed generation as of 8 August 2019.
Note 5 | Cost estimates aligned with Western Victoria Renewable Integration PACR.
Note 6 | Additional infrastructure may be required, to be determine for the final 2020 ISP.
Note 7 | Cost estimate is to string vacant circuit on the 220 kV line developed as part of Project EnergyConnect.