## Index
Supply Demand Outlook and Network Limitation Information
Please note that the data format may need to be adjusted in order to view the data to the level of fidelity required. For example, you may need to format the cell to a more appropriate number of decimal places in some cases as desired.
About
This spreadsheet contains the generation and transmission outlook for the 2015 NTNDP Gradual Evolution scenario. For a complete description of the scenarios and sensitivities, please see Appendix A of 2015 NTNDP main report.
http://www.aemo.com.au/Electricity/Planning/National-Transmission-Network-Development-Plan
Index Table
Tab Name | Content Description
NEMInstalledCapacity Figure | Total NEM installed capacity by technology (MW) and total NEM installed capacity by technology and zone (MW), yearly resolution for period 2015–16 to 2034–35.
NEMInstalledCapacity Data
NEMEnergyGenerated Figure | Total NEM generated energy by technology (TWh) and total NEM generated energy by technology and zone (GWh), yearly resolution for period 2015–16 to 2034–35.
NEMEnergyGenerated Data
NewAndRetiredCapacity Figure | Cumulative NEM total new entry and retired capacity by technology (MW) and cumulative NEM total new entry and retired capacity by technology and zone, yearly resolution for period 2015–16 to 2034–35.
NewAndRetiredCapacity Data
GenerationInvestment | Generation investment across the NEM ($ million), yearly resolution for period 2015–16 to 2034–35.
GenerationConnectionCosts | New entry generation connection costs across the NEM ($ million), yearly resolution for period 2015–16 to 2034–35.
EconomicDispatchLimitations | The economic dispatch limitations which emerged under each scenario over the next 20 years.
NetworkLimitationCosts | The network limitations which emerged under each scenario over the next 20 years.
CommittedNetworkCosts | A description of committed transmission network projects in the NEM

## NEMInstalledCapacity Data
Total NEM Installed Capacity by Technology (MW)
Region | Technology | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
NEM | Black Coal | 18426 | 18426 | 18426 | 18426 | 18426 | 18426 | 18426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426 | 16426
| Brown Coal | 6806 | 6806 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260
| Hydro | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5 | 7568.5
| Liquid Fuel | 694 | 694 | 694 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 597 | 597 | 597 | 597 | 597 | 597 | 597 | 597 | 597
| Natural Gas | 9863.5 | 9863.5 | 9263.5 | 9136.8184 | 9293.8489 | 9293.8489 | 9293.8489 | 9293.8489 | 9293.8489 | 9293.8489 | 9293.8489 | 9293.8489 | 9904.9586 | 9904.9586 | 10875.4831 | 11298.8273 | 11576.6794 | 11666.3235 | 11666.3235 | 12540.9166
| Large Scale PV | 109 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
| Wind | 3583.49 | 3583.49 | 3823.49 | 6581.9845 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478 | 8568.4478
| Biomass | 0 | 0 | 0 | 75 | 75 | 151.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106
| Rooftop PV | 5001.5809 | 5840.9643 | 6698.081 | 7570.4428 | 8463.482 | 9367.7383 | 10274.4738 | 11158.7753 | 12017.9146 | 12861.1591 | 13692.9036 | 14514.6738 | 15329.5021 | 16140.6899 | 16944.9365 | 17731.6952 | 18512.6381 | 19304.0672 | 20098.1132 | 20890.3876
| Storage | 7.816 | 135.3462 | 252.4316 | 404.53 | 592.3914 | 796.9828 | 1007.8406 | 1223.0211 | 1440.2111 | 1658.1602 | 1877.2876 | 2095.2703 | 2315.8406 | 2534.1165 | 2752.5181 | 2972.7594 | 3194.8093 | 3420.0709 | 3641.0514 | 3857.5187
| Total | 52059.8869 | 53128.8005 | 53197.0026 | 56894.2758 | 60118.67 | 61303.9284 | 62471.5217 | 61571.0036 | 62647.3329 | 63708.5265 | 64759.3984 | 65736.1513 | 67382.6596 | 68412.1233 | 70405.2961 | 71835.6402 | 73116.4851 | 74222.8199 | 75237.8464 | 77121.1812
Region | Technology | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
NSW | Black Coal | 10240 | 10240 | 10240 | 10240 | 10240 | 10240 | 10240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240 | 8240
| Brown Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525 | 2525
| Liquid Fuel | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Natural Gas | 1978.9 | 1978.9 | 1978.9 | 1808 | 1808 | 1808 | 1808 | 1808 | 1808 | 1808 | 1808 | 1808 | 2223.0972 | 2223.0972 | 2604.7282 | 2805.258 | 3036.0614 | 3065.4003 | 3065.4003 | 3570.4793
| Large-scale PV | 109 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
| Wind | 650.7 | 650.7 | 650.7 | 1900.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7 | 3150.7
| Biomass | 0 | 0 | 0 | 0 | 0 | 75 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
| Rooftop PV | 1235.352 | 1428.3678 | 1624.5098 | 1823.3934 | 2025.6426 | 2230.8323 | 2440.7206 | 2653.0371 | 2867.8841 | 3085.585 | 3306.2745 | 3529.7702 | 3756.4781 | 3986.0642 | 4217.972 | 4450.5861 | 4685.895 | 4926.6357 | 5172.4282 | 5423.7133
| Storage | 0.016927 | 54.9874 | 96.4238 | 142.8388 | 196.8566 | 254.7505 | 314.5422 | 376.0033 | 438.904 | 503.1393 | 568.3885 | 634.5412 | 701.3389 | 768.6749 | 836.4426 | 907.0805 | 979.0391 | 1052.0517 | 1126.0099 | 1200.8079
QLD | Black Coal | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186 | 8186
| Brown Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4 | 652.4
| Liquid Fuel | 457.5 | 457.5 | 457.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5 | 423.5
| Natural Gas | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2608.3 | 2668.6052 | 2668.6052 | 3096.1193
| Large-scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 0 | 0 | 0 | 388.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945 | 588.4945
| Biomass | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rooftop PV | 1829.1792 | 2149.965 | 2473.6607 | 2800.5225 | 3131.7942 | 3459.9251 | 3761.9614 | 4039.7001 | 4299.614 | 4546.2829 | 4782.9136 | 5011.5215 | 5234.1777 | 5451.9417 | 5665.3269 | 5874.2134 | 6080.9124 | 6288.0527 | 6495.7273 | 6704.5388
| Storage | 7.7847 | 30.1983 | 60.7691 | 102.1185 | 164.2191 | 231.415 | 294.7909 | 355.4293 | 413.9653 | 470.5063 | 524.8405 | 577.3174 | 631.8336 | 684.4018 | 735.2093 | 784.9436 | 834.3488 | 885.2659 | 935.739 | 985.7434
SA | Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brown Coal | 546 | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Fuel | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 123.5 | 123.5 | 123.5 | 123.5 | 123.5 | 123.5 | 123.5 | 123.5 | 123.5
| Natural Gas | 2716.3 | 2716.3 | 2236.3 | 2280.5184 | 2437.5489 | 2437.5489 | 2437.5489 | 2437.5489 | 2437.5489 | 2437.5489 | 2437.5489 | 2437.5489 | 2466.4055 | 2466.4055 | 2766.4055 | 2989.2198 | 3036.2686 | 3036.2686 | 3036.2686 | 3036.2686
| Large-scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 1473 | 1473 | 1473 | 1973 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632 | 2409.4632
| Biomass | 0 | 0 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Rooftop PV | 769.1359 | 875.6634 | 989.3416 | 1106.83 | 1230.5766 | 1358.3803 | 1497.821 | 1632.5506 | 1754.4101 | 1863.713 | 1963.6517 | 2055.3195 | 2141.1499 | 2221.6248 | 2296.6367 | 2363.9193 | 2426.0271 | 2486.8101 | 2545.7988 | 2603.4602
| Storage | 0 | 0 | 0.9372 | 9.3489 | 19.3974 | 31.9677 | 49.7225 | 66.5789 | 82.8831 | 98.7081 | 115.2879 | 131.0124 | 145.7809 | 159.6519 | 172.6703 | 185.2215 | 197.6053 | 209.7435 | 221.6192 | 233.1588
VIC | Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brown Coal | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260 | 6260
| Hydro | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221 | 2221
| Liquid Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2382 | 2549.1559 | 2549.1559 | 2838.0494 | 2838.0494 | 2838.0494 | 2838.0494 | 2838.0494 | 2838.0494
| Large-scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 1151.79 | 1151.79 | 1391.79 | 1691.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79 | 1791.79
| Biomass | 0 | 0 | 0 | 25 | 25 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106 | 26.4106
| Rooftop PV | 1054.192 | 1252.1383 | 1453.7759 | 1659.8493 | 1871.0389 | 2088.1395 | 2315.2913 | 2546.1684 | 2779.3755 | 3018.1626 | 3260.8631 | 3507.7083 | 3759.0838 | 4016.3367 | 4276.0109 | 4531.9612 | 4788.1388 | 5051.7643 | 5315.4105 | 5573.4015
| Storage | 0.014164 | 48.7679 | 90.1732 | 142.977 | 200.9339 | 263.4238 | 328.4531 | 399.2386 | 471.9568 | 546.148 | 621.6252 | 698.3625 | 776.2451 | 854.7553 | 936.0788 | 1018.3338 | 1101.9335 | 1186.7465 | 1267.3447 | 1343.6547
TAS | Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brown Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1 | 2170.1
| Liquid Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas | 178 | 178 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0
| Large-scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 308 | 308 | 308 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628 | 628
| Biomass | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rooftop PV | 113.7218 | 134.8298 | 156.793 | 179.8477 | 204.4296 | 230.461 | 258.6794 | 287.3192 | 316.6309 | 347.4156 | 379.2007 | 410.3543 | 438.6126 | 464.7225 | 488.9901 | 511.0152 | 531.6648 | 550.8044 | 568.7483 | 585.2737
| Storage | 0.0002508 | 1.3926 | 4.1283 | 7.2468 | 10.9844 | 15.4258 | 20.3319 | 25.771 | 32.5019 | 39.6585 | 47.1455 | 54.0368 | 60.6421 | 66.6326 | 72.1171 | 77.18 | 81.8826 | 86.2633 | 90.3386 | 94.1539

## NEMEnergyGenerated Data
Total NEM Generated Energy by Technology (TWh)
Region | Technology | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
NEM | Black Coal | 112.1107 | 118.5804 | 122.7182 | 114.5946 | 108.7951 | 109.2061 | 109.1594 | 110.1683 | 111.9322 | 114.0071 | 115.4012 | 116.9631 | 118.1003 | 120.0848 | 122.1835 | 125.0501 | 126.5482 | 128.9327 | 130.8516 | 132.8059
| Brown Coal | 57.7847 | 55.986 | 52.9762 | 52.9762 | 53.1199 | 52.7741 | 52.5898 | 52.8134 | 52.9298 | 52.5885 | 53.1907 | 53.1907 | 53.3364 | 53.1907 | 53.1907 | 53.1907 | 53.3364 | 53.1907 | 53.1907 | 53.1907
| Hydro | 15.3639 | 15.419 | 15.4191 | 15.3559 | 15.0791 | 15.419 | 15.421 | 15.425 | 15.45 | 15.2577 | 15.2335 | 15.4266 | 15.4863 | 15.443 | 15.4329 | 15.9102 | 15.8561 | 15.8554 | 15.9916 | 15.9918
| Liquid Fuel | 0 | 0 | 0.00014962 | 0 | 0.000104 | 0 | 0 | 0 | 0 | 0.000142 | 0 | 0 | 0 | 3.7728e-06 | 0 | 5e-05 | 0 | 0 | 0 | 0
| Natural Gas | 1.1425 | 1.2679 | 1.4677 | 0.51583 | 0.24508 | 0.22042 | 0.20869 | 0.4209 | 0.57579 | 0.58985 | 0.62698 | 0.68865 | 1.0056 | 1.1903 | 1.562 | 1.4004 | 1.8129 | 2.1294 | 2.8005 | 3.8121
| Large Scale PV | 0.21251 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249
| Wind | 12.1222 | 12.1286 | 12.6881 | 22.028 | 28.9797 | 29.0109 | 28.9935 | 28.9444 | 28.7067 | 28.8323 | 28.8861 | 28.9991 | 29.139 | 28.6485 | 28.7405 | 28.8914 | 29.0529 | 28.9741 | 28.9104 | 28.6356
| Biomass | 0 | 0 | 0 | 0.5256 | 0.29623 | 1.0611 | 1.4115 | 1.4115 | 1.4154 | 1.4115 | 1.4115 | 1.4115 | 1.4154 | 1.4115 | 1.4115 | 1.4115 | 1.4154 | 1.4115 | 1.4115 | 1.4115
| Rooftop PV | 6.1003 | 7.192 | 8.3112 | 9.4502 | 10.6148 | 11.8023 | 12.9951 | 14.1717 | 15.3144 | 16.4267 | 17.5204 | 18.5985 | 19.6643 | 20.7224 | 21.773 | 22.8062 | 23.8213 | 24.8422 | 25.8728 | 26.902
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | 204.8367 | 211.0363 | 214.043 | 215.9087 | 217.5936 | 219.9563 | 221.2415 | 223.8176 | 226.7877 | 229.5762 | 232.7328 | 235.7406 | 238.6109 | 241.1537 | 244.7565 | 249.123 | 252.3066 | 255.7985 | 259.4916 | 263.2121
Region | Technology | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
NSW | Black Coal | 56.6324 | 61.8253 | 65.9631 | 57.8395 | 51.8846 | 52.451 | 52.4044 | 53.4132 | 55.0216 | 57.252 | 58.6461 | 60.208 | 61.0041 | 63.0541 | 64.5188 | 66.7504 | 67.7326 | 68.3928 | 68.3928 | 68.3928
| Brown Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 2.8991 | 2.8916 | 2.891 | 2.8941 | 2.8966 | 2.8911 | 2.8927 | 2.896 | 2.9017 | 2.8956 | 2.8953 | 2.8947 | 2.9131 | 2.9018 | 2.8984 | 3.3154 | 3.2229 | 3.1098 | 3.1744 | 3.1837
| Liquid Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas | 0 | 0 | 0 | 0 | 0 | 0.000855 | 0.003055 | 0.026859 | 0.092089 | 0.073548 | 0.10582 | 0.11321 | 0.25157 | 0.27617 | 0.41525 | 0.44327 | 0.50397 | 0.61156 | 0.83539 | 0.79605
| Large Scale PV | 0.21251 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249 | 0.46357 | 0.46249 | 0.46249 | 0.46249
| Wind | 2.1751 | 2.1562 | 2.1239 | 6.3796 | 10.6456 | 10.689 | 10.677 | 10.6798 | 10.5329 | 10.6387 | 10.6304 | 10.689 | 10.7462 | 10.5224 | 10.6156 | 10.627 | 10.7029 | 10.677 | 10.6798 | 10.5224
| Biomass | 0 | 0 | 0 | 0 | 0 | 0.5256 | 0.876 | 0.876 | 0.8784 | 0.876 | 0.876 | 0.876 | 0.8784 | 0.876 | 0.876 | 0.876 | 0.8784 | 0.876 | 0.876 | 0.876
| Rooftop PV | 1.462 | 1.7053 | 1.9536 | 2.2054 | 2.4613 | 2.7211 | 2.9859 | 3.2552 | 3.5276 | 3.8034 | 4.0831 | 4.3663 | 4.6535 | 4.9445 | 5.2389 | 5.535 | 5.8329 | 6.1365 | 6.4469 | 6.764
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QLD | Black Coal | 55.4784 | 56.7551 | 56.7551 | 56.7551 | 56.9106 | 56.7551 | 56.7551 | 56.7551 | 56.9106 | 56.7551 | 56.7551 | 56.7551 | 57.0962 | 57.0308 | 57.6647 | 58.2996 | 58.8156 | 60.5399 | 62.4588 | 64.4131
| Brown Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 0.64462 | 0.6433 | 0.64431 | 0.64571 | 0.64576 | 0.6433 | 0.6438 | 0.64521 | 0.65262 | 0.6484 | 0.64471 | 0.6483 | 0.67769 | 0.65663 | 0.64986 | 0.7097 | 0.73764 | 0.86083 | 0.93391 | 0.92333
| Liquid Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas | 0.0020814 | 0.00071889 | 0.0077002 | 0 | 0.0072516 | 0.011292 | 0.011696 | 0.1999 | 0.2498 | 0.24613 | 0.28101 | 0.33582 | 0.49864 | 0.59071 | 0.70277 | 0.52868 | 0.8459 | 1.0581 | 1.3929 | 2.4273
| Large Scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 0 | 0 | 0 | 1.2679 | 1.9413 | 1.9456 | 1.9516 | 1.9563 | 1.946 | 1.9415 | 1.9423 | 1.9456 | 1.9618 | 1.941 | 1.9438 | 1.9387 | 1.9464 | 1.9516 | 1.9563 | 1.941
| Biomass | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rooftop PV | 2.3113 | 2.7476 | 3.1908 | 3.6375 | 4.09 | 4.5457 | 4.9783 | 5.3746 | 5.7427 | 6.0896 | 6.4209 | 6.7399 | 7.0495 | 7.3517 | 7.6477 | 7.9374 | 8.2223 | 8.5066 | 8.7916 | 9.0777
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SA | Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brown Coal | 4.5333 | 3.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Fuel | 0 | 0 | 0.00014962 | 0 | 0.000104 | 0 | 0 | 0 | 0 | 0.000142 | 0 | 0 | 0 | 3.7728e-06 | 0 | 5e-05 | 0 | 0 | 0 | 0
| Natural Gas | 0.31538 | 0.60934 | 1.1755 | 0.50435 | 0.2259 | 0.20394 | 0.19133 | 0.1884 | 0.22429 | 0.24661 | 0.22609 | 0.236 | 0.24673 | 0.30702 | 0.42635 | 0.41023 | 0.4316 | 0.45121 | 0.56067 | 0.58035
| Large Scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 4.9996 | 4.9446 | 4.9106 | 6.6072 | 8.1702 | 8.1481 | 8.1441 | 8.1066 | 8.0619 | 8.0991 | 8.1226 | 8.1364 | 8.1642 | 8.0353 | 8.0577 | 8.1288 | 8.1618 | 8.1247 | 8.0727 | 8.0224
| Biomass | 0 | 0 | 0 | 0.3504 | 0.16979 | 0.3504 | 0.3504 | 0.3504 | 0.35136 | 0.3504 | 0.3504 | 0.3504 | 0.35136 | 0.3504 | 0.3504 | 0.3504 | 0.35136 | 0.3504 | 0.3504 | 0.3504
| Rooftop PV | 0.99371 | 1.137 | 1.2888 | 1.4473 | 1.6138 | 1.7867 | 1.9711 | 2.1606 | 2.3375 | 2.495 | 2.6383 | 2.7692 | 2.8909 | 3.0047 | 3.1114 | 3.2087 | 3.2967 | 3.3811 | 3.4634 | 3.5435
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VIC | Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brown Coal | 53.2514 | 52.9762 | 52.9762 | 52.9762 | 53.1199 | 52.7741 | 52.5898 | 52.8134 | 52.9298 | 52.5885 | 53.1907 | 53.1907 | 53.3364 | 53.1907 | 53.1907 | 53.1907 | 53.3364 | 53.1907 | 53.1907 | 53.1907
| Hydro | 3.1906 | 3.1839 | 3.1836 | 3.1841 | 3.1912 | 3.1844 | 3.1843 | 3.1836 | 3.1921 | 3.183 | 3.1838 | 3.1834 | 3.1919 | 3.1843 | 3.1844 | 3.1849 | 3.192 | 3.1846 | 3.183 | 3.1845
| Liquid Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas | 0.00095334 | 0.00087957 | 0.0090467 | 0.01148 | 0.011932 | 0.0043293 | 0.0026151 | 0.005736 | 0.0096121 | 0.023569 | 0.014064 | 0.0036235 | 0.0086686 | 0.016426 | 0.017611 | 0.018217 | 0.031403 | 0.0085101 | 0.01158 | 0.008452
| Large Scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 3.867 | 3.9566 | 4.5858 | 5.5844 | 6.0064 | 6.0127 | 6.0139 | 5.9986 | 5.9681 | 5.958 | 5.9857 | 6.0127 | 6.0495 | 5.9539 | 5.9345 | 5.9886 | 6.025 | 6.0139 | 5.9986 | 5.9539
| Biomass | 0 | 0 | 0 | 0.1752 | 0.12644 | 0.18509 | 0.18509 | 0.18509 | 0.18559 | 0.18509 | 0.18509 | 0.18509 | 0.18559 | 0.18509 | 0.18509 | 0.18509 | 0.18559 | 0.18509 | 0.18509 | 0.18509
| Rooftop PV | 1.2003 | 1.443 | 1.6916 | 1.945 | 2.2044 | 2.4713 | 2.7477 | 3.033 | 3.3215 | 3.6153 | 3.9149 | 4.2195 | 4.5293 | 4.846 | 5.1676 | 5.4882 | 5.8057 | 6.1291 | 6.4586 | 6.7825
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TAS | Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Brown Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hydro | 8.6296 | 8.7002 | 8.7002 | 8.632 | 8.3455 | 8.7002 | 8.7002 | 8.7002 | 8.7036 | 8.5306 | 8.5097 | 8.7002 | 8.7036 | 8.7002 | 8.7002 | 8.7002 | 8.7036 | 8.7002 | 8.7002 | 8.7002
| Liquid Fuel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Natural Gas | 0.82404 | 0.657 | 0.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Large Scale PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind | 1.0805 | 1.0712 | 1.0678 | 2.189 | 2.2162 | 2.2154 | 2.2069 | 2.203 | 2.1978 | 2.195 | 2.2051 | 2.2154 | 2.2173 | 2.1959 | 2.189 | 2.2083 | 2.2167 | 2.2069 | 2.203 | 2.1959
| Biomass | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rooftop PV | 0.13299 | 0.15901 | 0.18641 | 0.21498 | 0.24525 | 0.27755 | 0.31206 | 0.34831 | 0.38509 | 0.42336 | 0.46318 | 0.50358 | 0.54111 | 0.57553 | 0.60744 | 0.63675 | 0.66366 | 0.6889 | 0.7124 | 0.73425
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## NewAndRetiredCapacity Data
Cumulative NEM Total New Entry / Retired Capacity by Technology (MW)
Technology | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
Black Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000 | -2000
Brown Coal | -579 | -579 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125 | -1125
Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Liquid Fuel | 0 | 0 | 0 | -34 | -34 | -34 | -34 | -34 | -34 | -34 | -34 | -97 | -97 | -97 | -97 | -97 | -97 | -97 | -97 | -97
Natural Gas | 0 | 0 | -600 | -726.6816 | -569.6511 | -569.6511 | -569.6511 | -569.6511 | -569.6511 | -569.6511 | -569.6511 | -569.6511 | 41.4586 | 41.4586 | 1011.9831 | 1435.3273 | 1713.1794 | 1802.8235 | 1802.8235 | 2677.4166
Large Scale PV | 0 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
Wind | 0 | 0 | 240 | 2998.4945 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578 | 4984.9578
Biomass | 0 | 0 | 0 | 75 | 75 | 151.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106 | 201.4106
Rooftop PV | 1767.4809 | 2606.8643 | 3463.981 | 4336.3428 | 5229.382 | 6133.6383 | 7040.3738 | 7924.6753 | 8783.8146 | 9627.0591 | 10458.8036 | 11280.5738 | 12095.4021 | 12906.5899 | 13710.8365 | 14497.5952 | 15278.5381 | 16069.9672 | 16864.0132 | 17656.2876
Storage | 7.816 | 135.3462 | 252.4316 | 404.53 | 592.3914 | 796.9828 | 1007.8406 | 1223.0211 | 1440.2111 | 1658.1602 | 1877.2876 | 2095.2703 | 2315.8406 | 2534.1165 | 2752.5181 | 2972.7594 | 3194.8093 | 3420.0709 | 3641.0514 | 3857.5187
Total | 1196.2969 | 2265.2105 | 2333.4126 | 6030.6858 | 9255.08 | 10440.3384 | 11607.9317 | 10707.4136 | 11783.7429 | 12844.9365 | 13895.8084 | 14872.5613 | 16519.0696 | 17548.5333 | 19541.7061 | 20972.0502 | 22252.8951 | 23359.2299 | 24374.2564 | 26257.5912

## GenerationInvestment
Generation Investment across the NEM ($ million)
Region | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
NSW | 0 | 0 | 0 | 3403.7191 | 3455.4844 | 392.6468 | 261.607 | 0 | 0 | 0 | 0 | 0 | 329.8979 | 0 | 304.1779 | 160.0887 | 184.6981 | 23.5555 | 0 | 409.008
QLD | 0 | 0 | 0 | 1074.1336 | 569.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.4173 | 0 | 503.7512
VIC | 0 | 0 | 0 | 946.6513 | 276.4389 | 7.3847 | 0 | 0 | 0 | 0 | 0 | 0 | 132.8463 | 0 | 230.2606 | 0 | 0 | 0 | 0 | 0
SA | 0 | 0 | 0 | 1655.9763 | 1333.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9336 | 0 | 239.113 | 177.8804 | 37.6502 | 0 | 0 | 0
TAS | 0 | 0 | 0 | 871.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## GenerationConnectionCosts
New Entry Generation Connection Costs across the NEM ($ million)
Region | 2015-16 | 2016-17 | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
NSW | 0 | 0 | 0 | 119.5249 | 119.5249 | 1.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 31.4278 | 0 | 28.894 | 15.1825 | 17.4745 | 2.2213 | 0 | 38.2405
QLD | 0 | 0 | 0 | 30.4418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0352 | 0 | 35.6956
VIC | 0 | 0 | 0 | 34.7407 | 12.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9988 | 0 | 19.0092 | 0 | 0 | 0 | 0 | 0
SA | 0 | 0 | 0 | 77.8651 | 68.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9912 | 0 | 20.701 | 15.375 | 3.2465 | 0 | 0 | 0
TAS | 0 | 0 | 0 | 40.4929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## EconomicDispatchLimitations
Potential Economic Dispatch Limitations across the NEM under the Gradual Evolution Scenario
Reference | Region | Zone | Potential transmission limitations | Dispatch scenario
| QLD | None
E-N1 | NSW | NNS | Transmission limitations on the 132kV network betweend Lismore and Dunoon/Mullumbimby | High wind generation in NNS zone when power flows from NSW to QLD
E-N2 |  | NNS | Transmission limitations between Tamworth and Muswellbrook/Liddell | High levels of wind generation in NNS zone when power flows from NNS zone to NCEN zone
E-N3 |  | CAN | Transmission limitations on the network between CAN and NCEN | High levels of wind generation in the CAN zone when power flows from the SWNSW zone to CAN zone.
E-V1 | VIC | MEL | Transmission limitation on South Morang 500/330kV transformer | High export from Vic to NSW
E-V2 |  | MEL | Transmission limitations on Dederang-South Morang 330 kV circuits | High transfer between VIC to NSW (export or import)
E-V3 |  | MEL | Transmission limitations on Eildon-Thomastown 220 kV line | High transfer between VIC to NSW (export or import)
E-V4 |  | CVIC | Transmission limitations on Ballarat-Horsham 220kV line | High wind generation connected between Ballarat and Horsham and/or between Horsham and Redcliffs
E-S1 | SA | NSA | Transmission limitations on NSA-ADE 275kV corridor | High levels of wind/solar generation in the NSA zone
E-S2 |  | NSA | Transmission limitations on the 132kV network in the Mid North region | High levels of wind/solar generation in the NSA zone
E-S3 |  | NSA | Transmission limitations on the 132kV network in the Riverland region | High levels of wind/solar generation in the NSA zone
E-S4 |  | NSA | Transmission limitations on the 132kV network in the Eyre Peninsula | High levels of wind/solar generation in the NSA zone
E-T1 | TAS | TAS | Transmission limitations on the Burnie-Sheffield transmission corridor | High levels of wind generation in North-west Tasmania
E-T2 |  | TAS | Transmission limitations on the Farrell-Sheffield transmission corridor | High levels of wind generation in West Tasmania

## NetworkLimitationCosts
Transmission Limitations across the NEM under the Gradual Evolution Scenario
Reference | Region | Zone | 2015 Timing (G) | Observed limitation | Network needs | Comment | Cost Estimate ($ million)
L-N1 | New South Wales | NCEN | 2020–21 to 2024–25 to 2029-30 | Overload of the Sydney South–Beaconsfield West 330 kV cable for an outage of the Sydney South–Haymarket 330 kV cable. | A new supply to the Beaconsfield West Substation from another 330 kV supply point. | The shortfall in supply capacity is expected to occur in the early to mid-2020s and is primarily dependent on the timing of AusGrid 132 kV cable retirements in Sydney. | 647

## CommittedNetworkCosts
Committed main transmission network projects across the NEM
Region | Zone | Project | Anticipated Timing | Estimated Cost ($ million)
Victoria | CVIC | Additional Moorabool- Ballarat 220 kV transmission line | Early 2017 | 27.8
South Australia | NSA | ElectraNet NCIPAP project - Riverland uprating (2016/17) - increasing conductor clearances to facilitate improved thermal capability. | 2016/17 | 4.43
Victoria and South Australia | MEL - SESA | VIC-SA Interconnect (Heywood) incremental augmentation:- (Scope of work in Victoria) • A third 370 MVA 500/275 kV transformer and bus tie at Heywood • 275 kV series compensation • 132 kV network works | 2016 | 107.7
|  |  | Total | 139.93