## Introduction
In December 2018, AER made a final determination on a new Transmission Annual Planning Report (TAPR) Guideline, requiring TNSPs to publish specified information on emerging transmission line and terminal station limitations.
The "Summary of Transmission connection point (TCP) data" spreadsheet provides information on a selected set of transmission terminal stations associated with Declared Shared Network(DSN) transformer emerging limitations and connection asset limitations.
The DSN transformer emerging limitations were selected based on AEMO’s VAPR and RIT-T reports, and the connection asset limitations were selected based on the 2022 Transmission Connection Planning report (TCPR), produced jointly by the Victorian Electricity Distribution Businesses.
As AEMO's RIT-T projects are still works in progress, the information provided is subject to change.
The general criteria for selecting the existing assets to be included in the data reporting are:
• For DSN assets, they are associated with both load and generation driven emerging or priority limitations for which AEMO has yet to finalise the preferred option to address.
• For connection assets , their augmentations are required in the near future according to the 2022 TCPR.
For connection assets, the information is purely based on that available in the 2022 TCPR. AEMO has noted that some Victorian DNSPs may use their own connection point demand forecast, which is different from AEMO’s connection point demand forecast
In addition to the information on emerging limitations specified in the TAPR guideline, The "Summary of TCP data sheet" also includes information related to terminal stations with monitored limitations, and other terminal stations in Vic.
The information on monitored limitations includes:
• Constrained connection point ID
• Constraint primary driver
• Constraint investment type
• Constrained connection point location
• Voltage level
• Preferred investment— Description
• Preferred investment — Capital cost (if available)
• Preferred investment— Cost accuracy (if available)
• Maximum fault level
The information on other terminal stations not associated with any limitation includes terminal station location, voltage level and maximum fault level at the high voltage side.

## Summary of TCP data 2021 (hidden)
Region | Limitation Type | Constrained connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point location | Annual energy and peak demand of residential customers affected | Annual energy and peak demand of industrial customers affected | Annual energy and peak demand of commercial customers affected | Forecast 10% and 50% Probability of Exceedance (POE) peak demand on maximum demand day | Maximum demand on minimum demand day | Forecast daily demand profile on maximum demand day | Forecast daily demand profile on minimum demand day | Voltage level | Forecast maximum load at risk per year | Connection point load duration curve data | Preferred investment— Description | Preferred investment — Capital cost | Preferred investment — Annual network operating cost | Preferred investment— Cost accuracy | Preferred investment— Proposed timing | Demand reduction required to defer investment by 1 year | Annual deferral value | Load transfer capacity | Historic load trace | Historic connection point rating | Limitation asset | Unplanned outages | Maximum fault level | Annual economic cost of constraint | VCR | Annual expected unserved energy
Greater Melourne & Geelong | Emerging | Altona West terminal station | Customer load at risk (market benefit) | Augmentation | 37.839oS, 144.789oE | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona West MD forecast spreadsheet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits | $18M | Unavailable from TCPR | Unavailable from TCPR | 2026 | 9 MW | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 158 MW (summer) | Unavailable from TCPR | Unavailable from TCPR | 19kA (66kV) | $1.79M in 2029 | $34,740/MWh | 51.6 MWh in 2029 | 51.5256
| Emerging | Cranbourne terminal station | Customer load at risk (market benefit) | Augmentation | 38.085oS, 145.265oE | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Cranbourne MD forecast spreadseet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 4th 150MVA transformer | $26M | Unavailable from TCPR | Unavailable from TCPR | 2023 | 7MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 359MVA | Unavailable from TCPR | Unavailable from TCPR | 22kA (66kV) | $2.46M in 2026 | $34,778/MWh | 70.8MWh in 2026 | 51.581
| Emerging | Deer Park terminal station | Customer load at risk (market benefit) | Augmentation | 37.778⁰ S 144.735⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Deer Park MD forecast spreadseet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 3rd 225MVA transformer, initially "spare", not terminated. | $4M | Unavailable from TCPR | [9 empty] | 11kA (66kV) | $0.45M in 2026 | $38,272/MWh | 11.8MWh in 2026
| Monitored | South Morang terminal station | Increased demand in Metropolitan Melbourne and/or increased import from NSW. | Augmentation | 37.644⁰ S 145.078⁰ E | [7 empty] | 330/220kV |  |  | Replace the existing transformer with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $44M |  | not available | 2024 | Not applicable | [6 empty] | 25kA (330kV)
| Developing | Cranbourne terminal station | Increased demand around the Eastern Melbourne Metropolitan area. | Augmentation | 38.085oS, 145.265oE | [7 empty] | 500/220kV |  |  | Install additional transformation capacity | $72.5M |  | 50% | [8 empty] | 17kA (500kV)
| Developing | Rowville terminal station | Increased demand in Eastern Metropolitan Melbourne. | Augmentation | 37.928⁰ S 145.226⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity at Cranbourne terminal station. | $72.5M |  | 50% | [8 empty] | 21kA (500kV)
Murray River REZ | Emerging | Wemen terminal station | Posible increased generation embedded inte distribution network. | Augmentation | 34.791⁰ S 142.522⁰ E | [7 empty] | 220kV |  |  | Install additional transformation capacity at Wemen terminal station. | Unavailable from TCPR | [10 empty] | 5kA
South - West Victoria REZ | Developing | Moorabool terminal station | Large-scale new generation in western Victoria area | Augmentation | 38.037⁰ S 144.296⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity | $102M |  | 50% | [8 empty] | 17kA (500kV)
Ovens Murray REZ | Developing | Dederang terminal station | High imports from NSW and Murray generation (with the DBUSS transformer control scheme being active). | Augmentation | 36.454⁰ S 146.992⁰ E | [7 empty] | 330/220kV |  |  | Install additional transformation capacity | Unavailable |  | 50% | [8 empty] | 18kA (330kV)
Eastern Corridor |  | Hazelwood terminal station |  |  | 38.281⁰ S 146.428⁰ E | [7 empty] | 500kV | [14 empty] | 27kA
|  | Hazelwood power station |  |  | 38.273⁰ S 146.392⁰ E | [7 empty] | 220kV | [14 empty] | 41kA
|  | Jeeralang terminal station |  |  | 38.275⁰ S 146.425⁰ E | [7 empty] | 220kV | [14 empty] | 33kA
|  | Loy Yang power staton |  |  | 38.254⁰ S 146.576⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Morwell terminal station |  |  | 38.259⁰ S 146.421⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
|  | Yallourn terminal station |  |  | 38.177⁰ S 146.344⁰ E | [7 empty] | 220kV | [14 empty] | 26kA
Ovens Murray REZ |  | Wodonga terminal station |  |  | 36.155⁰ S 146.95⁰ E | [7 empty] | 330kV | [14 empty] | 10kA
|  | Mt Beauty terminal station |  |  | 36.743⁰ S 147.165⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Eildon terminal station |  |  | 37.224⁰ S 145.921⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Dartmouth terminal station |  |  | 36.556⁰ S 147.521⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Mckay Creek terminal station |  |  | 36.858⁰ S 147.235⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | West Kiewa terminal station |  |  | 36.759⁰ S 147.186⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Bogong terminal station |  |  | 36.805⁰ S 147.229⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Greater Melbourne & Geelong |  | East Rowville terminal station |  |  | 37.941⁰ S 145.236⁰ E | [7 empty] | 220kV | [14 empty] | 32kA
|  | Tyabb terminal station |  |  | 38.268⁰ S 145.201⁰ E | [7 empty] | 220kV | [14 empty] | 16kA
|  | Western Port terminal station |  |  | 38.283⁰ S 145.208⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Malvern terminal station |  |  | 37.878⁰ S 145.084⁰ E | [7 empty] | 220kV | [14 empty] | 17kA
|  | Springvale terminal station |  |  | 37.928⁰ S 145.146⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Heatherton terminal station |  |  | 37.941⁰ S 145.078⁰ E | [7 empty] | 220kV | [14 empty] | 18kA
|  | Ringwood terminal station |  |  | 37.821⁰ S 145.216⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Templestowe terminal station |  |  | 37.749⁰ S 145.171⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Thomastown terminal station |  |  | 37.693⁰ S 145.01⁰ E | [7 empty] | 220kV | [14 empty] | 29kA
|  | Richmond terminal station |  |  | 37.831⁰ S 145.002⁰ E | [7 empty] | 220kV | [14 empty] | 26kA
|  | Brunswick terminal station |  |  | 37.773⁰ S 144.985⁰ E | [7 empty] | 220kV | [14 empty] | 28kA
|  | Keilor terminal station |  |  | 37.738⁰ S 144.846⁰ E | [7 empty] | 500kV | [14 empty] | 30kA
|  | West Melbourne terminal station |  |  | 37.8⁰ S 144.935⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Fishermans Bend terminal station |  |  | 37.825⁰ S 144.929⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Brooklyn terminal station |  |  | 37.826⁰ S 144.86⁰ E | [7 empty] | 220kV | [14 empty] | 24kA
|  | Newport terminal station |  |  | 37.841⁰ S 144.894⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Laverton North terminal station |  |  | 37.842⁰ S 144.789⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Geelong terminal station |  |  | 38.083⁰ S 144.339⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
Central North REZ |  | Fosterville terminal station |  |  | 36.738⁰ S 144.511⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Glenrowan terminal station |  |  | 36.494⁰ S 146.075⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Shepparton terminal station |  |  | 36.353⁰ S 145.365⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
Murray River REZ |  | Bendigo terminal station |  |  | 36.796⁰ S 144.252⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Kerang terminal station |  |  | 35.782⁰ S 143.945⁰ E | [7 empty] | 220kV | [14 empty] | 4kA
|  | Kiamal terminal station |  |  | 35.027⁰ S 142.299⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Red Cliffs terminal station |  |  | 34.275⁰ S 142.2⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
South West Victoria REZ |  | Heywood terminal station |  |  | 38.182⁰ S 141.638⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Berrybank substation |  |  | 37.900⁰ S 143.438⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Blue Gum substation |  |  | 38.067⁰ S 142.674⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Haunted Gully terminal station |  |  | 38.006⁰ S 143.317⁰ E | [7 empty] | 500kV | [14 empty] | 13kA
|  | Mortlake terminal station |  |  | 38.062⁰ S 142.67⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Portland substation |  |  | 38.387⁰ S 141.631⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Tarrone terminal station |  |  | 38.179⁰ S 142.181⁰ E | [7 empty] | 500kV | [14 empty] | 8kA
|  | Terang terminal station |  |  | 38.256⁰ S 142.925⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
Western Victoria REZ |  | Ararat terminal station |  |  | 37.164⁰ S 143.245⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Ballarat terminal station |  |  | 37.567⁰ S 143.921⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Bulgana terminal station |  |  | 37.037⁰ S 142.984⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | Crowlands terminal station |  |  | 37.121⁰ S 143.154⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Elaine terminal station |  |  | 37.731⁰ S 144.012⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Horsham terminal station |  |  | 36.731⁰ S 142.246⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Murra Warra terminal station |  |  | 36.455⁰ S 142.321⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Waubra terminal station |  |  | 37.356⁰ S 143.606⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
Maximum fault levels are the maximum of three phase and single phase to ground fault levels, at the low voltage side of constrained transformers, for the next 5 years, taken from AEMO's Annual Fault Level Review report.
South Morang project annual deferral value is present value of a one year deferment of project cost, using 6% pa discount rate.
Altona West, Cranbourne, and Deer Park Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
[13 empty] | 50pcl | 10pcl | $M
[9 empty] | $M pa | $M capex |  | VCR | MWh | MWh |  | MWh
[8 empty] | ATS W | 1.33 | 18 | 0.073889 | 34740 | 43.07 | 71.44 | 1.7919 | 51.581 | 1.7919
[8 empty] | CBTS | 1.9 | 26 | 0.073077 | 34778 | 21 | 187 | 2.4623 | 70.8 | 2.4623
[8 empty] | DPTS | 0.3 | 4.0826 | 0.073483 | 38272 | 5.32 | 26.78 | 0.45 | 11.758 | 0.45

## Summary of TCP data
Region | Limitation Type | Constrained connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point location | Annual energy and peak demand of residential customers affected | Annual energy and peak demand of industrial customers affected | Annual energy and peak demand of commercial customers affected | Forecast 10% and 50% Probability of Exceedance (POE) peak demand on maximum demand day | Maximum demand on minimum demand day | Forecast daily demand profile on maximum demand day | Forecast daily demand profile on minimum demand day | Voltage level | Forecast maximum load at risk per year | Connection point load duration curve data | Preferred investment— Description | Preferred investment — Capital cost | Preferred investment — Annual network operating cost | Preferred investment— Cost accuracy | Preferred investment— Proposed timing | Demand reduction required to defer investment by 1 year | Annual deferral value | Load transfer capacity | Historic load trace | Historic connection point rating | Limitation asset | Unplanned outages | Maximum fault level | Annual economic cost of constraint | VCR | Annual expected unserved energy
Greater Melourne & Geelong | Emerging | Altona West terminal station | Customer load at risk (market benefit) | Augmentation | 37.839⁰S, 144.789⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona West MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits | $25M | $1.75M | Unavailable from TCPR | 2025 | 17 MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 170 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 19kA (66kV) | $1.80M in 2025 | $36,000/MWh | 50.2 MWh in 2026
| Emerging | Cranbourne terminal station | Customer load at risk (market benefit) | Augmentation | 38.085⁰S, 145.265⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Cranbourne MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 4th 150MVA transformer | $26M (from 2021 TCPR) | Unavailable from TCPR | Unavailable from TCPR | 2025 | 9 MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 369MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 22kA (66kV) | $0.63M in 2025 | $35,537/MWh | 18.0 MWh in 2025
| Emerging | Deer Park terminal station | Customer load at risk (market benefit) | Augmentation | 37.778⁰ S 144.735⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Deer Park MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 3rd 225MVA transformer, initially "spare", not terminated. | Unavailable from TCPR 2022 | $300k | Unavailable from TCPR | 2025 | 24 MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 280 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 11kA (66kV) | $0.19M in 2025 | $38,000/MWh | 4.8 MWh in 2025
| Emerging | South Morang terminal station | Customer load at risk (market benefit) | Augmentation | 37.644⁰ S 145.078⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "South Morang MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 3rd 225 MVA 220/66kV transformer | $30M | $2.1M | Unavailable from TCPR | 2028 | 4 MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 265 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 22kA (66kV) | $2.57M in 2028 | $37,355/MWh | 68.8 MWh in 2028
| Monitored | Keilor terminal station | Customer load at risk (market benefit) | Replacement | 37.738⁰ S 144.846⁰ E | [7 empty] | 500/220kV |  |  | Replace the existing transformer with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $71M (AusNet Asset Renewal Plan 2023) |  | not available | 2028 (AusNet Asset Renewal Plan 2023) | Not applicable | [6 empty] | 31kA (220kV) |  | Unavailable from TCPR
| Monitored | South Morang terminal station | Customer load at risk (market benefit) | Replacement | 37.644⁰ S 145.078⁰ E | [7 empty] | 330/220kV |  |  | Replace the existing transformer with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $44M (AusNet Asset Renewal Plan 2023) |  | not available | 2029 (AusNet Asset Renewal Plan 2023) | Not applicable | [6 empty] | 26kA (330kV) |  | Unavailable from TCPR
| Emerging | Rowville terminal station | Increased demand in Eastern Metropolitan Melbourne and/or reduced 220kV infeed from Latrobe Valley | Augmentation | 37.928⁰ S 145.226⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity at Cranbourne, Rowville, Templestowe or Ringwood terminal station. | [11 empty] | 21kA (500kV) |  | Unavailable from TCPR
Central North REZ | Monitored | Glenrowan terminal station | Possible increased generation embedded in the distribution network. | Augmentation | 36.494⁰ S 146.075⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Glenrowan MD forecast" tab |  |  |  | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity at Glenrowan terminal station. | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 275 MVA N rating for embedded generation export | Unavailable from TCPR | Unavailable from TCPR | 15kA | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR
Murray River REZ | Emerging | Wemen terminal station | Possible increased generation embedded in the distribution network. | Augmentation | 34.791⁰ S 142.522⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity at Wemen terminal station. | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 140MVA N rating for embedded generation export | Unavailable from TCPR | Unavailable from TCPR | 7kA | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR
Eastern Corridor |  | Hazelwood terminal station |  |  | 38.281⁰ S 146.428⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Hazelwood power station |  |  | 38.273⁰ S 146.392⁰ E | [7 empty] | 220kV | [14 empty] | 41kA
|  | Jeeralang terminal station |  |  | 38.275⁰ S 146.425⁰ E | [7 empty] | 220kV | [14 empty] | 34kA
|  | Loy Yang power staton |  |  | 38.254⁰ S 146.576⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Morwell terminal station |  |  | 38.259⁰ S 146.421⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
|  | Yallourn terminal station |  |  | 38.177⁰ S 146.344⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
Ovens Murray REZ |  | Dederang terminal station |  |  | 36.454⁰ S 146.992⁰ E | [7 empty] | 330/220kV | [14 empty] | 19kA (330kV)
|  | Wodonga terminal station |  |  | 36.155⁰ S 146.95⁰ E | [7 empty] | 330kV | [14 empty] | 11kA
|  | Mt Beauty terminal station |  |  | 36.743⁰ S 147.165⁰ E | [7 empty] | 66kV | [14 empty] | 5kA
|  | Eildon terminal station |  |  | 37.224⁰ S 145.921⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Dartmouth terminal station |  |  | 36.556⁰ S 147.521⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Mckay Creek terminal station |  |  | 36.858⁰ S 147.235⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | West Kiewa terminal station |  |  | 36.759⁰ S 147.186⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Bogong terminal station |  |  | 36.805⁰ S 147.229⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Greater Melbourne & Geelong |  | Cranbourne terminal station |  |  | 38.085oS, 145.265oE | [7 empty] | 500/220kV | [14 empty] | 17kA (500kV)
|  | East Rowville terminal station |  |  | 37.941⁰ S 145.236⁰ E | [7 empty] | 66kV | [14 empty] | 16kA
|  | Tyabb terminal station |  |  | 38.268⁰ S 145.201⁰ E | [7 empty] | 66kV | [14 empty] | 21kA
|  | Western Port terminal station |  |  | 38.283⁰ S 145.208⁰ E | [7 empty] | 220kV | [14 empty] | 16kA
|  | Malvern terminal station |  |  | 37.878⁰ S 145.084⁰ E | [7 empty] | 66kV | [14 empty] | 19kA
|  | Springvale terminal station |  |  | 37.928⁰ S 145.146⁰ E | [7 empty] | 66kV | [14 empty] | 16kA
|  | Heatherton terminal station |  |  | 37.941⁰ S 145.078⁰ E | [7 empty] | 66kV | [14 empty] | 19kA
|  | Ringwood terminal station |  |  | 37.821⁰ S 145.216⁰ E | [7 empty] | 66kV | [14 empty] | 22kA
|  | Templestowe terminal station |  |  | 37.749⁰ S 145.171⁰ E | [7 empty] | 66kV | [14 empty] | 22kA
|  | Thomastown terminal station |  |  | 37.693⁰ S 145.01⁰ E | [7 empty] | 66kV | [14 empty] | 23kA
|  | Richmond terminal station |  |  | 37.831⁰ S 145.002⁰ E | [7 empty] | 66kV | [14 empty] | 22kA
|  | Brunswick terminal station |  |  | 37.773⁰ S 144.985⁰ E | [7 empty] | 66kV | [14 empty] | 16kA (66kV)
|  | West Melbourne terminal station |  |  | 37.8⁰ S 144.935⁰ E | [7 empty] | 66kV | [14 empty] | 16kA
|  | Fishermans Bend terminal station |  |  | 37.825⁰ S 144.929⁰ E | [7 empty] | 66kV | [14 empty] | 22kA
|  | Brooklyn terminal station |  |  | 37.826⁰ S 144.86⁰ E | [7 empty] | 66kV | [14 empty] | 20kA
|  | Newport terminal station |  |  | 37.841⁰ S 144.894⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Laverton North terminal station |  |  | 37.842⁰ S 144.789⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Geelong terminal station |  |  | 38.083⁰ S 144.339⁰ E | [7 empty] | 66kV | [14 empty] | 22kA
Central North REZ |  | Fosterville terminal station |  |  | 36.738⁰ S 144.511⁰ E | [7 empty] | 220kV | [14 empty] | 9kA (220kV)
|  | Glenrowan terminal station |  |  | 36.494⁰ S 146.075⁰ E | [7 empty] | 66kV | [14 empty] | 15kA
|  | Shepparton terminal station |  |  | 36.353⁰ S 145.365⁰ E | [7 empty] | 66kV | [14 empty] | 18kA
Murray River REZ |  | Bendigo terminal station |  |  | 36.796⁰ S 144.252⁰ E | [7 empty] | 66kV | [14 empty] | 12kA
|  | Kerang terminal station |  |  | 35.782⁰ S 143.945⁰ E | [7 empty] | 66kV | [14 empty] | 7kA
|  | Kiamal terminal station |  |  | 35.027⁰ S 142.299⁰ E | [7 empty] | 220kV | [14 empty] | 8kA (220V)
|  | Red Cliffs terminal station |  |  | 34.275⁰ S 142.2⁰ E | [7 empty] | 66kV | [14 empty] | 21kA
South West Victoria REZ |  | Heywood terminal station |  |  | 38.182⁰ S 141.638⁰ E | [7 empty] | 500kV | [14 empty] | 10kA (500kV)
|  | Berrybank substation |  |  | 37.900⁰ S 143.438⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Blue Gum substation |  |  | 38.067⁰ S 142.674⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Moorabool terminal station |  |  | 38.037⁰ S 144.296⁰ E | [7 empty] | 500/220kV | [14 empty] | 17kA (500kV)
|  | Haunted Gully terminal station |  |  | 38.006⁰ S 143.317⁰ E | [7 empty] | 500kV | [14 empty] | 13kA
|  | Mortlake terminal station |  |  | 38.062⁰ S 142.67⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Portland substation |  |  | 38.387⁰ S 141.631⁰ E | [7 empty] | 500kV | [14 empty] | 9kA
|  | Tarrone terminal station |  |  | 38.179⁰ S 142.181⁰ E | [7 empty] | 500kV | [14 empty] | 9kA
|  | Terang terminal station |  |  | 38.256⁰ S 142.925⁰ E | [7 empty] | 500kV | [14 empty] | 14kA
Western Victoria REZ |  | Ararat terminal station |  |  | 37.164⁰ S 143.245⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Ballarat terminal station |  |  | 37.567⁰ S 143.921⁰ E | [7 empty] | 66kV | [14 empty] | 17kA
|  | Bulgana terminal station |  |  | 37.037⁰ S 142.984⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | Crowlands terminal station |  |  | 37.121⁰ S 143.154⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Elaine terminal station |  |  | 37.731⁰ S 144.012⁰ E | [7 empty] | 220kV | [14 empty] | 20kA
|  | Horsham terminal station |  |  | 36.731⁰ S 142.246⁰ E | [7 empty] | 66kV | [14 empty] | 10kA
|  | Murra Warra terminal station |  |  | 36.455⁰ S 142.321⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Waubra terminal station |  |  | 37.356⁰ S 143.606⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
Maximum fault levels are the maximum of three phase and single phase to ground fault levels, at the low voltage side of constrained transformers, for the next 5 years, taken from AEMO's Annual Fault Level Review report.
Altona West, Cranbourne, Deer Park, and Terang Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
[13 empty] | 50pcl | 10pcl | $M
[9 empty] | $M pa | $M capex |  | VCR | MWh | MWh |  | MWh
[8 empty] | ATS W | 1.33 | 18 | 0.073889 | 34740 | 43.07 | 71.44 | 1.7919 | 51.581 | 1.7919
[8 empty] | CBTS | 1.9 | 26 | 0.073077 | 34778 | 21 | 187 | 2.4623 | 70.8 | 2.4623
[8 empty] | DPTS | 0.3 | 4.0826 | 0.073483 | 38272 | 5.32 | 26.78 | 0.45 | 11.758 | 0.45

## Altona West MD forecast
Station: ATS West
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
50th percentile Summer Maximum Demand (MVA) | 281.2 | 305.9 | 323.2 | 334 | 345 | 354.9 | 372.6 | 394.8 | 416.2 | 438.9
50th percentile Winter Maximum Demand (MVA) | 206 | 225.7 | 235.9 | 244.4 | 254.1 | 267 | 283.5 | 301.7 | 319.2 | 335.9
10th percentile Summer Maximum Demand (MVA) | 303.2 | 327.9 | 345.6 | 356.5 | 366.7 | 377.7 | 396.8 | 419.1 | 441.6 | 465.4
10th percentile Winter Maximum Demand (MVA) | 213.5 | 233.6 | 244.2 | 252.6 | 262.3 | 274.9 | 291.6 | 310.2 | 327.9 | 344.6

## Cranbourne MD forecast
Station: CBTS 66 kV
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
50th percentile Summer Maximum Demand (MVA) | 448.4 | 458.9 | 466.1 | 474.9 | 487.1 | 498.7 | 511.2 | 523.8 | 537.7 | 552
50th percentile Winter Maximum Demand (MVA) | 384.5 | 395 | 405.7 | 417.3 | 429.7 | 442.4 | 456 | 470.3 | 484.4 | 498.4
10th percentile Summer Maximum Demand (MVA) | 500.5 | 513.1 | 523.2 | 536.8 | 548.4 | 562.3 | 577.2 | 592.2 | 608.5 | 625.1
10th percentile Winter Maximum Demand (MVA) | 405.5 | 416.6 | 427.8 | 440 | 453.1 | 466.4 | 480.4 | 495.4 | 510.1 | 524.7

## Deer Park MD forecast
Station: DPTS 66 kV
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
50th percentile Summer Maximum Demand (MVA) | 253.6 | 284.4 | 308.5 | 309.5 | 309.7 | 311.4 | 320.8 | 337.5 | 352.7 | 369.5
50th percentile Winter Maximum Demand (MVA) | 230.3 | 271.3 | 277.9 | 277.4 | 277.6 | 282.1 | 293.1 | 307.1 | 320.2 | 333.7
10th percentile Summer Maximum Demand (MVA) | 282 | 311.4 | 336.1 | 337.4 | 337.4 | 339.3 | 349.5 | 367.7 | 384.6 | 402.5
10th percentile Winter Maximum Demand (MVA) | 242.9 | 284.6 | 291.5 | 291.2 | 291.7 | 296.4 | 307.9 | 322.6 | 336.6 | 350.8

## Glenrowan MD forecast
Station: GNTS 66 kV
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
50th percentile Summer Maximum Demand (MVA) | 101.8 | 102.8 | 103.8 | 104.8 | 105.8 | 106.7 | 107.7 | 108.8 | 109.9 | 111
50th percentile Winter Maximum Demand (MVA) | 105.9 | 107 | 108.2 | 109.4 | 110.6 | 111.8 | 113 | 114.2 | 115.4 | 116.6
10th percentile Summer Maximum Demand (MVA) | 109.8 | 110.9 | 112 | 113.1 | 114.2 | 115.4 | 116.6 | 117.8 | 119.1 | 120.3
10th percentile Winter Maximum Demand (MVA) | 109.3 | 110.5 | 111.6 | 112.7 | 113.8 | 115 | 116.1 | 117.3 | 118.4 | 119.5

## South Morang MD forecast
Station: SMTS 66 kV
Year | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
50th percentile Summer Maximum Demand (MVA) | 329.7 | 340.1 | 351.6 | 361.6 | 370.5 | 381.4 | 394.4 | 408.3 | 424.2 | 440.3
50th percentile Winter Maximum Demand (MVA) | 308.5 | 319 | 329.2 | 338.1 | 347.1 | 358.1 | 370.2 | 384 | 398.9 | 415
10th percentile Summer Maximum Demand (MVA) | 370.7 | 382.7 | 395.4 | 406.8 | 417.2 | 429.8 | 444.5 | 460.1 | 477.7 | 495.5
10th percentile Winter Maximum Demand (MVA) | 328.7 | 339.8 | 350.8 | 360.4 | 370.1 | 381.1 | 393.2 | 407.7 | 423.1 | 439.6