## Index
The National Electricity Market Constraint Report 2013
Electronic Material – supplementary data
This supplement provides:
* Binding constraint equations (energy and FCAS separately)
* Market Impact of constraint equations
* Binding Interconnector limit setters and the hours those constraint equations set the limits
* Outages using constraint equations
* Data on the number of outages and time from the submit time

## Binding 2013
Constraint Equation ID | 2013 Hours (2012 Hours) | Description | Type | Region
N_X_MBTE_3A & N_X_MBTE_3B | 3,773 (503) | Out = all three Directlink cables | Outage | NSW
#MUSSELR1_E | 1,107 (0) | Quick constraint equation to limit Musselroe to various levels This constraint equation was invoked in 2013 for the Musselroe wind farm commissioning. | Outage | Quick
V>S_NIL_HYTX_HYTX | 992 (48) | Out = Nil, avoid overloading the remaining Heywood 275/500 kV transformer on trip of one Heywood 275/500 kV transformer With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
V>>S_NIL_SETB_SGKH | 652 (0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line This will bind for high import into SA with high levels of generation from the wind farms and gas turbines in the south east. With a revised rating provided in December 2013 AEMO expects this constraint equation to bind less in 2014. | NIL | SA
T_MRWF_100 | 597 (0) | Discretionary 100 MW upper limit on Musselroe Wind Farm This constraint equation was invoked in 2013 for the Musselroe wind farm commissioning. | Outage | Tas
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 531 (103) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
Q>NIL_BI_FB | 493 (484) | Out = Nil, avoid overloading on Boyne Island feeder bushing on Calliope River to Boyne Island 132 kV lines, for the contingent loss of a single Calliope River to Boyne Island 132 kV line | NIL | Qld
S>>V_NIL_SETX_SETX | 456 (444) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer This constraint equation binds when there is export from South Australia to Victoria and high generation from the wind farms and gas turbines in the south east of South Australia. | NIL | SA
VSML_ZERO | 424 (33) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
T_TAMARCCGT_GCS | 358 (911) | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) The Tamar Valley output is dependent on the GCS so AEMO expects that this constraint equation will bind for a high number of hours in 2014. | NIL | Tas
T>T_NIL_BL_IMP_5F | 327 (27) | Out = Nil, avoid overloading Hadspen to Georgetown No.1 220 kV line (flow to North) for trip of the Hadspen to Georgetown No.2 220 kV line with no SPS action This constraint only binds when the NCSPS control scheme is unavailable. | NIL | Tas
V>S_460 | 301 (15) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
T>T_NIL_BL_IMP_1B | 300 (5) | Out = Nil, avoid overloading either Gordon to Chapel St 220 kV line for trip of the other Gordon to Chapel St 220 kV line with no SPS action This constraint equation binds at times of high Gordon generation when the NCSPS control scheme is unavailable. | NIL | Tas
NSA_Q_GSTONE34_xxx | 284 (367) | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
Q>>NIL_855_871 | 278 (279) | Out = Nil, avoid overload on Calvale to Wurdong (871) 275 kV line on trip of Calvale to Stanwell (855) 275 kV line This constraint equation has been removed following the construction of the new double circuit 275 kV lines between Calvale and Stanwell (8873 and 8874) in late 2013. | NIL | Qld
T_MRWF_QLIM_xx | 217 (0) | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
V^^S_NIL_MAXG_xxx | 209 (240) | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off There are two constraint equations that make up the voltage stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 202 (164) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. AEMO expects the combination of these three constraint equations will bind for a similar amount in 2014. | NIL | Vic
N_X_MBTE2_A & N_X_MBTE2_B | 196 (483) | Out = two Directlink cables | Outage | NSW
T>T_NIL_110_1 | 189 (0) | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
SVML_ZERO | 175 (283) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
N>N-NIL_LSDU | 160 (62) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
S_LB3_0 | 156 (83) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
T>T_NIL_BL_3C | 136 (1) | Out = Nil, avoid overloading a Hadspen to Palmerston 220 kV line for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action | NIL | Tas
T^V_NIL_BL_6 | 133 (0) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
Q>NIL_TR_TX1_4 | 121 (26) | Out = Nil, avoid overloading a Tarong 275/132 kV transformer ( No.1 or No.4) on trip of the other Tarong 275/132 kV transformer (No.1 or No.4) | NIL | Qld
T_MRWF_120 | 108 (0) | Discretionary 120 MW upper limit on Musselroe Wind Farm This constraint equation was invoked in 2013 for the commissioning of the Musselroe wind farm. | Outage | Tas
T>T_NIL_BL_IMP_5FF | 107 (8) | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
N^^V_NIL_1 | 104 (108) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
NC_V_APS | 96 (162) | Non Conformance constraint equation for Anglesea Power Station | Outage | Non-Conformance
V>>S_HYML_1 | 90 (107) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 1 | Outage | SA
T>T_NIL_BL_5C | 89 (2) | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
S>V_NWRB2_RBNW1 | 86 (15) | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage | SA
N^N_KKLS_1 | 82 (19) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
V::S_NIL_MAXG_xxx | 79 (4) | Out = Nil, Vic to SA Transient Stability limit for loss of the largest generation unit in SA There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
T>>T_NIL_BL_EXP_6E | 73 (0) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
V>>SML_NIL_7A | 72 (14) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line This constraint equation only binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for high flows on Murraylink into SA. | NIL | Vic
S>>V_NIL_NOTI_x and S>NIL_NOTI_x | 69 (1) | Out = Nil with Torrens Island 66kV CB6W2, CB6W3 & CB6E6 open; avoid O/L of Torrens Island - New Osborne 66kV No.4 line on trip of Torrens Island - New Osborne 66kV No.3 line, Feedback | NIL | SA
VSML_220 | 68 (5) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
NC_N_SITHE01 | 61 (1) | Non Conformance Constraint for Smithfield Energy Facility | Outage | Non-Conformance
V>>S_HYML_2 | 58 (58) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 2 | Outage | SA
S>NIL_NIL_MYSG-T | 55 (13) | Out = Nil, avoid overloading Mayura to Snuggery 132 kV line on no line trips | NIL | SA
V^SML_NSWRB_2 | 54 (12) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
S>V_NIL_NIL_RBNW | 52 (73) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink and AEMO expects it to continue to bind for a similar amount in 2014. | NIL | SA
T>>T_NIL_BL_EXP_5F | 43 (1) | Out = Nil, avoid overloading a Hadspen to George Town 220 kV line for trip of the other Hadspen to George Town 220 kV line considering NCSPS action | NIL | Tas
V>>V-MSUT_1 | 43 (0) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | Outage | Vic
NC_V_YWPS1 | 43 (52) | Non Conformance Constraint for Yallourn 'W' 1 Power Station | Outage | Non-Conformance
V>SMLBAHO4 | 42 (12) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage | Vic
V>>S_NIL_PWKN_SGKH | 41 (0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL | SA
T>T_NIL_BL_110_18_1 | 41 (10) | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
V>>S_PWSE_SETB_SGKH | 40 (0) | Out = Penola West to South East 132 kV line, avoid overloading Snuggery to Keith 132 kV line on trip of South East to Tailem Bend 275 kV line | Outage | SA
T_GO_ZERO | 37 (0) | Discretionary 0 MW upper limit on total Gordon generation | Outage | Tas
V^^S_PAVC_MAXG | 36 (15) | Out = Para one SVC, VIC to SA Voltage Stability limit for loss of the largest generation unit in SA | Outage | SA
N>>V_DBUSS_1 | 36 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line DBUSS - line is a control scheme that splits Dederang 330 kV bus on trip of a Murray to Dederang line. This was implemented to allows higher NSW to Vic interconnector capability. For a number of outages in southern NSW and northern Victoria either the line or transformer control schemes are also taken out of service. | Outage | NSW
V>V_NIL_GGMS_1 | 35 (0) | Out = Nil, avoid overloading Guthega to Murray (97G/3) 132 kV line | NIL | Vic
V>S_NWRB2_NWRB1 | 34 (0) | Out = North West Bend to Robertstown No.2 132 kV line, avoid overloading North West Bend to Robertstown No.1 132 kV line | Outage | Vic
T>T_GTHA_IMP_4J | 34 (0) | Out = Hadspen to George Town No. 1 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
N^Q_NIL_A | 33 (0) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
NC_V_YWPS2 | 32 (23) | Non Conformance Constraint for Yallourn 'W' 2 Power Station | Outage | Non-Conformance
NRM_QLD1_NSW1 | 30 (20) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V>>V_NIL1A_R | 30 (47) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line This constraint equation only binds for high flows from Victoria to NSW | NIL | Vic
NSA_Q_BARCALDN | 30 (18) | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
V>>SML_NIL_8 | 29 (0) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
T>T_GTHA_5L | 29 (19) | Out = Hadspen to George Town 220 kV line, avoid O/L line terminal equipment of Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line, feedback | Outage | Tas
VS_250 | 27 (39) | Victoria to South Australia on Heywood upper transfer limit of 250 MW This constraint equation is included in a number of constraint sets which are used for outages of the 500 kV lines in from Sydenham to Heywood and the 275 kV lines from Heywood to South East. | Outage | Vic
T>T_NIL_NCSPS5_1B | 27 (0) | Out = Nil, avoid overloading the line terminal equipment of either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line | NIL | Tas
S>>NIL_SETB_KHTB1 | 27 (14) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
V^^S_TBTX4_MAXG | 26 (0) | Out =Tailem Bend 275/132 kV transformer #4; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S) | Outage | SA
NC_V_YWPS4 | 25 (28) | Non Conformance Constraint for Yallourn 'W' 4 Power Station | Outage | Non-Conformance
T>T_GTHA_IMP_4H | 25 (0) | Out = Hadspen to George Town No. 2 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
N^^V_NIL_2 | 24 (5) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL | NSW
T>T_TU_LE_WA12_2 | 23 (0) | Out = either Tungatinah to Waddamana 110kV line (direct or via Lake Echo tee), avoid O/L the remaining Tungatinah to Waddamana 110 kV line (flow to North) for loss of the Meadowbank to New Norfolk No.2 line, feedback | Outage | Tas
V::N_HYSE_xxx | 22 (42) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
T>T_PMWA_IMP_4D | 22 (0) | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
NC_N_REDBANK1 | 21 (18) | Non Conformance Constraint for Redbank Power Station | Outage | Non-Conformance
Q>>NIL_871_855 | 21 (100) | Out = Nil, avoid overload on Calvale to Stanwell (855) 275 kV line on trip of Calvale to Wurdong (871) 275 kV line | NIL | Qld
NC_Q_CPP_4 | 21 (23) | Non Conformance Constraint for Callide C CPP_4 | Outage | Non-Conformance
V>>SML_NIL_7B | 21 (3) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
T_MRWF_ZERO | 20 (0) | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Tas
NSA_S_PORxxx | 20 (0) | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
N>N-EWMB_TE_A | 19 (40) | Out = Ballina to Lennox Head 66 kV line, avoid overloading Lismore to Dunoon 132 kV line on trip of the other Lismore to Dunoon 132 kV line | Outage | NSW
NC_V_YWPS3 | 19 (32) | Non Conformance Constraint for Yallourn 'W' 3 Power Station | Outage | Non-Conformance
S>>NIL_SETB_KHTB2 | 19 (0) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
S>MYTX2_MYTX1 | 18 (4) | Out = Mayura 132/33 kV transformer #2 with the 33kV bus tie isolator 44248 closed, avoid O/L Mayura 132/33 kV transformer #1, Feedback. | Outage | SA
V::N_MSUT_xxx | 17 (21) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
NQTE_ROC | 17 (25) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
T>T_GTHA_IMP_4I | 17 (0) | Out = Hadspen to George Town No. 2 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of either Sheffield to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_GTHA_IMP_4O | 16 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Sheffield) for trip of remaining Hadspen to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
N^^Q_MPP_N-2 | 16 (0) | Out = Nil, avoid Voltage Collapse on trip of Millmerran 1 & 2 declared credible | Outage | NSW
T^V_NIL_8 | 16 (0) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, swamped if TVCC in service | NIL | Tas
T>T_GTHA_IMP_4K | 16 (6) | Out = Hadspen to George Town No. 1 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of either Sheffield to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
V_MACARTHUR_ZERO | 15 (0) | Macarthur upper limit of 0 MW | Outage | Vic
VTBL_ROC | 15 (23) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
T>T_GTSH_IMP_4D | 15 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
V^^S_MOTB_MAXG | 15 (0) | Out= Mobilong - Tailem Bend 132kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage | SA
V>>V_NIL_1B | 15 (7) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
#SNOWSTH1_E | 14 (0) | SBLWS2.ENERGY * 1 <= 96 (Wt = 360) | Outage | Quick
T>T_HAGT_N-2 | 14 (0) | Out=NIL, Loss of both Hadspen to George Town 220kV lines or Palmerston to Hadspen 220kV lines declared credible, Restrict the power flow on HA-GT corridor based on AETV CCGT service status | Outage | Tas
S-LB2_0 | 14 (1) | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
T>T_NIL_LIPM_N-2_2A | 14 (6) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to North) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
V^^S_PWSE_MAXG | 14 (2) | Out= Penola West - South East 132 kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
N^N_CHLS_1 | 14 (1) | Out = Coffs Harbour to Lismore (89) 330 kV line, avoid voltage collapse on trip of Koolkhan to Lismore 132 kV line (967) | Outage | NSW
TVBL_ROC | 13 (17) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
V>SML_BUDP_2 | 13 (33) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
T>T_GTSH_IMP_4E | 13 (5) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>SML_NIL_1 | 13 (3) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
T>T_GTHA_1E | 13 (0) | Out = Hadspen to George Town No. 2 220 kV line, avoid pre-contingent O/L of the Hadspen to George Town No. 1 220kV line (flow to George Town), feedback | Outage | Tas
N^Q_ARTW_1 | 13 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage | NSW
T>T_GTSH_220_1_N-2 | 13 (11) | Out = Nil, loss of both Georgetown to Sheffield 220 kV lines declared credible, avoid overloading the Sheffield to Palmerston 220 kV line (flow to south) for loss of both Georgetown to Sheffield 220 kV lines | Outage | Tas
TV_315 | 12 (0) | Tas to Vic on Basslink upper limit of 315 MW | Outage | Tas
T>T_FASH_1_N-2 | 12 (2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
T_ROCOF_1 | 12 (0) | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
QNTE_ROC | 12 (18) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
T>T_HAPM_1B | 12 (0) | Out = Hadspen to Palmerston No. 1 220 kV line, avoid pre-contingent O/L of the Hadspen to Palmerston No. 2 220kV line (flow North), feedback | Outage | Tas
T>T_GT_HA_3A_N-2 | 12 (0) | Out = NIL, Loss of both Hadspen to Georgetown 220kV lines declared credible, avoid O/L the Sheffield to Palmerston 220 kV line (flow to North) for loss of both Hadspen to Georgetown 220 kV lines | Outage | Tas
T>T_FASH_1_2_C1 | 11 (8) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hampshire link closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
NC_T_POAT110 | 11 (9) | Non Conformance Constraint for Poatina 110kV Power Station | Outage | Non-Conformance
T>T_GTSH_5K | 11 (4) | Out = Sheffield to Georgetown 220 kV line, avoid O/L line terminal equipment of Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
TV_500 | 11 (0) | Tas to Vic on Basslink upper limit of 500 MW | Outage | Tas
V::N_NIL_xxx | 11 (420) | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
NC_Q_CPP_3 | 11 (12) | Non Conformance Constraint for Callide C CPP_3 | Outage | Non-Conformance
T>T_GTSH_IMP_4K | 10 (83) | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
NC_N_VP6 | 10 (5) | Non Conformance Constraint for Vales Point VP6 Power Station | Outage | Non-Conformance
V^^S_MOTB+PAVC_MAXG | 10 (0) | Out= Mobilong - Tailem Bend 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
V_T_NIL_BL1 | 9 (53) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
T>T_GTSH_IMP_4A | 9 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAGT_SHGT_N-2 | 9 (0) | Out= NIL, Loss of both Sheffield to Georgetown 220kV lines declared credible, avoid O/L the Hadspen to Georgetown 220kV line for loss of both Sheffield to Georgetown 220kV lines, Feedback | Outage | Tas
V>>S_KNPW_SETB_SGKH | 9 (2) | Out= Kincraig - Penola West 132kV line, avoid O/L Snuggery - Keith 132kV on trip of one South East - Tailem Bend 275kV line, Feedback | Outage | SA
Q_CS_1100 | 9 (0) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer | Outage | Qld
S_CMWF_0 | 9 (33) | Discretionary upper limit for Clements Gap WF generation of 0 MW | Outage | SA
N>N-GITN_TE_C1 | 9 (5) | Out = Glen Innes to Tenterfield (96R) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
T_T_BA_JB_RC2_250 | 8 (0) | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
NC_T_POAT220 | 8 (14) | Non Conformance Constraint for Poatina 220kV Power Station | Outage | Non-Conformance
V::N_HWSM_xxx | 8 (48) | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
VT_ZERO | 8 (0) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
T_FASH_MAXGEN_1 | 8 (0) | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link closed. Constraint swamped if only one machine on line | Outage | Tas
S_PF_4_UNITS | 8 (15) | Out = 4 Playford generators, upper limit on Playford generation of 0MW | Outage | SA
S>>V_KNPW_SETX_SETX | 8 (2) | Out = Kincraig to Penola West 132 kV line, avoid overloading the remaining South East 275/132kV transformer on trip of one South East 275/132kV transformer | Outage | SA
V>>S_NIL_NIL_SGKHC | 7 (15) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on Nil trip, Feedback | NIL | SA
NC_N_TALWA1 | 7 (9) | Non Conformance Constraint for Tallawarra Power Station | Outage | Non-Conformance
NSA_V_BDL0xxx | 7 (7) | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
S>>XSEVC1+CB_SETB2_4 | 7 (0) | Out= South East #1 SVC and South East CB6606 & CB6610, avoid O/L Snuggery - Keith 132kV on trip of South East - Tailem Bend #2 275kV line, Feedback | Outage | SA
T>T_HAPM_2B | 7 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow North) for trip of a Sheffield to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V>>N_SMTXF2_2 | 7 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Ballarat to Bendigo 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
N_GUNNING1_ZERO | 6 (16) | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
V>>S_TBTU_TBCG_TBMO | 6 (0) | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage | SA
V>SMLBAHO1 | 6 (5) | Out = Ballarat to Horsham, or Bendigo to Kerang line, avoid overloading or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang or Ballarat to Horsham line | Outage | Vic
S>S_PAPG_PPLF_PSSB | 6 (0) | Out= Para to Parafield Gardens West 275kV line, avoid O/L Parafield Gardens-Salisbury #1 66kV on trip of Pelican Point-Lefevre 275kV line, Feedback | Outage | SA
T>>T_GTHA_EXP_3H | 6 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_HAPM_5L | 6 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L line terminal equipment of Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line, feedback | Outage | Tas
T>T_GTSH_2C | 6 (6) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
NC_N_WW8 | 6 (2) | Non Conformance Constraint for Wallerawang WW8 Power Station | Outage | Non-Conformance
S>>V_NIL_RBTXW_RBTX1 | 6 (49) | Out = Nil, avoid overloading Robertstown No.1 275/132 kV transformer on trip of the Robertstown No.2 275/132 kV transformer This constraint equation normally binds when there is high generation from Northern, Hallett GT and the wind farms connected to the 275 kV between Robertstown and Davenport. | NIL | SA
T>T_NIL_BL_IMP_6E | 6 (234) | Out = Nil, avoid overloading Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) on trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action | NIL | Tas
S>>XSEVC2+CB_SETB1_4 | 6 (0) | Out= South East #2 SVC and South East CB6607 & CB6611, avoid O/L Snuggery - Keith 132kV on trip of South East - Tailem Bend #1 275kV lines, Feedback | Outage | SA
S>>X_TBTU+CB_TBCG_1 | 6 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage | SA
T_MRWF_UPLIM | 6 (0) | Limit Musselroe generation to current MW + 10 | Outage | Tas
T>T_SHGT_N-2 | 6 (0) | Out=NIL, Loss of both Sheffield to George Town 220kV lines declared credible, Restrict the power flow on SH-GT corridor based on AETV CCGT service status | Outage | Tas
T_GO_250 | 6 (0) | Discretionary 250 MW upper limit on total Gordon generation | Outage | Tas
N>N-ARGI_TE_C1 | 6 (0) | Out= Armidale to Glen Innes (96T), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 Directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
V>>V_NIL_5 | 6 (7) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
S>SE132CB_SETX_SGKH | 6 (22) | Out = South East CB6160 or CB6162, avoid overloading Snuggery to Keith 132 kV line on trip of a South East 275/132 kV transformer | Outage | SA
TV_325 | 6 (0) | Tas to Vic on Basslink upper limit of 325 MW | Outage | Tas
T_V_NIL_BL1 | 5 (21) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
V>>V_SMTXF2_4AR | 5 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Richmond to Brunswick 220 kV cable on trip of Rowville A1 500/220 kV transformer | Outage | Vic
T>T_NIL_BL_IMP_3F | 5 (0) | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Tas
NC_T_CETHANA | 5 (0) | Non Conformance Constraint for Cethana Power Station | Outage | Non-Conformance
T>T_GTSH_IMP_4F | 5 (2) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow North) for trip of Hadspen to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_110_IMP_4B | 5 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L a Palmerston to Hadspen No. 1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
S>BGCB6246_BGPT_HUWT | 5 (0) | Out= Bungama 132kV East Bus(i.e.Bungama 132kV CB6246 & CB6243 & Bungama 132/33kV No.3 TX O/S) OR Bungama CB6246 O/S, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama- Port Pirie 132kV line, feedback. | Outage | SA
T>>T_GTSH_EXP_3H | 5 (2) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage | Tas
#T-V-MNSP1_E_E | 5 (0) | T-V-MNSP1. * 1 <= 290 (Wt = 35) | Outage | Quick
CA_SPS_40D62A5B_01 | 5 (0) | During the outage of Hazelwood A2 500/220kV transformer with the Victorian network configured in 3/5 Parallel at Hazelwood four Yallourn units tripped. RTCA (Real Time Contingency Analysis) indicated that trip of Hazelwood to Yallourn No.1 or No.2 would cause overload on the remaining line. Constraint Automation was used to manage this issue. | Outage | Constraint Automation
T>T_GTHA_IMP_4L | 5 (33) | Out = Hadspen to Georgetown 220 kV line, avoid overloading Sheffield to Georgetown No.1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No.2 220 kV line with no NCSPS action | Outage | Tas
S_LB2WF_CONF | 5 (6) | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
N>Q_LSLS_9U8 | 4 (9) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage | NSW
NC_N_VP5 | 4 (6) | Non Conformance Constraint for Vales Point VP5 Power Station | Outage | Non-Conformance
Q:N_NIL_BCK2L-G | 4 (115) | Out = Nil, avoid transient instability for a 2 phase to ground fault on a Bulli Creek to Dumaresq 330 kV line at Bulli Creek For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_OSC will bind. | NIL | Qld
S>>X_TBTU+CB_CGTB_4 | 4 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Mobilong - Tailem Bend 132kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | Outage | SA
N>>N-WWSS+WWIG_3 | 4 (0) | Out = Sydney South to Wallerawang & Ingleburn to Wallerawang(76 + 77), avoid Mt. Piper 500/330kV tie Tx overload on trip of the other; Feedback | Outage | NSW
V::S_MAXG_NPS_N-2 | 4 (0) | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA with loss of both Northern Power Station units declared as credible. | Outage | SA
Q>NIL_CLBCN_7350 | 4 (6) | Out = Nil, avoid overloading Chinchilla to Columboola (7350) 132 kV line on trip of Chinchilla to Columboola (7349) 132 kV line | NIL | Qld
NC_N_MP2 | 4 (1) | Non Conformance Constraint for Mt Piper 2 Power Station | Outage | Non-Conformance
V>>V-HWLY_3 | 4 (0) | Outage = Hazlewood to Loy Yang (HWTS-LYPS) No.3 500kV line, avoid overloading Hazelwood to Loy Yang No.1 or No.2 500kV line on trip of any of the remaining Hazelwood to Loy Yang 500kV line,feedback | Outage | Vic
V^^S_MTSE+PAVC_MAXG | 4 (0) | Out= Mt Gambier - South East 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
N^^Q_BCDM_B1 | 4 (0) | Out = One Bulli Creek - Dumaresq (8L or 8M) 330 kV line, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V>>S_HYML_4 | 4 (54) | Out = one Heywood 500/275 kV transformer, avoid overloading remaining Heywood 500/275 kV transformer for loss of a Pelican Point GT and consequent offloading of Pelican Point ST | Outage | SA
I_CTRL_ISSUE_TE | 4 (0) | DC Link Control Issue Constraint for Terranora | Outage | Other
NRM_NSW1_VIC1 | 4 (2) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
T>T_PMSH_IMP_4A | 4 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
#SNOWNTH1_E | 4 (0) | SBLWS1.ENERGY * 1 <= 54 (Wt = 360) | Outage | Quick
N::Q_BWMP_KC | 4 (0) | Out = Bayswater to Mt Piper(5A3) 500 kV line or Bayswater to Wollar(5A4) 500 kV line or Wollar to Mt. Piper (5A5) 500 kV line, NSW to Qld Transient Stability Limit for trip of Kogan Creek | Outage | NSW
S^NIL_PL_MAX | 4 (2) | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
TV_410 | 4 (0) | Tas to Vic on Basslink upper limit of 410 MW | Outage | Tas
T_V_NIL_FCSPS | 4 (2) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
V>S_NIL_NIL_HYTX1 | 4 (1) | Out = NIL, avoid O/L Heywood M1 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL | Vic
NC_Q_SWAN_E | 3 (3) | Non Conformance Constraint for Swanbank E Power Station | Outage | Non-Conformance
V::S_XKHTB1+2_SETB | 3 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S; Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage | SA
V>>N-WA_330_BUSB_2 | 3 (0) | Out = Wagga 330kV B Bus(Wagga Bus B), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
N^^Q_ARDM_B1 | 3 (7) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage | NSW
NC_Q_BRAEMAR3 | 3 (2) | Non Conformance Constraint for Braemar 3 Power Station | Outage | Non-Conformance
V>>S_NIL_KHTB2_KHTB1 | 3 (4) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV one trip of Keith - Tailem Bend #2 132kV line, Feedback | NIL | SA
NC_V_BDL02 | 3 (5) | Non conformance constraint equation for Bairnsdale 2 power station | Outage | Non-Conformance
T>T_HAPM_220_5A_N-2 | 3 (0) | Out = NIL, Loss of both Hadspen to Palmerston 220kV lines declared credible, avoid O/L either Palmerston to Hadspen (No. 3 or No. 4) 110kV line (flow to North) for loss of both Hadspen to Palmerston 220kV lines, feedback | Outage | Tas
V::S_HYSE | 3 (0) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of one NPS unit or South East-Tailem Bend 275 kV line. | Outage | SA
V>>N-NIL_HA | 3 (9) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL | Vic
T_MRWF_42 | 3 (0) | Discretionary 42 MW upper limit on Musselroe Wind Farm | Outage | Tas
T>T_NIL_BL_220_6B | 3 (15) | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
T_FARC1 | 3 (0) | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
T_FARC2 | 3 (0) | Out=Farrell-Reece 2 220KV line. Energy <= 0MW | Outage | Tas
T_X_GTSH_1 | 3 (0) | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation <= West Coast + North West load + 10MW, limiting SH-PM line flow to 10 MW | Outage | Tas
V_HYML1_5 | 3 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No. 1 500 kV line, limit voltage unbalance at the APD 500 kV bus, two Mortlake units in service | Outage | Vic
N>N-NIL__4_15M | 3 (1) | Out = Nil, avoid overloading Muswellbrook to Tamworth (88) 330 kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL | NSW
NC_Q_KPP_1 | 3 (2) | Non Conformance Constraint for Kogan Creek Power Station | Outage | Non-Conformance
NC_Q_TNPS1 | 3 (0) | Non Conformance Constraint for Tarong North Power Station | Outage | Non-Conformance
N^N-89_LSTX_SVC | 3 (3) | Out = Coffs Harbour to Lismore (89) 330 kV line and Lismore 330/132 kV transformer with Lismore SVC in reactive power control mode, avoid voltage collapse on trip of Koolkhan to Lismore (967) 132 kV line | Outage | NSW
T>T_HAPM_1A | 3 (0) | Out = Hadspen to Palmerston No. 2 220 kV line, avoid pre-contingent O/L of the Hadspen to Palmerston No. 1 220kV line (flow North), feedback | Outage | Tas
V^^S_KNPW+PAVC_MAXG | 3 (0) | Out= Kincraig - Penola West 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
NC_N_WW7 | 3 (3) | Non Conformance Constraint for Wallerawang WW7 Power Station | Outage | Non-Conformance
NC_V_HWPS7 | 3 (2) | Non Conformance Constraint for Hazelwood HWPS 7 Power Station | Outage | Non-Conformance
T>>T_GTSH_EXP_3FH | 3 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown and Palmerston to Sheffield 220 kV line for trip of Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overloads. | Outage | Tas
V>>N_DDMS_2 | 3 (6) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Murray to Dederang 330 kV line, feedback | Outage | Vic
S>>MOTB_TBTU_TBCG | 3 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
T>T_NIL_BL_5B | 3 (0) | Out = Nil, avoid pre-contingent O/L of the Hadspen to Georgetown No. 2 220kV line (flow to North), feedback | NIL | Tas
NC_V_NPS | 3 (4) | Non Conformance Constraint for Newport Power Station | Outage | Non-Conformance
V::S_TBCP_MAXG_2 | 3 (0) | Out= Tailem Bend 275kV Cap Bank (Tungkillo 275kV Cap available); Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S) (Swamp out if SA demand less/equal to 3200MW) | Outage | SA
NC_T_LI_WY_CA | 2 (7) | Non Conformance Constraint for Liapootah + Wayatinah + Catagunya Power Stations | Outage | Non-Conformance
NC_V_BDL01 | 2 (2) | Non Conformance constraint equation for Bairnsdale 1 Power Station | Outage | Non-Conformance
N^^Q_ARTW_MPP_N-2 | 2 (0) | Out = Armidale to Tamworth (85 or 86) and trip of both Millmerran units declare credible, avoid Voltage collapse on loss of both Millmerran units | Outage | NSW
V>>S_HYML_3 | 2 (0) | Out = One Heywood 500/275 kV txfmr in service only, prevent overload of the in service 500/275 kV Heywood transformer for loss of Lake Bonney Wind Farm | Outage | SA
NC_T_BBTHREE1 | 2 (0) | Non Conformance Constraint for Bell Bay Three Unit 1 Power Station | Outage | Non-Conformance
T>>T_GTHA_EXP_3GH | 2 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Hadspen to George Town and Sheffield to George Town 220 kV line for trip of Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
V::S_SESG_SETB | 2 (0) | Out= South East-Snuggery 132kV (including line section connecting Lake Bonney WFs + Lake Bonney WFs O/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line (Note: with NPS and Playford PS assumed to be O/S). | Outage | SA
V>>S_KHTB1_SETB_KHTB | 2 (0) | Out = Keith - Tailem Bend #1 132 kV line. Prevent Keith - Tailem Bend #2 line OL for South East - Tailem Bend line trip. | Outage | SA
V^^S_TBCPTX_MAXG | 2 (0) | Out= Tailem Bend 275/132kV transformer and Tailem Bend 100Mvar Cap Bank; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage | SA
#V-SA_RAMP_I_F | 2 (8) | V-SA >= MIN(-70, InitialFlow + 50) (Wt=35) | Outage | Quick
N>>N-RGSW_A | 2 (0) | Out = Regentville to Sydney West(38), avoid Bayswater to Liddell(34) O/L on Bayswater to Liddell(33) trip; Feedback | Outage | NSW
NC_V_LYA2 | 2 (11) | Non Conformance Constraint for Loy Yang A2 Power Station | Outage | Non-Conformance
V::S_SEVC_MAXG_2 | 2 (0) | Out= South East one SVC; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
V_MACARTHUR_210 | 2 (2) | Limit Macarthur Wind Farm to 210 MW to limit voltage unbalance at the APD 500 kV bus | Outage | Vic
N>Q-MUTW_2 | 2 (0) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage | NSW
NC_V_HWPS6 | 2 (1) | Non Conformance Constraint for Hazelwood HWPS 6 Power Station | Outage | Non-Conformance
NC_V_LYA1 | 2 (20) | Non Conformance Constraint for Loy Yang A1 Power Station | Outage | Non-Conformance
N>>N-DP_TIETX_A | 2 (0) | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (330 to 220 kV) on Kerang-Bendigo trip; Feedback | Outage | NSW
NC_Q_BARRON-1 | 2 (2) | Non Conformance Constraint for Barron Gorge 1 Power Station | Outage | Non-Conformance
NRM_VIC1_SA1 | 2 (0) | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
Q:N_NIL_OSC | 2 (25) | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
Q>>NIL_871_855_POST | 2 (0) | Out = Nil, Post-8868 commissioning, avoid overload on Calvale to Stanwell (855) 275kV line on trip of Calvale to Wurdong (871) 275kV line, Feedback | NIL | Qld
T>T_X_HAPM110_1 | 2 (0) | Out= both Palmerston to Hadspen 110 kV lines, avoid O/L either Palmerston to Hadspen 220 kV line (flow to North) on trip of the parallel Palmerston to Hadspen 220 kV line, feedback | Outage | Tas
V::N_LTWG_xxx | 2 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V::N_SMF2_xxx | 2 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
NC_S_AGLHAL | 2 (1) | Non Conformance Constraint for AGL Hallet Power Station | Outage | Non-Conformance
NC_T_BLNKTAS | 2 (0) | Non Conformance Constraint for Basslink from Tas to Vic | Outage | Non-Conformance
V>V_NIL_7 | 2 (1) | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Vic
NC_V_HWPS8 | 2 (1) | Non Conformance Constraint for Hazelwood HWPS 8 Power Station | Outage | Non-Conformance
N^^V_MSDD2 | 2 (2) | Out = Dederang to Murray 330 kV line, avoid voltage collapse for trip of the remaining Dederang to Murray 330 kV line | Outage | NSW
Q>>BRTR_MRTX5_MRTX4 | 2 (0) | Out = Braemar to Tarong (8814 or 8815) 275 kV line, avoid overloading Middle Ridge 330/275 kV No.4 transformer, on trip of Middle Ridge 330/275 kV No.5 transformer | Outage | Qld
CA_SPS_40381C26_01 | 2 (0) | Constraint Automation, O/L MOBTAB_1 @T_BEND for CTG LSIQ on trip of CH_GDN - T_BEND 275KV LINE. Generated by STNET[MANFR] Host NOREEMP3(SP) | Outage | Constraint Automation
NC_N_ER02 | 2 (0) | Non Conformance Constraint for Eraring ER02 Power Station | Outage | Non-Conformance
NC_Q_BRAEMAR1 | 2 (4) | Non Conformance Constraint for Braemar 1 Power Station | Outage | Non-Conformance
N^^V_MSUT_1 | 2 (2) | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
S>>V_NIL_NIL_HUWT | 2 (2) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL | SA
N>N-ARCH_87_TE_C1 | 2 (0) | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | NSW
NC_Q_KAREEYA1 | 2 (2) | Non Conformance Constraint for Kareeya 1 Power Station | Outage | Non-Conformance
NC_T_TREVALLN | 2 (3) | Non Conformance Constraint for Trevallyn Power Station | Outage | Non-Conformance
NRM_VIC1_NSW1 | 2 (5) | Negative Residue Management constraint equation for VIC to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
S_NBH_0 | 2 (0) | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | SA
T>T_NIL_BL_IMP_6EE | 2 (0) | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
#NSW1-QLD1_E_E | 2 (0) | NSW1-QLD1.ENERGY * 1 <= 125 (Wt = 20) | Outage | Quick
NC_Q_GSTONE6 | 2 (2) | Non Conformance Constraint for Gladstone 6 Power Station | Outage | Non-Conformance
NC_V_LOYYB2 | 2 (1) | Non Conformance Constraint for Loy Yang B2 Power Station | Outage | Non-Conformance
N^^V_LTUT_1 | 2 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
N^^V_LTUT_2 | 2 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage | NSW
T>T_BUSH1_220 | 2 (0) | Out = Burnie to Sheffield 220kV line, Hampshire link open, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer | Outage | Tas
T>T_HAPM_IMP_4C | 2 (0) | Out = Hadspen to Palmerston No. 1 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_NIL_NCSPS5_5FF | 2 (0) | Out = Nil, avoid overloading the line terminal equipment of the Hadspen to Georgetown No. 2 220 kV line (flow to North) for trip of the Hadspen to Georgetown No. 1 220 kV line, feedback equation | NIL | Tas
V>>S_TB6125+28_KHTB1 | 2 (0) | Out = Tailem Bend CBs 6125 and/or 6128 (both or either CB); Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend 132kV #1 line for loss of Tailem Bend transformer #4. | Outage | SA
N>>N-NIL_1A_OPENED & CLOSED | 2 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL | NSW
NC_Q_TARONG#1 | 2 (2) | Non Conformance Constraint for Tarong 1 Power Station | Outage | Non-Conformance
NC_V_HWPS2 | 2 (2) | Non Conformance Constraint for Hazelwood HWPS 2 Power Station | Outage | Non-Conformance
NC_V_MORTLK11 | 2 (0) | Non Conformance Constraint for Mortlake GT unit 1 | Outage | Non-Conformance
Q>NIL_CLBCN_7349 | 2 (1) | Out = Nil, avoid overloading Chinchilla to Columboola (7349) 132 kV line on trip of Chinchilla to Columboola (7350) 132 kV line | NIL | Qld
S>NIL_BWPA_HUWT | 2 (0) | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West - Para 275kV line, Feedback | NIL | SA
V>>N-WA_330_BUSB_1 | 2 (0) | Out = Wagga 330kV B Bus(Wagga Bus B), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
V_HWMW | 2 (0) | Out = Hazelwood PS to Morwell PS 220 kV line, Limit Morwell Units 4 & 5 upper limit set to zero | Outage | Vic
V_HYMO2_1 | 2 (3) | Out = Heywood to Mortlake No.2 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
NC_N_LD02 | 1 (2) | Non Conformance Constraint for Liddell LD02 Power Station | Outage | Non-Conformance
SV_200 | 1 (0) | SA to Victoria on VicSA upper transfer limit of 200 MW | Outage | SA
T>T_GTHA_1F | 1 (0) | Out = Hadspen to George Town No. 1 220 kV line, avoid pre-contingent O/L of the Hadspen to George Town No. 2 220kV line (flow to George Town), feedback | Outage | Tas
T>T_NIL_BL_IMP_5H | 1 (0) | Out = Nil, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow to North) for trip of either Sheffield to Georgetown 220 kV line with no SPS action, feedback | NIL | Tas
V>>V_SMTXF2_6 | 1 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage | Vic
CA_SPS_41CE7351_01 | 1 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N>>V-NIL_O | 1 (0) | Out = Nil, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line and subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | NIL | NSW
NC_V_HWPS3 | 1 (0) | Non Conformance Constraint for Hazelwood HWPS 3 Power Station | Outage | Non-Conformance
S_TBL_0 | 1 (0) | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
V>>SML_NIL_7C | 1 (0) | Out = Nil, avoid O/L Arrarat to Stawell 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
V>>V_NIL_3 | 1 (0) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL | Vic
V^^S_SEVC_MAXG | 1 (4) | Out= South East one SVC; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
N>>N-KVCW_9 | 1 (0) | Out = KangarooValley to Capital(3W), avoid Yass to Canberra(9) O/L on Yass to Lower Tumut(3) trip; Feedback | Outage | NSW
NC_N_LD03 | 1 (2) | Non Conformance Constraint for Liddell LD03 Power Station | Outage | Non-Conformance
NC_T_BBTHREE2 | 1 (0) | Non Conformance Constraint for Bell Bay Three Unit 2 Power Station | Outage | Non-Conformance
NC_V_HWPS1 | 1 (2) | Non Conformance Constraint for Hazelwood HWPS 1 Power Station | Outage | Non-Conformance
NC_V_HWPS5 | 1 (2) | Non Conformance Constraint for Hazelwood HWPS 5 Power Station | Outage | Non-Conformance
T>>T_NIL_BL_EXP_1B | 1 (0) | Out = Nil, avoid O/L a Gordon to Chapel St 220 kV line for trip of the parallel line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_FASH_2_N-2 | 1 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.2 transformer | Outage | Tas
T>T_HAPM_IMP_4D | 1 (0) | Out = Hadspen to Palmerston No. 1 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow North) for trip of either Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
TV_350 | 1 (0) | Tas to Vic on Basslink upper limit of 350 MW | Outage | Tas
#N-Q-MNSP1_I_E | 1 (8) | Quick constraint equation applied to Terranora Interconnector at various levels | Outage | Quick
#V-S-MNSP1_E_E | 1 (0) | V-S-MNSP1.ENERGY * 1 = 6 (Wt = 20) | Outage | Quick
NC_Q_GSTONE5 | 1 (1) | Non Conformance Constraint for Gladstone 5 Power Station | Outage | Non-Conformance
NC_T_DEVILS_G | 1 (0) | Non Conformance Constraint for Devils Gate Power Station | Outage | Non-Conformance
NC_V_LYA4 | 1 (11) | Non Conformance Constraint for Loy Yang A4 Power Station | Outage | Non-Conformance
NC_V_MORTLK12 | 1 (12) | Non Conformance Constraint for Mortlake GT unit 2 | Outage | Non-Conformance
T>>T_GTSH_EXP_3C | 1 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage | Tas
T_LE_ZERO | 1 (0) | Discretionary 0 MW upper limit on Lake Echo generation | Outage | Tas
V>SMLBSRC2 | 1 (0) | Out = Buronga to Redcliffs (0X1) 220 kV line, avoid O/L Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line, feedback | Outage | Vic
V>V_NIL_ROYP56_R5_1 | 1 (0) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 500 kV, feedback | NIL | Vic
VS_150 | 1 (0) | Victoria to SA on VicSA upper transfer limit of 150 MW | Outage | Vic
#QLD1_E_20130223 | 1 (0) | Multiple QLD1 LHS <= 0 (Wt = 360) | Outage | Quick
NC_V_LOYYB1 | 1 (1) | Non Conformance Constraint for Loy Yang B1 Power Station | Outage | Non-Conformance
NC_V_LYA3 | 1 (5) | Non Conformance Constraint for Loy Yang A3 Power Station | Outage | Non-Conformance
CA_SPS_3FFA5B9A_01 | 1 (0) | Constraint Automation, O/L BATS_BETS_220 @BATS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
CA_SPS_41B92B29_02 | 1 (0) | Constraint Automation, O/L 84 @LIDDELL for CTG LNPF on trip of LIDDELL-MUSBK330 83 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N>N-ARTW86_1B | 1 (0) | Out = Armidale to Tamworth (86) 330 kV line, avoid overloading Tamworth to Armidale (85) 330 kV line on trip of largest Queensland generator | Outage | NSW
N>N-X_8505_9U6_1 | 1 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 66kV line between Mullumbimby and Ballina (8505,8508 or 8504), avoid O/L remaining 132kV line, NSW to Qld limit | Outage | NSW
NC_N_HUMENSW | 1 (0) | Non Conformance Constraint for Hume Hydro Power Station | Outage | Non-Conformance
T>T_FASH_3_N-2 | 1 (2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Hampshire link closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Tas
V^^S_TB6594_35_SETB | 1 (0) | Out= Tailem Bend 275kV CB6594 OR CB6535 O/S; Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
V_T_NIL_FCSPS | 1 (325) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
N::Q_30+38_KC | 1 (0) | Out= Liverpool-SydWest(30) + Regentville-SydWest(38) 330kV lines, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
NC_Q_STAN-3 | 1 (2) | Non Conformance Constraint for Stanwell STAN-3 Power Station | Outage | Non-Conformance
NC_T_TRIBUTE | 1 (0) | Non Conformance Constraint for Tribute Power Station | Outage | Non-Conformance
V::N_2RP_xxx | 1 (0) | Out = 2 dynamic reactive plant from Vic metro or SESS SVC's, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V>>S_KH_X_SETB_SETB | 1 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East - Tailembend 275kV on trip of one South East - Tailembend 275kV line, Feedback | Outage | SA
#NSW1-QLD1_I_E | 1 (0) | NSW1-QLD1.ENERGY * -1 >= 100 (Wt = 20) | Outage | Quick
#NSW1-QLD1_RAMP_I_F | 1 (3) | NSW1-QLD1 >= MIN(-130, InitialFlow + 200) (Wt=20) | Outage | Quick
N>LSDU9U6_LSDU9U7 | 1 (0) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
N>N-CHLS_TE_A1 | 1 (0) | Out = Coffs Harbour to Lismore (89) 330 kV line, avoid overloading Tenterfield to Lismore (96L) 132 kV line on trip of Koolkhan to Lismore (967) 132 kV line | Outage | NSW
N>N-LSTN_TE_C1 | 1 (5) | Out = Lismore to Tenterfield (96L) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
NC_N_BW04 | 1 (0) | Non Conformance Constraint for Bayswater 4 Power Station | Outage | Non-Conformance
NC_Q_GSTONE1 | 1 (2) | Non Conformance Constraint for Gladstone 1 Power Station | Outage | Non-Conformance
NC_V_HWPS4 | 1 (1) | Non Conformance Constraint for Hazelwood HWPS 4 Power Station | Outage | Non-Conformance
Q>>NIL_855_871_POST | 1 (0) | Out = Nil, Post-8868 commissioning, avoid overload on Calvale to Wurdong (871) 275kV line on trip of Calvale to Stanwell (855) 275kV line, Feedback | NIL | Qld
TV_560 | 1 (0) | Tas to Vic on Basslink upper limit of 560 MW | Outage | Tas
TV_ZERO | 1 (0) | Tas to Vic on Basslink upper limit of 0 MW | Outage | Tas
V>>V_SMTXF2_3P | 1 (0) | Out = South Morang F2 500/330 kV txfmr, avoid O/L Richmond to Brunswick 220 kV cable on NIL trip, 3/5 parallel mode, feedback | Outage | Vic
V>V_DDMB_1 | 1 (0) | Out= one Dederang to Mount Beauty 220 kV line, avoid O/L the remaining Dederang to Mount Beauty 220kV line on trip of the Eildon to Thomastown 220 kV line, feedback | Outage | Vic
V>V_NIL_HW3-BUS1_1 | 1 (0) | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus | NIL | Vic
#JBUTTERS_E | 1 (0) | TJB11.ENERGY * 1 <= 0 (Wt = 20) | Outage | Quick
#N-Q-MNSP1_RAMP_I_F | 1 (1) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage | Quick
CA_SPS_3FF8E592_02 | 1 (0) | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
NC_Q_STAN-2 | 1 (4) | Non Conformance Constraint for Stanwell STAN-2 Power Station | Outage | Non-Conformance
NC_Q_TARONG#3 | 1 (3) | Non Conformance Constraint for Tarong 3 Power Station | Outage | Non-Conformance
NC_S_OSB-AG | 1 (7) | Non Conformance Constraint for Osborne Power Station | Outage | Non-Conformance
NC_T_MUSSELR1 | 1 (0) | Non Conformance Constraint for MUSSELROE WF U 1-56 | Outage | Non-Conformance
Q>NIL_MRTA_B | 1 (0) | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line. | NIL | Qld
S_PLN_ISL32 | 1 (20) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T>T_HAPM_110_IMP_4A | 1 (0) | Out = Hadspen to Palmerston No. 3 110 kV line, avoid O/L the Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_220_5A | 1 (0) | Out = Hadspen to Palmerston 220kV line, avoid O/L either Palmerston to Hadspen (No. 3 or No. 4) 110kV line (flow to North) for loss of the remaining Hadspen to Palmerston 220kV line, Feedback | Outage | Tas
V::S_TBCB6594_MAXG_2 | 1 (0) | Out = Tailem Bend CB6594 O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available) with NPS and Playford assumed to be OOS. | Outage | SA
V>>N-JNWG_RADIAL_2 | 1 (0) | Out = Jindera to Wagga(62), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V>>V_KTS_TX_A2_2_P | 1 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage | Vic
V_HYML1_4 | 1 (1) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
CA_SPS_41C52A3F_01 | 1 (0) | Constraint Automation, O/L DDTS_SHTS_220 @DDTS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N>N-KKLS_TE_2 | 1 (1) | Out = Koolkhan to Lismore (967) 132 kV line, avoid overloading the Armidale to Glen Innes (96T) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects that this constraint equation will continue to bind for a reasonable portion of any future outage times. | Outage | NSW
NC_N_BW03 | 1 (1) | Non Conformance Constraint for Bayswater 3 Power Station | Outage | Non-Conformance
NC_Q_BARRON-2 | 1 (2) | Non Conformance Constraint for Barron Gorge 2 Power Station | Outage | Non-Conformance
NC_Q_GSTONE2 | 1 (2) | Non Conformance Constraint for Gladstone 2 Power Station | Outage | Non-Conformance
NC_Q_GSTONE4 | 1 (1) | Non Conformance Constraint for Gladstone 4 Power Station | Outage | Non-Conformance
NC_Q_STAN-4 | 1 (1) | Non Conformance Constraint for Stanwell STAN-4 Power Station | Outage | Non-Conformance
NC_S_DRYCGT1 | 1 (0) | Non Conformance Constraint for Dry Creek 1 Power Station | Outage | Non-Conformance
T>T_PMHA_SHGT_N-2 | 1 (0) | Out= NIL, Loss of both Sheffield to Georgetown 220kV lines declared credible, avoid O/L the Palmerston to Hadspen 220 kV line for loss of both Sheffield to Georgetown 220 kV lines, Feedback | Outage | Tas
T^V_GTSH_1 | 1 (0) | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse or voltage violations for trip of the remaining Sheffield to Georgetown 220 kV line | Outage | Tas
T_FISH | 1 (0) | Out=Sheffield-Fisher 220KV line. Energy <= 0MW | Outage | Tas
V^SML_NIL_3 | 1 (0) | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW | NIL | Vic
V^^S_SECP_MAXG | 1 (0) | Out = South East 275 kV capacitor; Vic to SA Long Term Voltage Stability limit for loss of one NPS generator or the largest generation block in SA (Note: with NPS and Playford assumed I/S). | Outage | SA
V::S_SETB_SETB | 1 (86) | Out = South East to Tailem Bend 275 kV line, avoid transient instability for loss of the parallel South East to Tailem Bend 275 kV line | Outage | SA
N>>N-BYYS_4 | 1 (0) | Out = Bannaby to Yass(61), avoid Marulan to Yass(4) O/L on Marulan-Yass(5) trip; Feedback | Outage | NSW
NC_Q_YABULU | 1 (1) | Non Conformance Constraint for Yabulu Power Station | Outage | Non-Conformance
NC_T_TVPP104 | 1 (0) | Non Conformance Constraint for Tamar Valley 110 kV OCGT | Outage | Non-Conformance
NC_V_JLB01 | 1 (0) | Non Conformance Constraint for Jeeralang B - 01 Power Station | Outage | Non-Conformance
N^^Q_AR_VC_B1 | 1 (0) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
N_MBTE1_B | 1 (158) | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
N_WOODLWN1_ZERO | 1 (10) | Discretionary upper limit for Woodlawn generation of 0 MW | Outage | NSW
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | 1 (90) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
S_PLN_ISL2 | 1 (21) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
T>>T_GTSH_EXP_3D | 1 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown 220 kV line (flow North) for trip of other Hadspen to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage | Tas
T>T_GTHA_2G | 1 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L remaining Hadspen to George Town 220 kV line (flow to George Town) for trip of a Sheffield to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
T>T_PMSH_IMP_4B | 1 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_PMSH_IMP_4C | 1 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T_T_FASH_HM_OPEN_2 | 1 (0) | Out = one Farrell to Sheffield 220kV line, Hampshire link open, Farrell 220 kV bus not split, limit West Coast gen >= 90% of West Coast load | Outage | Tas
V::N_JNWG_xxx | 1 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
V>>N-JNWG_RADIAL_1 | 1 (0) | Out = Jindera to Wagga(62), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
V>>V_NIL_4A | 1 (0) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. Similar to DBUSS - Line, the DBUSS – Transformer scheme splits the Dederang 330 kV bus on trip of a Dederang transformer. | NIL | Vic
V>V_HWA34_OP1_2 | 1 (0) | Out = Hazelwood A3 or A4 500/220 kV txfmr, avoid O/L Yallourn to Rowville No. 7 or No. 8 220 kV line on trip of Hazelwood A4 or A3 500/220 kV txfmr, 3/5 parallel mode, Jeeralang A connected to HWPS B3/4 side, feedback | Outage | Vic
#BASTYAN_E | 1 (0) | TFA11.ENERGY * 1 <= 0 (Wt = 20) | Outage | Quick
#V-SA_RAMP_E_F | 1 (6) | V-SA <= MAX(86, InitialFlow - 30) (Wt=35) | Outage | Quick
NC_N_LD01 | 1 (1) | Non Conformance Constraint for Liddell LD01 Power Station | Outage | Non-Conformance
NC_Q_GSTONE3 | 1 (1) | Non Conformance Constraint for Gladstone 3 Power Station | Outage | Non-Conformance
NC_T_TUNGATIN | 1 (1) | Non Conformance Constraint for Tungatinah Power Station | Outage | Non-Conformance
S>XKHTB1+2_SETX_SETX | 1 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East 132/275kV transformer on trip of one South East 132/275kV transformer, Feedback | Outage | SA
S_PLN_ISL1 | 1 (9) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
T>>T_NIL_BL_EXP_7C | 1 (1) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_NIL_LIPM_N-2_2B | 1 (5) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
T_T_FASH_5_N-2 | 1 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Mackintosh P/S unavailable, Hampshire link open, limit Mackintosh + Tribute + Reece 1 <= 110% of West Coast load | Outage | Tas
V_APHY1_1 | 1 (31) | Out = Heywood to APD No. 1 500 kV line section & Heywood M2 500/275 kV txfmr, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
#POR03_E | 0 (0) | SPL31P.ENERGY * 1 >= 15 (Wt = 20) | Outage | Quick
CA_SPS_41B7F9D7_02 | 0 (0) | Constraint Automation, O/L 84 @LIDDELL for CTG LNPF on trip of LIDDELL-MUSBK330 83 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N>>N-CNUT_HA | 0 (0) | Out = Canberra-UpperTumut(1), avoid Upper Tumut to Lower Tumut(64) O/L on Upper Tumut to Yass(2) trip; Feedback | Outage | NSW
NC_N_MP1 | 0 (2) | Non Conformance Constraint for Mt Piper 1 Power Station | Outage | Non-Conformance
NC_Q_CALL_B_1 | 0 (1) | Non Conformance Constraint for Callide B_1 | Outage | Non-Conformance
NC_T_TVCC201 | 0 (0) | Non Conformance Constraint for Tamar Valley 220 kV CCGT | Outage | Non-Conformance
S_HALWF2_0 | 0 (0) | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
T>>T_GTHA_EXP_3G | 0 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L remaining Hadspen to George Town 220 kV line (flow to George Town) for trip of a Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>>T_NIL_BL_EXP_3F | 0 (0) | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T>T_CSNN_1 | 0 (0) | Out = Chapel St to New Norfolk 110 kV line, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Creek Rd to New Norfolk 110kV line, feedback | Outage | Tas
T_LIPM_PMWA_1_N-3 | 0 (19) | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to <= southern load + 15 MW | Outage | Tas
V>>S_KHKN_SETB_SGKH | 0 (30) | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line | Outage | SA
CA_MQS_416718EE_01 | 0 (0) | Constraint Automation, O/L KEISNG_1 @SNUGGY for CTG TSIA on trip of S_EAST 2 275/132KV TX. Generated by STNET[MANBL] Host MANEEMP2(MQ) | Outage | Constraint Automation
CA_SPS_3FF8E592_04 | 0 (0) | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
CA_SPS_41B7F9D7_01 | 0 (0) | Constraint Automation, O/L 83 @LIDDELL for CTG LNPA on trip of TAMWORTH-LIDDELL 84 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N::Q_RGSW_KC | 0 (0) | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
N>N-CHKK_TE_1 | 0 (0) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
NC_Q_DDPS1 | 0 (1) | Non Conformance Constraint for Darling Downs Power Station | Outage | Non-Conformance
NC_Q_MPP_2 | 0 (1) | Non Conformance Constraint for Millmerran 2 Power Station | Outage | Non-Conformance
NC_S_LKBONNY2 | 0 (0) | Non conformance constraint equation for Lake Bonney 2 wind farm | Outage | Non-Conformance
NQ_450 | 0 (0) | NSW to Qld on QNI upper transfer limit of 450 MW | Outage | NSW
Q>NIL_MRTA_A | 0 (0) | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line. | NIL | Qld
SVML_010 | 0 (0) | SA to Vic on ML upper transfer limit of 10 MW | Outage | SA
T>T_GTHA_IMP_4N | 0 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_GTSH_IMP_4H | 0 (1) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_PMSH_IMP_4D | 0 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_X_HAPM110_4 | 0 (0) | Out= both Palmerston to Hadspen 110 kV lines, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) on trip of the parallel Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
T_T_JB_RC1+2_TI_250 | 0 (0) | Discretionary 250 MW upper limit on John Butters, Reece 1+2 and Tribute | Outage | Tas
T_V_FCSPS_RAMP | 0 (1) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
V>>N-DDWO_RADIAL_2 | 0 (0) | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V>>SML_BAML2_1 | 0 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line (complete line or line sections), prevent overload of the Moorabool to Ballarat No. 1 220 kV line for trip of the Moorabool to Terang 220 kV line, feedback | Outage | Vic
V>V_NIL_HW3-BUS1_3 | 0 (0) | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus | NIL | Vic
V^^S_CGMB_SECP_MAXG2 | 0 (0) | Out = Cherry Gardens - Mt Barker 132kV line and South East 275 kV capacitor O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
V_HYML1_3 | 0 (1) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
#T-V-MNSP1_RAMP_E_F | 0 (0) | T-V-MNSP1 <= MAX(160, InitialFlow - 200) (Wt=35) | Outage | Quick
CA_SPS_3FF8E592_06 | 0 (0) | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCC on trip of ROTS-YPS8 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
CA_SPS_3FF8E592_08 | 0 (0) | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N>>N-NIL__3_OPENED & CLOSED | 0 (0) | Out= NIL, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
N>N-LS_TX_TE_B | 0 (0) | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. DS only | Outage | NSW
NC_N_ER03 | 0 (0) | Non Conformance Constraint for Eraring ER03 Power Station | Outage | Non-Conformance
NC_Q_CALL_B_2 | 0 (1) | Non Conformance Constraint for Callide B_2 | Outage | Non-Conformance
NC_Q_KAREEYA4 | 0 (0) | Non Conformance Constraint for Kareeya 4 Power Station | Outage | Non-Conformance
NC_Q_MSTUART2 | 0 (0) | Non Conformance Constraint for Mt Stuart 2 Power Station | Outage | Non-Conformance
NC_Q_OAKEY2 | 0 (0) | Non Conformance Constraint for Oakey 2 Power Station | Outage | Non-Conformance
NC_Q_STAN-1 | 0 (1) | Non Conformance Constraint for Stanwell STAN-1 Power Station | Outage | Non-Conformance
NC_T_REECE1 | 0 (1) | Non Conformance Constraint for Reece 1 Power Station | Outage | Non-Conformance
NC_V_JLA04 | 0 (1) | Non Conformance Constraint for Jeeralang A - 04 Power Station | Outage | Non-Conformance
N_MBTE1_A | 0 (0) | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
Q_N_NIL-1078 | 0 (33) | Out = Nil, reduce QNI when it is over the 1078 MW limit by 1078 minus the MW over the 1078 MW limit (capped at 1000 MW) This constraint equation only operates when the NSW1-QLD1 interconnector flow is greater than 1103 MW from Queensland to NSW. It ensures that the interconnector flow does not excessively exceed the 1078 MW limit as a thermal overload limit exists at 1105 MW. | NIL | Qld
S_PLN_ISL31 | 0 (8) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
T>>T_GTSH_EXP_3A | 0 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow North) for trip of other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage | Tas
T>T_NIL_BL_IMP_7CC | 0 (5) | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
T>T_PM_TX_1A | 0 (0) | Out= Palmerston 220/110kV transformer, prevent overload of either Palmerston to Hadspen 110kV line (flow to North) for trip of the parallel Palmerston to Hadspen 110 kV line, feedback | Outage | Tas
V::S_NIL_TBSE | 0 (0) | Out = Nil; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available) with NPS and Playford assumed to be OOS. | NIL | SA
V>>V_HWPS-RO_3-5_4 | 0 (0) | Out = Hazelwood to Rowville No.1 or No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, void O/L Hazelwood #1 or #2 500/220kV transformer for loss of either transformer | Outage | Vic
V>SMLHORC1 | 0 (0) | Out = Horsham to Red Cliffs 220kV line, avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line | Outage | Vic
V>S_NIL_NIL_HYTX2 | 0 (30) | Out = NIL, avoid O/L Heywood M2 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL | Vic
@NSA_V_BDL_65 | 0 (0) | Eff = 10/05/2013 ; RHS = 65 ; Op = ">=" ; Wt = 20 | Outage | Ad-Hoc
N>>N-NIL__2_15M | 0 (0) | Out= NIL, avoid O/L Liddell to Tamworth (84) on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
N>N-NIL_TE_E2 | 0 (0) | Out= Nil, avoid Koolkhan to Lismore (967) O/L on CoffsHarbour - Lismore (89) trip; Feedback, TG formulation in PD/ST | NIL | NSW
NC_N_BW02 | 0 (1) | Non Conformance Constraint for Bayswater 2 Power Station | Outage | Non-Conformance
NC_S_DRYCGT3 | 0 (0) | Non Conformance Constraint for Dry Creek 3 Power Station | Outage | Non-Conformance
NC_S_LKBONNY3 | 0 (0) | Non Conformance Constraint for Lake Bonney 3 Windfarm | Outage | Non-Conformance
NC_S_NPS1 | 0 (0) | Non Conformance Constraint for Northern NPS1 Power Station | Outage | Non-Conformance
N^^Q_LS_VC_B1 | 0 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
Q>>NIL_MRTX5_MRTX4 | 0 (2) | Out = Nil, avoid overloading Middle Ridge No.4 330/275 kV transformer on trip of Middle Ridge No.5 330/275 kV transformer | NIL | Qld
S>>V_NIL_RBTXW_RBTX2 | 0 (0) | Out=Nil: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformer #2 on trip Robertstown transformer #1, Feedback | NIL | SA
S>NIL_HUWT_STBG | 0 (7) | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line. | NIL | SA
S>S_PAPG_PPLF_PGPS | 0 (0) | Out= Para to Parafield Gardens West 275kV line, avoid O/L Parafield Gardens West-Parafield Gardens 66kV #1 line on trip of Pelican Point-Lefevre 275kV line, Feedback | Outage | SA
T::T_NIL_5 | 0 (0) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
T>T_HAPM_IMP_4K | 0 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow North) for trip of Hadspen to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
TV_400 | 0 (0) | Tas to Vic on Basslink upper limit of 400 MW | Outage | Tas
T_X_GTSH_2 | 0 (0) | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation => West Coast + North West load - 10MW, limiting PM-SH line flow to 10 MW | Outage | Tas
V::S_MOTB_MAXG_2 | 0 (0) | Out= Mobilong - Tailem Bend 132kV line; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
V>>S_KHTB2_SETB_KHTB | 0 (0) | Out = Keith - Tailem Bend #2 132 kV line. Prevent Keith - Tailem Bend #1 line OL on trip one of the South East - Tailem Bend lines. | Outage | SA
V>>V_ROTS_TX_2_P | 0 (0) | Out = Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, 3/5 parallel mode, feedback | Outage | Vic
V^^S_KHKN_MAXG | 0 (6) | Out= Keith - Kincraig 132 kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
#GUNNING1_E | 0 (0) | NYS12A.ENERGY * 1 = 0 (Wt = 360) | Outage | Quick
CA_SPS_41B92B29_01 | 0 (0) | Constraint Automation, O/L 83 @LIDDELL for CTG LNPA on trip of TAMWORTH-LIDDELL 84 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
N>>N-NIL_996_IN | 0 (0) | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL | NSW
N>>V-NIL_N | 0 (0) | Out= Nil, avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines trips; Feedback | NIL | NSW
NC_N_BW01 | 0 (1) | Non Conformance Constraint for Bayswater 1 Power Station | Outage | Non-Conformance
NC_N_CG2 | 0 (0) | Non Conformance Constraint for Colongra 2 Power Station | Outage | Non-Conformance
NC_N_ER04 | 0 (2) | Non Conformance Constraint for Eraring ER04 Power Station | Outage | Non-Conformance
NC_N_URANQ11 | 0 (0) | Non Conformance Constraint for Uranquinty 1 Power Station | Outage | Non-Conformance
NC_N_URANQ13 | 0 (0) | Non Conformance Constraint for Uranquinty 3 Power Station | Outage | Non-Conformance
NC_Q_MSTUART3 | 0 (0) | Non Conformance Constraint for Mt Stuart 3 Power Station | Outage | Non-Conformance
NC_Q_OAKEY1 | 0 (0) | Non Conformance Constraint for Oakey 1 Power Station | Outage | Non-Conformance
NC_Q_W/HOE#2 | 0 (0) | Non Conformance Constraint for Wivenhoe No 2 Power Station | Outage | Non-Conformance
NC_S_NPS2 | 0 (2) | Non Conformance Constraint for Northern NPS2 Power Station | Outage | Non-Conformance
NC_S_PPCCGT | 0 (0) | Non Conformance Constraint for Pelican Point Power Station | Outage | Non-Conformance
NC_S_SNOWSTH1 | 0 (0) | Non Conformance Constraint for SNOWTWN STH WF U1-42 | Outage | Non-Conformance
NC_S_TORRB3 | 0 (0) | Non Conformance Constraint for Torrens B3 Power Station | Outage | Non-Conformance
NC_T_BBTHREE3 | 0 (0) | Non Conformance Constraint for Bell Bay Three Unit 3 Power Station | Outage | Non-Conformance
NC_T_GORDON | 0 (1) | Non Conformance Constraint for Gordon Power Station | Outage | Non-Conformance
NC_T_JBUTTERS | 0 (1) | Non Conformance Constraint for John Butters Power Station | Outage | Non-Conformance
NC_V_JLA01 | 0 (0) | Non Conformance Constraint for Jeeralang A - 01 Power Station | Outage | Non-Conformance
NC_V_MCKAY1 | 0 (0) | Non Conformance Constraint for McKay Creek & Bogong Power Stations (aggregated unit) | Outage | Non-Conformance
NC_V_VPGS | 0 (0) | Non Conformance Constraint for Valley Power Power Station | Outage | Non-Conformance
N^^V_DDMB_1 | 0 (2) | Out = Dederang to Mt Beauty 220 kV line, avoid voltage collapse for trip of the largest Vic generating unit or Basslink | Outage | NSW
N^^V_LTMS | 0 (0) | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse for trip of the largest Vic generating unit or Basslink | Outage | NSW
Q>CLWU_CLST | 0 (0) | Constraint Automation, O/L 275KV_855 @H24_CALV for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage | Constraint Automation - RT
S>>V_NIL_TBSE_KHSG | 0 (0) | Out= Nil, avoid O/L Keith - Snuggery 132 kV on trip of Tailem Bend - South East 275kV line, Feedback | NIL | SA
S>>X_TBTU+CB_TBCG_2 | 0 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Snuggery - Keith 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage | SA
S>SE132BUS_SETX_SGKH | 0 (0) | Out= one South East 132 kV bus (W or E bus), avoid O/L Snuggery to Keith 132 kV line on trip of South East 275/132 transformer connected to the in service 132 kV bus | Outage | SA
SV_250 | 0 (0) | SA to Victoria on Heywood upper transfer limit of 250 MW | Outage | SA
T>>T_HAPM_EXP_3A | 0 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_GTSH_2A | 0 (2) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow North) for trip of other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
T>T_HAPM_110_IMP_4D | 0 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L a Palmerston to Hadspen No. 2 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 1 220kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_110_IMP_4P | 0 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L of Palmerston to Hadspen No. 3 110 kV line (flow to North) for trip of the Palmerston 220/110 kV transformer with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_IMP_4B | 0 (0) | Out = Hadspen to Palmerston No. 2 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of either Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_HAPM_IMP_4H | 0 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_NIL_BL_110_25 | 0 (0) | Out = Nil, avoid pre-contingent O/L of Lake Echo No. 1 Tee line, feedback. | NIL | Tas
T>T_NIL_BL_IMP_7C | 0 (64) | Out = Nil, avoid overloading Farrell to Sheffield No.1 220 kV line for trip of the Farrell to Sheffield No.2 220 kV line with no SPS action | NIL | Tas
V>>N-CNUT_HB_15M | 0 (0) | Out = Canberra-UpperTumut(1), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
V>>N-MSUT_2 | 0 (0) | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage | Vic
V>>S_KHKN_NIL_SGKH | 0 (0) | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip. | NIL | SA
V>>V_NIL_4C | 0 (0) | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL | Vic
V>V_NIL_HW3-BUS1_2 | 0 (0) | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 220kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus | NIL | Vic
V>V_NIL_HW3-BUS1_4 | 0 (0) | Outage = Nil, limit Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 220kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus | NIL | Vic
V^^S_NIL_MAXG-10MW | 0 (0) | System normal limit -10 MW offset; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. (South East Capacitor Available) | NIL | SA
V^^S_TBCP_SETB | 0 (0) | Out= Tailem Bend 275kV Cap Bank (Tungkillo 275kV Cap available); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line (Note: with NPS and Playford PS assumed to be O/S) (Swamp out if SA demand less/equal to 3200MW) | Outage | SA
V_APHY1_2_1 | 0 (0) | Out = Heywood to APD No. 1 500 kV line section only, both Heywood 500/275 kV txfmrs in service, limit voltage unbalance at the APD 500 kV bus | Outage | Vic
V_HWPS_BUS2 | 0 (0) | Hazelwood PS Unit 5 upper limit set to zero due to outage of Hazelwood No 2 220 kV Bus | Outage | Vic

## Binding FCAS 2013
Constraint Equation ID | 2013 Hours (2012 Hours) | Description | Type
F_I+NIL_MG_R5 | 7,086 (7,498) | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL
F_I+NIL_MG_R6 | 6,285 (6,375) | NEM raise 6 second requirement for a NEM generation event | NIL
F_I+NIL_MG_R60 | 6,256 (6,280) | NEM raise 60 second requirement for a NEM generation event | NIL
F_I+ML_L5_0400 | 5,982 (5,999) | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL
F_I+NIL_DYN_LREG | 5,354 (6,618) | NEM lower regulation requirement | NIL
F_T++NIL_TL_L60 | 5,130 (4,007) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_T++NIL_TL_L6 | 4,629 (3,470) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_I+ML_L6_0400 | 3,416 (1,962) | NEM lower 6 second requirement for a NEM load event | NIL
F_MAIN++NIL_MG_R60 | 2,424 (2,655) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_I+APHY_L5 | 1,949 (1,494) | Out = Alcoa Portland to Heywood 500 kV line, NEM lower 5 minute requirement for the loss of the other Alcoa Portland to Heywood 500 kV line | Outage
F_I+NIL_DYN_RREG | 1,880 (1,615) | NEM raise regulation requirement | NIL
F_I+ML_L60_0400 | 1,610 (934) | NEM lower 60 second requirement for a NEM load event | NIL
F_MAIN++NIL_MG_R6 | 1,548 (2,256) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_MAIN++NIL_MG_R5 | 1,466 (1,729) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
F_T++NIL_TL_L5 | 1,439 (610) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
F_I+APHY_L60 | 1,039 (718) | Out = Heywood to Alcoa Portland 500 kV line, lower 60 second requirement | Outage
F_T++LREG_0050 | 926 (636) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_MAIN++ML_L5_0400 | 837 (1,693) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_T+NIL_TL_L60 | 760 (688) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_T+NIL_TL_L6 | 760 (699) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_MAIN+NIL_MG_R6 | 729 (700) | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R5 | 729 (700) | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_MAIN+NIL_MG_R60 | 729 (700) | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL
F_T+NIL_TL_L5 | 691 (503) | Out=Nil, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL
F_T+LREG_0050 | 623 (520) | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN++ML_L60_0400 | 591 (280) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_T++NIL_MG_R6 | 570 (434) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_MAIN++ML_L6_0400 | 535 (1,301) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
F_MAIN+ML_L6_0400 | 367 (343) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++APHY_L5 | 354 (511) | Out = Alcoa Portland to Heywood 500 kV line, Mainland lower 5 minute requirement for the loss of the remaining Alcoa Portland to Heywood 500 kV line, Basslink able to transfer FCAS | Outage
F_I+MPP_TG_R5_N-2 | 345 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Global Raise 5 Min requirement | Outage
F_T+RREG_0050 | 344 (365) | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL
F_MAIN++MPP_TGR60N-2 | 330 (0) | Out = Nil, loss of all Millmerran units declared credible as a generation event, Mainland raise 60 second requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_MG_R60 | 327 (371) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_I+ML_L5_APD | 326 (369) | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage
F_T++RREG_0050 | 319 (995) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
F_T+NIL_MG_R6 | 311 (337) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R60 | 310 (336) | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_MG_R5 | 305 (252) | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL
F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | 292 (1,648) | Tasmania raise 6 second requirement for loss of Basslink, FCSPS available In November 2011 the 4 constraint equations were replaced with 2 constraint equations due to advice that the loss of link time on Basslink was changed to 400ms. The binding results from all the constraint equations have been combined. | NIL
F_MAIN+ML_L5_0400 | 289 (288) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++APHY_L60 | 274 (206) | Out = Heywood to Alcoa Portland 500 kV line, lower 60 second requirement for the loss of the remaining Alcoa Portland to Heywood 500 kV line, Basslink able to transfer FCAS | Outage
F_MAIN+ML_L60_0400 | 271 (259) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL
F_MAIN++MPP_TGR6_N-2 | 243 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_MG_R5 | 231 (68) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
F_I+MPP_TG_R6_N-2 | 224 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Global Raise 6 sec requirement | Outage
F_I+MPP_TG_R60_N-2 | 218 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Global Raise 60 sec requirement | Outage
F_T+NIL_BL_R60_1 & F_T++NIL_BL_R60_x | 205 (1,387) | Tasmania raise 60 second requirement for loss of Basslink, FCSPS available See note for F_T+NIL_BL_R6_1 & F_T++NIL_BL_R6_x | NIL
F_MAIN++MPP_TGR5_N-2 | 162 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
F_T+NIL_BL_R5 | 161 (1,042) | Tasmania raise 5 minute requirement for loss of Basslink, FCSPS available | NIL
F_I+ML_L6_APD | 153 (201) | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage
F_MAIN+NIL_DYN_RREG | 109 (83) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL
F_S++HYSE_L60 | 105 (231) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
F_MAIN+APHY_L5 | 89 (75) | Out=Heywood to Alcoa Portland 500kV line, Lower 5 min Service Requirement for the loss of the remaining 500kV line, Basslink unable to transfer FCAS | Outage
F_MAIN+APHY_L60 | 88 (68) | Out=Heywood to Alcoa Portland 500kV line, Lower 60 sec Service Requirement for the loss of the remaining 500kV line, Basslink unable to transfer FCAS | Outage
F_I+ML_L60_APD | 83 (144) | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage
F_MAIN++ML_L5_APD | 73 (66) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_MAIN+NIL_DYN_LREG | 67 (155) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL
F_S_NPS1_R6_ZERO | 58 (0) | Out= NIL, Northern PS 1 R6 Requirement <= 0MW | Outage
F_MAIN++NIL_BL_L60 | 54 (1,267) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
F_S_NPS1_RREG_ZERO | 50 (0) | Out= NIL, Northern PS 1 RREG Requirement <= 0MW | Outage
F_MAIN++ML_L60_APD | 48 (52) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_MAIN++NIL_DYN_RREG | 46 (38) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL
F_T++CSGO_TG_R60 | 43 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
F_MAIN+MPP_TG_R5_N-2 | 42 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 5 Min requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+MPP_TG_R6_N-2 | 42 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage
F_MAIN+MPP_TG_R60N-2 | 42 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage
F_T++CSGO_TG_R6 | 40 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
F_T+NIL_WN_TG_R5 | 37 (15) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WN_TG_R6 | 34 (15) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WN_TG_R60 | 33 (15) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS | NIL
F_Q++ARTW_R6 | 26 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage
F_S++HYSE_L6 | 25 (95) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 6 second requirement | Outage
F_S++HYSE_L5 | 25 (88) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage
F_ESTN++HYTR_L60 | 24 (9) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_T+NIL_WF_TG_R60 | 21 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R6 | 21 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_T+NIL_WF_TG_R5 | 21 (0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL
F_S_NPS2_R6_ZERO | 21 (0) | Out= NIL, Northern PS 2 R6 Requirement <= 0MW | Outage
F_Q++ARTW_R60 | 19 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
F_S_NPS2_RREG_ZERO | 19 (0) | Out= NIL, Northern PS 2 RREG Requirement <= 0MW | Outage
F_T+FASH_N-2_RREG | 19 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage
F_V+NIL_PTH01_R60 | 16 (19) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_V+NIL_PTH01_R6 | 16 (20) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_V+NIL_PTH01_R5 | 16 (19) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_ESTN++HYTR_L5 | 15 (7) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
F_S++HYML_L60 | 15 (76) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 60 second requirement | Outage
F_V+NIL_PTH01_L5 | 15 (19) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_PTH02_R5 | 14 (16) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_PTH02_R6 | 14 (16) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_T+BL_CO_N-2_L6 | 14 (0) | Out= Nil, Tasmania Lower 6 second Requirement for loss of Basslink and a Comalco potline declared credible | Outage
F_V+NIL_PTH02_R60 | 14 (16) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_T+BL_CO_N-2_L60 | 13 (0) | Out= Nil, Tasmania Lower 60 second Requirement for loss of Basslink and a Comalco potline declared credible | Outage
F_I+TL_L5_0500 | 13 (1) | Lower 5 min Service Requirement for a NEM Network Event, TL = 500 | Outage
F_Q++ARDM_L6 | 13 (3) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage
F_V+NIL_APD01_R5 | 12 (10) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_APD01_R6 | 12 (10) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_Q++ARDM_L60 | 12 (3) | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 60 sec Requirement | Outage
F_V+NIL_APD01_R60 | 12 (10) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_ESTN++MLSY_L60 | 12 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 60 sec Requirement | Outage
F_V+NIL_PTH02_L5 | 12 (15) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_T++NIL_WN_TG_R6 | 11 (37) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL
F_Q++LDTW_R6 | 11 (4) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
F_V+NIL_APD01_L5 | 11 (10) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_T++FASH_N-2_TG_R5 | 11 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_Q++ARTW_L6 | 10 (58) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage
F_Q++LDTW_L6 | 10 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
F_Q++ARTW_L60 | 10 (57) | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage
F_T_GORDON_R6 | 9 (0) | Out= NIL, Gordon R6 Requirement <= 0MW | Outage
F_ESTN++MLSY_L5 | 9 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 5 min Requirement | Outage
F_Q++LDTW_L60 | 9 (0) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
F_I+TL_L5_0450 | 9 (1) | Lower 5 min Service Requirement for a NEM Network Event, TL = 450 | Outage
F_Q++LDTW_R60 | 9 (2) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage
F_T++FARE_N-2_TG_R60 | 8 (1) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
F_V+NIL_APD02_R5 | 7 (5) | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_APD02_R60 | 7 (5) | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_Q++ARTW_L5 | 7 (55) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage
F_V+NIL_APD02_R6 | 7 (5) | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_I+TL_L60_0500 | 6 (0) | Lower 60 sec Service Requirement for a NEM Network Event, TL = 500 | Outage
F_T++NIL_WF_TG_R5 | 6 (0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
F_T_REECE2_DS_R6 | 6 (1) | Determine upper limit for R6 FCAS enablement for Reece 2 based on FCAS Boost Mode status point for unit | NIL
F_Q++LDTW_L5 | 6 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
F_T++FASH_N-2_TG_R60 | 6 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_V+NIL_PTH03_R5 | 6 (10) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 5 Min service | NIL
F_V+NIL_PTH03_R6 | 5 (10) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 6 sec service | NIL
F_V+NIL_PTH03_R60 | 5 (10) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 60 sec service | NIL
F_Q++ARDM_L5 | 5 (2) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage
F_T++NIL_WF_TG_R6 | 5 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
F_T++NIL_WF_TG_R60 | 5 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
F_V+NIL_PTH03_L5 | 5 (10) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_V+NIL_APD02_L5 | 5 (5) | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 5 Min service | NIL
F_T++FASH_N-2_TG_R6 | 5 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T++FASH1_2C_TG_R5 | 5 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_S++HYML_L6 | 5 (43) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 6 second requirement | Outage
F_MAIN++ML_L6_APD | 5 (25) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
F_ESTN++HYTR_L6 | 5 (0) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
F_MAIN++NIL_DYN_LREG | 4 (133) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL
F_MAIN++NIL_BL_R60 | 4 (0) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
F_V+NIL_PTH02_L6 | 4 (5) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_T++FARE_N-2_TG_R6 | 4 (1) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
F_T++FARE_N-2_TG_R5 | 4 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS | Outage
F_V+NIL_PTH01_L60 | 4 (8) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_V+NIL_PTH01_L6 | 4 (7) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_Q++ARTW_R5 | 4 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
F_V+NIL_APD01_L6 | 4 (3) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_T++COGT_TL_L60 | 4 (7) | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
F_T++COGT_TL_L6 | 4 (2) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
F_ESTN++MLSY_L6 | 3 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 6 sec Requirement | Outage
F_V+NIL_PTH02_L60 | 3 (8) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_ESTN++HYMO_L60 | 3 (70) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
F_V+NIL_APD01_L60 | 3 (2) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_I+TL_L60_0450 | 3 (0) | Lower 60 sec Service Requirement for a NEM Network Event, TL = 450 | Outage
F_QNV++HYMO_L60 | 3 (10) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_I+DD_N-2_MG_R60 | 2 (0) | Out= Nil, loss of all Darling Downs units declared credible, Global Raise 60 sec requirement | Outage
F_Q++LDMU_R6 | 2 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
F_I+DD_N-2_MG_R6 | 2 (0) | Out= Nil, loss of all Darling Downs units declared credible, Global Raise 6 sec requirement | Outage
F_I+DD_N-2_MG_R5 | 2 (0) | Out= Nil, loss of all Darling Downs units declared credible, Global Raise 5 Min requirement | Outage
F_T_GORDON_R5 | 2 (0) | Out= NIL, Gordon R5 Requirement <= 0MW | Outage
F_S++HYML_L5 | 2 (42) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 5 minute requirement | Outage
F_MAIN+ML_L6_APD | 2 (26) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_MAIN+ML_L60_APD | 2 (26) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_MAIN+ML_L5_APD | 2 (26) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage
F_QNV++HYTR_L60 | 2 (0) | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_Q++LDMU_R60 | 2 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement | Outage
F_T++NIL_WN_TG_R60 | 2 (33) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL
F_T+BL_650_R5 | 2 (9) | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 650 ms | Outage
F_MAIN++TL_L5_0500 | 2 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage
F_STHN++ARTW_L60 | 1 (0) | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage
F_NVS++ARTW_L60 | 1 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T+BL_650_R6_1 | 1 (27) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage
F_V+NIL_PTH03_L6 | 1 (4) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_Q++MUTW_R6 | 1 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
F_Q_MK_33BUS_R5 | 1 (0) | Out=T38 Mackay 33kV C Bus (R5 Requirement) | Outage
F_T++NIL_BLSPS_L6_2 | 1 (1) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T++NIL_BLSPS_L5 | 1 (1) | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
F_T_REECE2_R6 | 1 (0) | Out= NIL, Reece 2 R6 Requirement <= 0MW | Outage
F_T+CSGO_TG_R5 | 1 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_T++FASH1_2C_TG_R6 | 1 (0) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_T++FASH1_2C_TG_R60 | 1 (0) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
F_V+NIL_PTH03_L60 | 1 (4) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_T++BLSPS_EXP_L6_1 | 1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
F_T++BLSPS_EXP_L60_1 | 1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
F_T_FISH_R6 | 1 (0) | Out=Sheffield-Fisher 220KV line. R6 <= 0MW | Outage
F_T++NIL_BLSPS_L60_2 | 1 (1) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
F_T++BLSPS_EXP_L5 | 1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
F_QNV++MLSY_L60 | 1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_BB_TG_R6 | 1 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS | NIL
F_T+CSGO_TG_R6 | 1 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_T+CSGO_TG_R60 | 1 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage
F_ESTN++MLTR_L60 | 1 (9) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
F_Q++MUTW_R60 | 1 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage
F_Q++LDMU_R5 | 1 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage
F_T++NIL_WN_TG_R5 | 1 (6) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL
F_T_GORDON_R60 | 0 (0) | Out= NIL, Gordon R60 Requirement <= 0MW | Outage
F_MAIN++RREG_0300 | 0 (1) | Mainland Raise Regulation Requirement greater than 300 MW, Basslink able transfer FCAS | Outage
F_T++NIL_BLSPS_L60_1 | 0 (0) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
F_I+RREG_0300 | 0 (1) | NEM Raise Regulation Requirement greater than 300 MW | Outage
F_T+BL_650_R60_1 | 0 (20) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage
F_ESTN++MLTR_L5 | 0 (10) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage
F_V+NIL_APD02_L6 | 0 (0) | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 6 sec service | NIL
F_T+FASH_N-2_TG_R5 | 0 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage
F_T++CSGO_TG_R5 | 0 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
F_NVS+ARTW_L60 | 0 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
F_T++BLSPS_EXP_L6_2 | 0 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage
F_STHN++LDTW_L60 | 0 (1) | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage
F_V+NIL_APD02_L60 | 0 (0) | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 60 sec service | NIL
F_QNV++MLTR_L60 | 0 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
F_QNV++HYMO_L5 | 0 (8) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_ML_L60 | 0 (0) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL
F_T++NIL_BB_TG_R60 | 0 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS | NIL
F_T+BL_CO_N-2_L5 | 0 (0) | Out= Nil, Tasmania Lower 5 min Requirement for loss of Basslink and a Comalco potline declared credible | Outage
F_ESTN++HYMO_L5 | 0 (50) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage
F_QNV++MLSY_L5 | 0 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
F_T++NIL_BLSPS_L6_1 | 0 (0) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL

## Market Impact 2013
Constraint Equation ID | 2013 Marginal Values (2012 Marginal Values) | 2013 Hours (2012 Hours) | Description | Type | Region
T_MRWF_100 | $7,481,617 (0) | 597.1 (0) | Discretionary 100 MW upper limit on Musselroe Wind Farm This constraint equation was invoked in 2013 for the Musselroe wind farm commissioning. | Outage | Tas
T_MRWF_QLIM_xx | $2,720,517 (0) | 217.3 (0) | Out = Nil, limit Musselroe Wind Farm based on status of the DVARs, capacitor banks or synchronous condensers at Musselroe The binding results from the six constraint equations have been combined. | NIL | Tas
Q>>NIL_855_871 | $2,435,502 ($1,431,065) | 277.8 (278.6) | Out = Nil, avoid overload on Calvale to Wurdong (871) 275 kV line on trip of Calvale to Stanwell (855) 275 kV line This constraint equation has been removed following the construction of the new double circuit 275 kV lines between Calvale and Stanwell (8873 and 8874) in late 2013. | NIL | Qld
T>T_NIL_110_1 | $2,345,388 (0) | 188.5 (0) | Out = Nil, avoid overloading the Derby to Scottsdale Tee 110 kV line on no line trips This constraint equation was implemented in mid-2013 with the Musselroe Wind Farm commissioning. It binds with high output from Musselroe. | NIL | Tas
NSA_Q_BARCALDN | $1,856,454 ($1,436,430) | 29.5 (17.7) | Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine for the outage of Clermont to Lilyvale (7153) 132 kV line This constraint equation is used for planned outages of the Clermont to Lilyvale (7153) or Barcaldine to Clermont (7154) 132 kV lines | Outage | Qld
NSA_S_PORxxx | $1,796,463 ($0) | 19.4 (0.1) | Network Support Agreement for Port Lincoln Units 1 and 2 | Outage | SA
NSA_Q_GSTONE34_xxx | $1,759,776 ($11,981,412) | 283.7 (366.3) | Gladstone 3 + 4 >= various levels for Network Support Agreement The binding results from three constraint equations that set the minimum level of Gladstone 3 and 4 generation have been combined. | Outage | Qld
Q>NIL_TR_TX1_4 | $1,479,171 ($312,478) | 120.7 (25.8) | Out = Nil, avoid overloading a Tarong 275/132 kV transformer ( No.1 or No.4) on trip of the other Tarong 275/132 kV transformer (No.1 or No.4) | NIL | Qld
T_MRWF_120 | $1,340,400 (0) | 107.8 (0) | Discretionary 120 MW upper limit on Musselroe Wind Farm This constraint equation was invoked in 2013 for the commissioning of the Musselroe wind farm. | Outage | Tas
N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | $898,361 ($73,013) | 531.3 (102.7) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator This voltage collapse limit is split into 7 constraint equations to co-optimise with each of the 6 largest generators in Queensland. Overall N^^Q_NIL_B1 (for trip of Kogan Creek) binds for the most number of intervals. | NIL | NSW
T_TAMARCCGT_GCS | $877,585 ($214,829) | 357.7 (911.3) | Limit output of Tamar Valley Power Station based on load available for shedding by Tamar Valley 220 kV generation control scheme (GCS) The Tamar Valley output is dependent on the GCS so AEMO expects that this constraint equation will bind for a high number of hours in 2014. | NIL | Tas
V>S_NIL_HYTX_HYTX | $804,155 ($3,682) | 990.8 (48.4) | Out = Nil, avoid overloading the remaining Heywood 275/500 kV transformer on trip of one Heywood 275/500 kV transformer With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
VTBL_ROC | $748,573 ($20,456) | 14.3 (22.3) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL | Vic
VSML_ZERO | $641,565 ($961) | 424.2 (30.0) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW This constraint equation is normally invoked for Murraylink out of service. | Outage | Vic
V>>SML_NIL_8 | $593,900 ($14) | 29.3 (0.3) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
V>>S_NIL_SETB_SGKH | $533,537 (0) | 652.1 (0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line This will bind for high import into SA with high levels of generation from the wind farms and gas turbines in the south east. With a revised rating provided in December 2013 AEMO expects this constraint equation to bind less in 2014. | NIL | SA
S>V_NIL_NIL_RBNW | $433,772 ($113,505) | 51.7 (69.4) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips This constraint equation normally sets the upper limit on Murraylink and AEMO expects it to continue to bind for a similar amount in 2014. | NIL | SA
N>N-NIL_LSDU | $325,000 ($115,282) | 159.6 (62.0) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line This constraint equation binds for high exports from NSW to Qld. | NIL | NSW
F_T+LREG_0050 | $323,429 ($9,899) | 622.6 (520.1) | Tasmania lower regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
N_X_MBTE_3A & N_X_MBTE_3B | $318,168 ($39,316) | 3,772.9 (503.1) | Out = all three Directlink cables | Outage | NSW
Q>>NIL_871_855 | $312,157 ($895,184) | 21.2 (99.8) | Out = Nil, avoid overload on Calvale to Stanwell (855) 275 kV line on trip of Calvale to Wurdong (871) 275 kV line | NIL | Qld
S>>V_NIL_SETX_SETX | $283,673 ($156,867) | 455.3 (444.1) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer This constraint equation binds when there is export from South Australia to Victoria and high generation from the wind farms and gas turbines in the south east of South Australia. | NIL | SA
NSA_V_BDL0xxx | $267,895 ($186,792) | 2.1 (1.3) | Bairnsdale Unit 1 or 2 >= various levels for Network Support Agreement The binding results from xx constraint equations that set the minimum level of Bairnsdale 1 or 2 generation have been combined. | Outage | Vic
V^SML_NSWRB_2 | $257,099 ($17,024) | 53.3 (11.6) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL | Vic
NRM_NSW1_VIC1 | $249,334 ($21,953) | 2.5 (1.8) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
T_MRWF_ZERO | $249,323 (0) | 20.0 (0) | Discretionary 0 MW upper limit on Musselroe Wind Farm | Outage | Tas
F_S++HYSE_L60 | $237,136 ($139,760) | 105.0 (231.4) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage | FCAS
Q>NIL_BI_FB | $205,386 ($131,585) | 492.6 (484.1) | Out = Nil, avoid overloading on Boyne Island feeder bushing on Calliope River to Boyne Island 132 kV lines, for the contingent loss of a single Calliope River to Boyne Island 132 kV line | NIL | Qld
S>>V_NIL_NOTI_x & S>NIL_NOTI_x | $192,236 ($1,522) | 68.8 (0.8) | Out = Nil, avoid overloading the Torrens Island to New Osborne No.4 66 kV line for trip of the Torrens Island to New Osborne No.3 66 kV line, Torrens Island 66 kV bus split These constraint equations manage the flows on the Torrens Island to New Osborne No.3 and No.4 66 kV lines for different configurations of the Torrens Island 66 kV bus. The different constraint equations were created in early 2013 following the splitting of the Torrens Island 66 kV bus. Their binding results have been combined. These constraint equations generally bind for high output from the Quarantine gas turbines. | NIL | SA
V>S_460 | $191,827 ($592) | 300.8 (15.0) | VIC to SA on Heywood upper transfer limit of 460 MW With the update to the V^^S_NIL_MAXG_xxx constraint equations in January 2013 this constraint equation is now more likely to bind. AEMO expects this will bind at similar levels until the Heywood upgrade in mid-2016. | NIL | Vic
F_T++NIL_TL_L6 | $179,206 ($22,050) | 4,628.3 (3,470.3) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
S>>V_NIL_RBTXW_RBTX1 | $174,474 ($158,347) | 5.7 (48.3) | Out = Nil, avoid overloading Robertstown No.1 275/132 kV transformer on trip of the Robertstown No.2 275/132 kV transformer This constraint equation normally binds when there is high generation from Northern, Hallett GT and the wind farms connected to the 275 kV between Robertstown and Davenport. | NIL | SA
V>>S_NIL_PWKN_SGKH | $161,160 (0) | 40.9 (0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL | SA
T>>T_NIL_BL_EXP_5F | $141,737 ($772) | 43.0 (0.9) | Out = Nil, avoid overloading a Hadspen to George Town 220 kV line for trip of the other Hadspen to George Town 220 kV line considering NCSPS action | NIL | Tas
F_T+NIL_TL_L6 | $122,298 ($22,022) | 759.9 (698.5) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
V_HWMW | $117,900 (0) | 0.8 (0) | Out = Hazelwood PS to Morwell PS 220 kV line, Limit Morwell Units 4 & 5 upper limit set to zero | Outage | Vic
V_HYML1_4 | $117,900 ($62,545) | 0.8 (0.5) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
F_S++HYML_L60 | $117,500 ($149,015) | 14.7 (75.7) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 60 second requirement | Outage | FCAS
V_HYMO2_1 | $106,548 ($56,365) | 1.5 (2.8) | Out = Heywood to Mortlake No.2 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
F_S++HYSE_L6 | $105,639 ($394) | 25.2 (95.3) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 6 second requirement | Outage | FCAS
S_LB3_0 | $104,857 ($244,861) | 155.8 (83.5) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW | Outage | SA
F_T++LREG_0050 | $102,409 ($9,266) | 926.3 (635.8) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
S_PF_4_UNITS | $96,375 ($179,452) | 7.8 (14.6) | Out = 4 Playford generators, upper limit on Playford generation of 0MW | Outage | SA
V>>SML_NIL_1 | $89,828 ($92,355) | 13.1 (3.3) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL | Vic
F_T+NIL_MG_R6 | $85,664 ($54,620) | 310.6 (336.5) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink unable to transfer FCAS | NIL | FCAS
F_I+NIL_MG_R5 | $79,125 ($122,115) | 7,085.5 (7,498.1) | NEM raise 5 minute requirement for a NEM generation event The largest unit is usually Kogan Creek or one of the large NSW units. | NIL | FCAS
T_MRWF_UPLIM | $71,858 (0) | 5.8 (0) | Limit Musselroe generation to current MW + 10 | Outage | Tas
V>V_NIL_GGMS_1 | $71,167 (0) | 35.4 (0) | Out = Nil, avoid overloading Guthega to Murray (97G/3) 132 kV line | NIL | Vic
T>T_HAGT_N-2 | $69,112 (0) | 13.3 (0) | Out=NIL, Loss of both Hadspen to George Town 220kV lines or Palmerston to Hadspen 220kV lines declared credible, Restrict the power flow on HA-GT corridor based on AETV CCGT service status | Outage | Tas
N>N-EWMB_TE_A | $68,882 ($43,648) | 19.2 (40.4) | Out = Ballina to Lennox Head 66 kV line, avoid overloading Lismore to Dunoon 132 kV line on trip of the other Lismore to Dunoon 132 kV line | Outage | NSW
VSML_220 | $65,147 ($1,582) | 67.9 (5.1) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL | Vic
N>>V-NIL_O | $63,883 ($66) | 1.3 (0.3) | Out = Nil, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line and subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | NIL | NSW
N>>V_DBUSS_1 | $63,745 (0) | 35.5 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line DBUSS - line is a control scheme that splits Dederang 330 kV bus on trip of a Murray to Dederang line. This was implemented to allows higher NSW to Vic interconnector capability. For a number of outages in southern NSW and northern Victoria either the line or transformer control schemes are also taken out of service. | Outage | NSW
V_HYML1_5 | $61,012 (0) | 2.9 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No. 1 500 kV line, limit voltage unbalance at the APD 500 kV bus, two Mortlake units in service | Outage | Vic
F_I+NIL_MG_R6 | $60,255 ($75,971) | 6,284.6 (6,374.9) | NEM raise 6 second requirement for a NEM generation event | NIL | FCAS
CA_SPS_40D62A5B_01 | $58,944 (0) | 4.8 (0) | During the outage of Hazelwood A2 500/220kV transformer with the Victorian network configured in 3/5 Parallel at Hazelwood four Yallourn units tripped. RTCA (Real Time Contingency Analysis) indicated that trip of Hazelwood to Yallourn No.1 or No.2 would cause overload on the remaining line. Constraint Automation was used to manage this issue. | Outage | Constraint Automation
N^Q_NIL_A | $58,192 ($1) | 32.8 (0.1) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL | NSW
NQTE_ROC | $57,465 ($44,818) | 16.7 (25.0) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL | NSW
T>T_NIL_BL_110_18_1 | $56,544 ($4,829) | 40.5 (10.2) | Out = Nil, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Tungatinah to Waddamana No.2 110 kV line, feedback | NIL | Tas
T>T_NIL_NCSPS5_1B | $56,422 (0) | 26.7 (0) | Out = Nil, avoid overloading the line terminal equipment of either Gordon to Chapel St 220kV line for trip of the other Gordon to Chapel St line | NIL | Tas
S^NIL_PL_MAX | $56,109 ($21,755) | 3.5 (1.8) | Out = Nil, Maximum generation at Port Lincoln Due to voltage stability limit. | NIL | SA
N_X_MBTE2_A & N_X_MBTE2_B | $55,736 ($84,205) | 196.1 (482.8) | Out = two Directlink cables | Outage | NSW
NRM_VIC1_SA1 | $52,366 (0) | 2.1 (0) | Negative Residue Management constraint for VIC to SA flow | NIL | Negative Residue
T>T_SHGT_N-2 | $52,097 (0) | 5.5 (0) | Out=NIL, Loss of both Sheffield to George Town 220kV lines declared credible, Restrict the power flow on SH-GT corridor based on AETV CCGT service status | Outage | Tas
T>T_NIL_BL_IMP_1B | $52,006 ($21,712) | 299.3 (4.8) | Out = Nil, avoid overloading either Gordon to Chapel St 220 kV line for trip of the other Gordon to Chapel St 220 kV line with no SPS action This constraint equation binds at times of high Gordon generation when the NCSPS control scheme is unavailable. | NIL | Tas
Q>NIL_CLBCN_7350 | $50,707 ($76,271) | 4.0 (6.1) | Out = Nil, avoid overloading Chinchilla to Columboola (7350) 132 kV line on trip of Chinchilla to Columboola (7349) 132 kV line | NIL | Qld
V>S_NIL_NIL_HYTX1 | $48,300 ($15) | 3.5 (0.5) | Out = NIL, avoid O/L Heywood M1 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL | Vic
N^^V_NIL_2 | $45,018 ($1,649) | 23.7 (5.2) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL | NSW
F_S++HYSE_L5 | $43,215 ($4,289) | 24.3 (87.7) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement | Outage | FCAS
S_PLN_ISL2 | $42,585 ($1,178,809) | 0.5 (21.4) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
S>NIL_NIL_MYSG-T | $42,258 ($3,587) | 55.4 (12.8) | Out = Nil, avoid overloading Mayura to Snuggery 132 kV line on no line trips | NIL | SA
V>>V_NIL_3 | $41,437 ($36,539) | 1.3 (0.4) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL | Vic
V>>V_NIL_1B | $40,047 ($199,598) | 14.5 (7.3) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL | Vic
NRM_QLD1_NSW1 | $39,952 ($52,213) | 30.4 (19.5) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
F_S++HYML_L6 | $39,302 ($63,348) | 4.1 (42.9) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 6 second requirement | Outage | FCAS
Q_CS_1100 | $39,273 (0) | 8.8 (0) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer | Outage | Qld
Q>>BRTR_MRTX5_MRTX4 | $38,812 (0) | 1.9 (0) | Out = Braemar to Tarong (8814 or 8815) 275 kV line, avoid overloading Middle Ridge 330/275 kV No.4 transformer, on trip of Middle Ridge 330/275 kV No.5 transformer | Outage | Qld
T_MRWF_42 | $37,628 (0) | 3.0 (0) | Discretionary 42 MW upper limit on Musselroe Wind Farm | Outage | Tas
T_GO_ZERO | $37,047 (0) | 36.5 (0) | Discretionary 0 MW upper limit on total Gordon generation | Outage | Tas
V>S_NWRB2_NWRB1 | $36,257 ($12,500) | 34.2 (0.1) | Out = North West Bend to Robertstown No.2 132 kV line, avoid overloading North West Bend to Robertstown No.1 132 kV line | Outage | SA
F_T+RREG_0050 | $35,604 ($18,185) | 343.7 (365.0) | Tasmania raise regulation requirement greater than 50 MW, Basslink unable to transfer FCAS | NIL | FCAS
CA_SPS_41C52A3F_01 | $35,195 (0) | 0.7 (0) | Constraint Automation, O/L DDTS_SHTS_220 @DDTS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
V>>S_PWSE_SETB_SGKH | $34,736 (0) | 40.3 (0) | Out = Penola West to South East 132 kV line, avoid overloading Snuggery to Keith 132 kV line on trip of South East to Tailem Bend 275 kV line | Outage | SA
F_I+NIL_MG_R60 | $34,381 ($58,313) | 6,255.8 (6,279.8) | NEM raise 60 second requirement for a NEM generation event | NIL | FCAS
V>>SML_NIL_7A | $34,306 ($14,177) | 72.0 (13.6) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line This constraint equation only binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for high flows on Murraylink into SA. | NIL | Vic
V^^S_NIL_MAXG_xxx | $34,225 ($13,835) | 209.0 (239.6) | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off There are two constraint equations that make up the voltage stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
F_T++NIL_MG_R6 | $34,055 ($48,401) | 569.9 (433.8) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
V>SML_BUDP_2 | $32,746 ($48,799) | 13.3 (31.5) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage | Vic
V>V_NIL_7 | $32,115 ($12) | 2.0 (0.6) | Out = NIL, prevent overload of either MBTS-DDTS 220 kV line (flow north) for trip of the EPS-TTS 220 kV line, feedback. | NIL | Vic
S_PLN_ISL32 | $30,722 ($12,837) | 0.7 (20.1) | Out = Yadnarie to Port Lincoln 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
F_T+NIL_BL_R6_1 | $29,906 ($33,074) | 292.2 (1,640.9) | Tasmania raise 6 second requirement for loss of Basslink, FCSPS available | NIL | FCAS
S_PLN_ISL1 | $29,489 ($1,361,364) | 0.4 (9.3) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln units 1 and 2 islanded | Outage | SA
N^^V_NIL_1 | $28,564 ($13,720) | 104.0 (108.3) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL | NSW
V_MACARTHUR_210 | $28,297 ($21,052) | 2.3 (1.7) | Limit Macarthur Wind Farm to 210 MW to limit voltage unbalance at the APD 500 kV bus | Outage | Vic
F_I+NIL_DYN_LREG | $27,464 ($65,010) | 5,353.6 (6,618.3) | NEM lower regulation requirement | NIL | FCAS
Q:N_NIL_BCK2L-G | $27,148 ($38,412) | 4.3 (114.8) | Out = Nil, avoid transient instability for a 2 phase to ground fault on a Bulli Creek to Dumaresq 330 kV line at Bulli Creek For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_OSC will bind. | NIL | Qld
T>T_NIL_BL_IMP_5F | $26,971 ($3,064) | 327.1 (26.8) | Out = Nil, avoid overloading Hadspen to Georgetown No.1 220 kV line (flow to North) for trip of the Hadspen to Georgetown No.2 220 kV line with no SPS action This constraint only binds when the NCSPS control scheme is unavailable. | NIL | Tas
F_T+BL_CO_N-2_L6 | $25,789 (0) | 14.0 (0) | Out= Nil, Tasmania Lower 6 second Requirement for loss of Basslink and a Comalco potline declared credible | Outage | FCAS
T>>T_NIL_BL_EXP_6E | $25,118 ($1) | 73.3 (0.1) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL | Tas
V::S_NIL_MAXG_xxx | $24,608 ($211) | 78.7 (4.3) | Out = Nil, Vic to SA Transient Stability limit for loss of the largest generation unit in SA There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL | SA
F_Q++ARTW_R6 | $22,570 (0) | 26.0 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
V>>S_HYML_1 | $22,360 ($3,646) | 89.4 (106.9) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 1 | Outage | SA
V>>S_HYML_2 | $21,941 ($3,600) | 58.0 (57.5) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 2 | Outage | SA
V>SMLBAHO4 | $21,603 ($73,526) | 41.0 (11.9) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line | Outage | Vic
Q>NIL_CLBCN_7349 | $19,883 ($10,445) | 1.5 (0.8) | Out = Nil, avoid overloading Chinchilla to Columboola (7349) 132 kV line on trip of Chinchilla to Columboola (7350) 132 kV line | NIL | Qld
T>T_PMHA_SHGT_N-2 | $18,803 (0) | 0.6 (0) | Out= NIL, Loss of both Sheffield to Georgetown 220kV lines declared credible, avoid O/L the Palmerston to Hadspen 220 kV line for loss of both Sheffield to Georgetown 220 kV lines, Feedback | Outage | Tas
F_S++HYML_L5 | $18,667 ($41,401) | 2.3 (41.5) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 5 minute requirement | Outage | FCAS
F_T+NIL_MG_R5 | $18,540 ($4,257) | 304.9 (252.0) | Out = Nil, Raise 5 min requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
S_CMWF_0 | $18,308 ($62,486) | 8.8 (33.0) | Discretionary upper limit for Clements Gap WF generation of 0 MW | Outage | SA
F_Q++ARTW_R60 | $17,593 (0) | 19.3 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage | FCAS
T>T_NIL_BL_3C | $16,525 ($128) | 136.3 (1.0) | Out = Nil, avoid overloading a Hadspen to Palmerston 220 kV line for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action | NIL | Tas
F_MAIN++NIL_MG_R6 | $16,476 ($36,082) | 1,547.3 (2,255.6) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
V_MACARTHUR_ZERO | $16,117 (0) | 15.2 (0) | Macarthur upper limit of 0 MW | Outage | Vic
F_I+ML_L5_0400 | $16,102 ($16,369) | 5,981.2 (5,999.2) | NEM lower 5 minute requirement for a NEM load event The largest single load in the NEM is 400 MW at Boyne Island in Queensland. | NIL | FCAS
F_T++NIL_TL_L60 | $15,828 ($8,185) | 5,129.3 (4,006.9) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
S-LB2_0 | $15,574 ($3,589) | 13.9 (1.4) | Discretionary upper limit for Lake Bonney 2 generation of 0 MW | Outage | SA
F_T+NIL_MG_R60 | $15,437 ($8,735) | 309.7 (335.4) | Out = Nil, Raise 60 sec requirement for a Tasmania Generation Event (both largest MW output and inertia), Basslink unable to transfer FCAS | NIL | FCAS
T>T_GTSH_220_1_N-2 | $15,209 ($12,044) | 12.7 (11.3) | Out = Nil, loss of both Georgetown to Sheffield 220 kV lines declared credible, avoid overloading the Sheffield to Palmerston 220 kV line (flow to south) for loss of both Georgetown to Sheffield 220 kV lines | Outage | Tas
F_MAIN++NIL_MG_R60 | $15,184 ($31,946) | 2,423.9 (2,654.8) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
T>T_FASH_1_N-2 | $14,961 ($221) | 12.2 (1.6) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Hampshire link closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV lines | Outage | Tas
S_PLN_ISL31 | $14,282 ($451,567) | 0.3 (8.1) | Out = Whyalla to Yadnarie 132 kV line, Port Lincoln unit No.3 islanded | Outage | SA
V>>V_NIL_4A | $14,004 ($29) | 0.6 (0.1) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. Similar to DBUSS - Line, the DBUSS – Transformer scheme splits the Dederang 330 kV bus on trip of a Dederang transformer. | NIL | Vic
F_MAIN++NIL_MG_R5 | $13,770 ($25,597) | 1,465.7 (1,728.8) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL | FCAS
CA_SPS_3FF8E592_02 | $13,301 (0) | 0.6 (0) | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCB on trip of ROTS-YPS7 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
T_V_NIL_BL1 | $13,024 ($2,699) | 5.3 (20.8) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL | Tas
F_T++NIL_BLSPS_L6_1 | $12,900 ($1) | 0.1 (0.2) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
T^V_NIL_BL_6 | $12,858 (0) | 132.8 (0) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL | Tas
N>N-NIL__4_15M | $12,800 ($15) | 2.8 (1.2) | Out = Nil, avoid overloading Muswellbrook to Tamworth (88) 330 kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL | NSW
SV_200 | $12,116 (0) | 1.2 (0) | SA to Victoria on VicSA upper transfer limit of 200 MW | Outage | SA
T>T_TU_LE_WA12_2 | $12,080 (0) | 23.1 (0) | Out = either Tungatinah to Waddamana 110kV line (direct or via Lake Echo tee), avoid O/L the remaining Tungatinah to Waddamana 110 kV line (flow to North) for loss of the Meadowbank to New Norfolk No.2 line, feedback | Outage | Tas
F_I+NIL_DYN_RREG | $11,796 ($11,349) | 1,879.9 (1,615.5) | NEM raise regulation requirement | NIL | FCAS
F_MAIN+NIL_MG_R5 | $11,752 ($16,189) | 729.4 (699.7) | Out = Nil, Raise 5 min requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
N>LSDU9U6_LSDU9U7 | $11,683 (0) | 0.8 (0) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage | NSW
T>T_NIL_BL_IMP_5FF | $11,406 ($1,029) | 107.3 (8.0) | Out = Nil, avoid overloading Hadspen to Georgetown No.2 220 kV line for trip of the Hadspen to Georgetown No.1 220 kV line with no SPS action | NIL | Tas
S>MYTX2_MYTX1 | $11,200 ($2,494) | 17.9 (4.1) | Out = Mayura 132/33 kV transformer #2 with the 33kV bus tie isolator 44248 closed, avoid O/L Mayura 132/33 kV transformer #1, Feedback. | Outage | SA
V^^S_MTSE+PAVC_MAXG | $11,137 (0) | 3.9 (0) | Out= Mt Gambier - South East 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
Q>NIL_MRTA_B | $10,888 (0) | 0.8 (0) | Out = Nil, Oakey PS constrained to the emergency rating of 732 Middle Ridge to Tangkam 110kV line. | NIL | Qld
V^^S_TBTX4_MAXG | $9,873 (0) | 26.2 (0) | Out =Tailem Bend 275/132 kV transformer #4; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S) | Outage | SA
T>T_GT_HA_3A_N-2 | $9,658 (0) | 11.3 (0) | Out = NIL, Loss of both Hadspen to Georgetown 220kV lines declared credible, avoid O/L the Sheffield to Palmerston 220 kV line (flow to North) for loss of both Hadspen to Georgetown 220 kV lines | Outage | Tas
F_MAIN+NIL_MG_R6 | $9,508 ($14,853) | 729.4 (699.7) | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | $9,407 ($4,983) | 202.1 (164.0) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV These constraint equations maintain flow on the South Morang F2 transformer below its continuous rating. AEMO expects the combination of these three constraint equations will bind for a similar amount in 2014. | NIL | Vic
S>SE132CB_SETX_SGKH | $9,155 ($9,028) | 5.5 (22.1) | Out = South East CB6160 or CB6162, avoid overloading Snuggery to Keith 132 kV line on trip of a South East 275/132 kV transformer | Outage | SA
SVML_ZERO | $8,869 ($26,270) | 174.7 (286.0) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage | SA
VS_250 | $8,669 ($1,940) | 27.3 (38.9) | Victoria to South Australia on Heywood upper transfer limit of 250 MW This constraint equation is included in a number of constraint sets which are used for outages of the 500 kV lines in from Sydenham to Heywood and the 275 kV lines from Heywood to South East. | Outage | Vic
T_FISH | $8,360 (0) | 0.7 (0) | Out=Sheffield-Fisher 220KV line. Energy <= 0MW | Outage | Tas
S>V_NWRB2_RBNW1 | $8,215 ($6,130) | 85.6 (15.3) | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage | SA
S>>NIL_SETB_KHTB2 | $7,892 (0) | 18.8 (0) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
F_MAIN+NIL_MG_R60 | $7,845 ($12,212) | 729.4 (699.7) | Out = Nil, Raise 60 sec requirement for a Mainland Generation Event, Basslink unable transfer FCAS | NIL | FCAS
CA_SPS_3FF8E592_04 | $7,715 (0) | 0.1 (0) | Constraint Automation, O/L ROTS_YPS8_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
F_I+MPP_TG_R5_N-2 | $7,579 (0) | 345.1 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Global Raise 5 Min requirement | Outage | FCAS
T>T_NIL_LIPM_N-2_2A | $7,495 ($386) | 13.9 (5.8) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to North) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
F_T++NIL_MG_R60 | $7,469 ($2,337) | 327.4 (371.8) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
N_WOODLWN1_ZERO | $7,330 ($128,716) | 0.6 (10.3) | Discretionary upper limit for Woodlawn generation of 0 MW | Outage | NSW
T>T_NIL_BL_5C | $7,158 ($107) | 89.2 (1.5) | Out = Nil, avoid O/L a Hadspen to George Town 220 kV line (flow to George Town) for trip of the other Hadspen to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | NIL | Tas
N>>N-NIL_996_IN | $7,062 ($185) | 0.1 (0.4) | Out = Nil, avoid Wagga to ANM(996) O/L on Wagga to Jindera(62) trip; Feedback | NIL | NSW
T_ROCOF_1 | $6,919 (0) | 12.0 (0) | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL | Tas
V^^S_PAVC_MAXG | $6,881 ($1,627) | 36.2 (14.5) | Out = Para one SVC, VIC to SA Voltage Stability limit for loss of the largest generation unit in SA | Outage | SA
N_GUNNING1_ZERO | $6,736 ($15,834) | 6.3 (15.4) | Discretionary upper limit for Gunning generation of 0 MW | Outage | NSW
V>V_HWA34_OP1_2 | $6,461 (0) | 0.6 (0) | Out = Hazelwood A3 or A4 500/220 kV txfmr, avoid O/L Yallourn to Rowville No. 7 or No. 8 220 kV line on trip of Hazelwood A4 or A3 500/220 kV txfmr, 3/5 parallel mode, Jeeralang A connected to HWPS B3/4 side, feedback | Outage | Vic
F_I+APHY_L5 | $6,454 ($5,062) | 1,948.9 (1,493.8) | Out = Alcoa Portland to Heywood 500 kV line, NEM lower 5 minute requirement for the loss of the other Alcoa Portland to Heywood 500 kV line | Outage | FCAS
F_MAIN++MPP_TGR6_N-2 | $6,314 (0) | 243.4 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
F_T++RREG_0050 | $5,963 ($21,982) | 319.1 (995.3) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL | FCAS
S>>NIL_SETB_KHTB1 | $5,916 ($1,675) | 26.7 (13.5) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL | SA
N>>V-NIL_N | $5,795 (0) | 0.1 (0) | Out= Nil, avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines trips; Feedback | NIL | NSW
V>>SML_NIL_7B | $5,780 ($82) | 20.5 (2.8) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
N^N_KKLS_1 | $5,717 ($1,196) | 81.8 (18.8) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. | Outage | NSW
V>SMLBAHO1 | $5,717 ($12,820) | 6.2 (4.6) | Out = Ballarat to Horsham, or Bendigo to Kerang line, avoid overloading or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang or Ballarat to Horsham line | Outage | Vic
F_Q++LDTW_L5 | $5,472 (0) | 5.7 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
S>BGCB6246_BGPT_HUWT | $5,365 (0) | 4.8 (0) | Out= Bungama 132kV East Bus(i.e.Bungama 132kV CB6246 & CB6243 & Bungama 132/33kV No.3 TX O/S) OR Bungama CB6246 O/S, avoid O/L Hummocks-Waterloo 132kV line on trip of Bungama- Port Pirie 132kV line, feedback. | Outage | SA
T>>T_GTSH_EXP_3C | $5,330 (0) | 1.1 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage | Tas
V>V_NIL_HW3-BUS1_1 | $5,298 (0) | 0.8 (0) | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A2 transformer for trip of A1 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus | NIL | Vic
F_T++CSGO_TG_R6 | $5,289 (0) | 40.3 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage | FCAS
V>V_NIL_HW3-BUS1_3 | $5,085 (0) | 0.3 (0) | Outage = Nil, limit Yallourn unit 1 +Hazelwood +Jeeralang +Bairnsdale +Morwell to avoid O/L Hazelwood 500/220kV A1 transformer for trip of A2 transformer, Yallourn unit 1 in 500kV mode, Radial with 1,2,3,4 busses split, Hazelwood unit 3 on HWPS #1 bus | NIL | Vic
F_MAIN++MPP_TGR60N-2 | $4,846 (0) | 330.2 (0) | Out = Nil, loss of all Millmerran units declared credible as a generation event, Mainland raise 60 second requirement, Basslink able to transfer FCAS | Outage | FCAS
F_MAIN++ML_L5_0400 | $4,672 ($30,941) | 837.0 (1,693.2) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
S_LB2WF_CONF | $4,644 ($5,154) | 4.6 (5.5) | Out= Nil; Limit Lake Bonney 2 & 3 generation based on DVAR availability. | NIL | SA
NRM_VIC1_NSW1 | $4,433 ($2,203) | 1.8 (4.1) | Negative Residue Management constraint equation for VIC to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL | Negative Residue
V>>S_KNPW_SETB_SGKH | $4,294 ($72) | 8.9 (1.7) | Out= Kincraig - Penola West 132kV line, avoid O/L Snuggery - Keith 132kV on trip of one South East - Tailem Bend 275kV line, Feedback | Outage | SA
V_T_NIL_BL1 | $4,264 ($10,481) | 9.3 (53.3) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL | Vic
VT_ZERO | $4,034 ($120) | 8.1 (0.3) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage | Vic
T>>T_GTSH_EXP_3FH | $3,947 (0) | 2.8 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown and Palmerston to Sheffield 220 kV line for trip of Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overloads. | Outage | Tas
T>T_GTHA_5L | $3,944 ($2,957) | 28.8 (18.8) | Out = Hadspen to George Town 220 kV line, avoid O/L line terminal equipment of Sheffield to George Town No. 1 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 2 220 kV line, feedback | Outage | Tas
Q>NIL_MRTA_A | $3,944 (0) | 0.3 (0) | Out = Nil, Oakey PS constrained to the emergency rating of 731 Middle Ridge to Tangkam 110kV line. | NIL | Qld
F_I+ML_L6_0400 | $3,925 ($1,564) | 3,416.4 (1,961.5) | NEM lower 6 second requirement for a NEM load event | NIL | FCAS
N>N-ARGI_TE_C1 | $3,860 (0) | 5.6 (0) | Out= Armidale to Glen Innes (96T), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 Directlink cable O/S, Feedback, TG formulation in PD/ST | Outage | NSW
T>T_GTHA_IMP_4J | $3,456 (0) | 33.5 (0) | Out = Hadspen to George Town No. 1 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
V>SMLBSRC2 | $3,436 (0) | 1.2 (0) | Out = Buronga to Redcliffs (0X1) 220 kV line, avoid O/L Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line, feedback | Outage | Vic
S>>V_NIL_RBTXW_RBTX2 | $3,425 ($50,000) | 0.2 (0.3) | Out=Nil: limit SA to Vic on Murraylink and SA generation to avoid overloading Robertstown transformer #2 on trip Robertstown transformer #1, Feedback | NIL | SA
T>T_FASH_1_2_C1 | $3,334 ($778) | 11.4 (7.5) | Out=Farrell to Sheffield No.1 or 2 line, Farrell 220kV bus split, Hampshire link closed, Bastyan + Mackintosh supplying txfmrs other gens supplying 220kV line to Sheffield, limit Bastyan and Mackintosh <= Rosebery + Queenstown + 20 MW | Outage | Tas
F_T++FASH_N-2_TG_R6 | $3,276 (0) | 5.0 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
F_MAIN++MPP_TGR5_N-2 | $3,251 (0) | 161.5 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage | FCAS
V^^S_PWSE_MAXG | $3,240 ($45) | 13.8 (2.1) | Out= Penola West - South East 132 kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
T>T_GTHA_IMP_4H | $3,233 (0) | 25.3 (0) | Out = Hadspen to George Town No. 2 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
S>>V_KNPW_SETX_SETX | $3,121 ($1,087) | 7.5 (2.1) | Out = Kincraig to Penola West 132 kV line, avoid overloading the remaining South East 275/132kV transformer on trip of one South East 275/132kV transformer | Outage | SA
F_I+MPP_TG_R6_N-2 | $2,941 (0) | 223.6 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Global Raise 6 sec requirement | Outage | FCAS
S_NBH_0 | $2,880 (0) | 1.8 (0) | Discretionary upper limit for North Brown Hill generation of 0 MW | Outage | SA
F_MAIN++APHY_L5 | $2,823 ($12,100) | 353.8 (510.6) | Out = Alcoa Portland to Heywood 500 kV line, Mainland lower 5 minute requirement for the loss of the remaining Alcoa Portland to Heywood 500 kV line, Basslink able to transfer FCAS | Outage | FCAS
F_T++NIL_TL_L5 | $2,815 ($2,009) | 1,439.3 (610.0) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL | FCAS
T>T_GTSH_IMP_4D | $2,808 (0) | 14.8 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
N^^Q_MPP_N-2 | $2,763 (0) | 16.2 (0) | Out = Nil, avoid Voltage Collapse on trip of Millmerran 1 & 2 declared credible | Outage | NSW
T_FASH_MAXGEN_1 | $2,761 (0) | 7.9 (0) | Upper limit on Mackintosh + Reece 1 + Tribute with both Farrell to Sheffield 220 kV lines declared credible, Farrell 220 kV bus split, Hampshire link closed. Constraint swamped if only one machine on line | Outage | Tas
F_MAIN+ML_L5_0400 | $2,731 ($4,098) | 289.3 (288.3) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
TVBL_ROC | $2,637 ($3,105) | 13.3 (16.6) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL | Tas
N^Q_ARTW_1 | $2,589 (0) | 12.8 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage | NSW
T>T_GTHA_IMP_4K | $2,559 ($620) | 15.6 (5.6) | Out = Hadspen to George Town No. 1 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of either Sheffield to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
F_MAIN+NIL_DYN_RREG | $2,253 ($1,028) | 109.0 (82.8) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink unable transfer FCAS | NIL | FCAS
T>T_PMWA_IMP_4D | $2,191 (0) | 21.7 (0) | Out = Palmerston to Waddamana 110 kV line, avoid overloading the Palmerston to Hadspen No. 1 220 kV line on trip of the Palmerston to Hadspen No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>S_NIL_NIL_SGKHC | $2,143 ($1,705) | 7.3 (14.8) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on Nil trip, Feedback | NIL | SA
S_TBL_0 | $2,141 (0) | 1.3 (0) | Discretionary upper limit for The Bluff generation of 0 MW | Outage | SA
T_GO_250 | $2,100 (0) | 5.1 (0) | Discretionary 250 MW upper limit on total Gordon generation | Outage | Tas
T>>T_GTSH_EXP_3A | $2,004 (0) | 0.3 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow North) for trip of other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage | Tas
T>T_GTSH_IMP_4E | $1,961 ($301) | 13.2 (4.8) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
T>T_GTHA_IMP_4I | $1,920 (0) | 16.5 (0) | Out = Hadspen to George Town No. 2 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of either Sheffield to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>V-MSUT_1 | $1,906 (0) | 42.9 (0) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | Outage | Vic
N::Q_BWMP_KC | $1,872 (0) | 3.6 (0) | Out = Bayswater to Mt Piper(5A3) 500 kV line or Bayswater to Wollar(5A4) 500 kV line or Wollar to Mt. Piper (5A5) 500 kV line, NSW to Qld Transient Stability Limit for trip of Kogan Creek | Outage | NSW
T_FARC2 | $1,827 (0) | 2.9 (0) | Out=Farrell-Reece 2 220KV line. Energy <= 0MW | Outage | Tas
T_FARC1 | $1,826 (0) | 2.9 (0) | Out=Farrell-Reece 1 220KV line. Energy <= 0MW | Outage | Tas
F_MAIN+MPP_TG_R6_N-2 | $1,802 (0) | 41.9 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 6 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_T++NIL_BLSPS_L6_2 | $1,778 ($30) | 1.0 (0.8) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
F_T+NIL_TL_L5 | $1,767 ($14,717) | 690.8 (502.8) | Out=Nil, Tasmania Lower 5 min requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
V^^S_KNPW+PAVC_MAXG | $1,736 (0) | 2.8 (0) | Out= Kincraig - Penola West 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
T>T_GTSH_IMP_4A | $1,709 ($21) | 9.2 (0.3) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
S>XKHTB1+2_SETX_SETX | $1,665 (0) | 0.5 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East 132/275kV transformer on trip of one South East 132/275kV transformer, Feedback | Outage | SA
TV_315 | $1,577 (0) | 12.4 (0) | Tas to Vic on Basslink upper limit of 315 MW | Outage | Tas
T>>T_GTSH_EXP_3H | $1,538 ($283) | 4.7 (1.8) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage | Tas
T_T_FASH_HM_OPEN_2 | $1,532 (0) | 0.6 (0) | Out = one Farrell to Sheffield 220kV line, Hampshire link open, Farrell 220 kV bus not split, limit West Coast gen >= 90% of West Coast load | Outage | Tas
T>T_GTSH_IMP_4K | $1,514 ($12,631) | 10.0 (83.2) | Out = Sheffield to Georgetown 220 kV line, avoid overloading Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action | Outage | Tas
S>NIL_BWPA_HUWT | $1,512 (0) | 1.5 (0) | Out= Nil, avoid O/L Hummocks - Waterloo 132kV on trip of Blyth West - Para 275kV line, Feedback | NIL | SA
T>T_GTHA_IMP_4O | $1,511 ($132) | 16.4 (0.3) | Out = Hadspen to George Town 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Sheffield) for trip of remaining Hadspen to George Town 220 kV line with no NCSPS action, feedback | Outage | Tas
V^^S_MOTB+PAVC_MAXG | $1,508 (0) | 9.6 (0) | Out= Mobilong - Tailem Bend 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
T^V_NIL_8 | $1,492 (0) | 16.2 (0) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, swamped if TVCC in service | NIL | Tas
F_T+NIL_TL_L60 | $1,435 ($1,608) | 760.1 (688.0) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink unable to transfer FCAS | NIL | FCAS
F_T+NIL_BL_R5 | $1,421 ($11,889) | 160.6 (1,042.1) | Tasmania raise 5 minute requirement for loss of Basslink, FCSPS available | NIL | FCAS
N^^V_LTUT_2 | $1,406 (0) | 1.6 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage | NSW
F_MAIN+MPP_TG_R5_N-2 | $1,392 (0) | 41.9 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 5 Min requirement, Basslink unable to transfer FCAS | Outage | FCAS
F_I+ML_L5_APD | $1,390 ($1,207) | 326.2 (368.8) | Out = Nil, Lower 5 min requirement for a NEM Load Event, ML = APD | Outage | FCAS
S>>V_NIL_NIL_HUWT | $1,390 ($1,027) | 1.8 (2.0) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL | SA
F_I+ML_L60_0400 | $1,379 ($328) | 1,609.5 (934.2) | NEM lower 60 second requirement for a NEM load event | NIL | FCAS
N>Q_LSLS_9U8 | $1,379 ($2,333) | 4.4 (8.9) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage | NSW
T>>T_GTSH_EXP_3D | $1,375 (0) | 0.6 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown 220 kV line (flow North) for trip of other Hadspen to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage | Tas
S>>X_TBTU+CB_TBCG_1 | $1,374 (0) | 5.8 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage | SA
F_T++NIL_MG_R5 | $1,322 ($601) | 230.6 (68.4) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL | FCAS
V>>S_HYML_4 | $1,304 ($32,794) | 3.8 (53.6) | Out = one Heywood 500/275 kV transformer, avoid overloading remaining Heywood 500/275 kV transformer for loss of a Pelican Point GT and consequent offloading of Pelican Point ST | Outage | SA
CA_SPS_41CE7351_01 | $1,300 (0) | 1.3 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
V>>V_NIL_5 | $1,289 ($2,303) | 5.6 (7.1) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL | Vic
T>>T_NIL_BL_EXP_1B | $1,287 (0) | 1.3 (0) | Out = Nil, avoid O/L a Gordon to Chapel St 220 kV line for trip of the parallel line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
V>>S_TBTU_TBCG_TBMO | $1,258 (0) | 6.3 (0) | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage | SA
F_T+CSGO_TG_R60 | $1,220 (0) | 0.6 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
T>T_HAPM_1B | $1,172 (0) | 11.7 (0) | Out = Hadspen to Palmerston No. 1 220 kV line, avoid pre-contingent O/L of the Hadspen to Palmerston No. 2 220kV line (flow North), feedback | Outage | Tas
T>T_GTSH_5K | $1,169 ($273) | 10.8 (3.8) | Out = Sheffield to Georgetown 220 kV line, avoid O/L line terminal equipment of Palmerston to Sheffield 220 kV line (flow to Palmerston) for trip of remaining Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
F_I+APHY_L60 | $1,136 ($555) | 1,038.9 (718.4) | Out = Heywood to Alcoa Portland 500 kV line, lower 60 second requirement | Outage | FCAS
F_MAIN++ML_L5_APD | $1,128 ($495) | 72.8 (66.1) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
V>>V_NIL1A_R | $1,104 ($2,355) | 30.4 (46.8) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line This constraint equation only binds for high flows from Victoria to NSW | NIL | Vic
T>T_HAPM_220_5A_N-2 | $1,086 ($23) | 3.2 (0.1) | Out = NIL, Loss of both Hadspen to Palmerston 220kV lines declared credible, avoid O/L either Palmerston to Hadspen (No. 3 or No. 4) 110kV line (flow to North) for loss of both Hadspen to Palmerston 220kV lines, feedback | Outage | Tas
T_LIPM_PMWA_1_N-3 | $1,081 ($1,445) | 0.2 (18.5) | Out=Nil, loss of both Liapootah to Waddamana (tee) to Palmerston 220 kV lines and Palmerston to Waddamana 110 kV line classified credible, limit southern generators to <= southern load + 15 MW | Outage | Tas
S>SE132BUS_SETX_SGKH | $1,050 (0) | 0.1 (0) | Out= one South East 132 kV bus (W or E bus), avoid O/L Snuggery to Keith 132 kV line on trip of South East 275/132 transformer connected to the in service 132 kV bus | Outage | SA
F_T+NIL_BL_R60_1 | $1,049 ($9,974) | 205.3 (1,378.8) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 400ms | NIL | FCAS
F_MAIN+APHY_L5 | $1,041 ($1,513) | 88.9 (75.1) | Out=Heywood to Alcoa Portland 500kV line, Lower 5 min Service Requirement for the loss of the remaining 500kV line, Basslink unable to transfer FCAS | Outage | FCAS
F_I+MPP_TG_R60_N-2 | $1,031 (0) | 218.2 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Global Raise 60 sec requirement | Outage | FCAS
VS_150 | $1,018 (0) | 1.2 (0) | Victoria to SA on VicSA upper transfer limit of 150 MW | Outage | Vic
F_MAIN+MPP_TG_R60N-2 | $983 (0) | 41.9 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 60 sec requirement, Basslink unable to transfer FCAS | Outage | FCAS
T>T_BUSH1_220 | $983 (0) | 1.6 (0) | Out = Burnie to Sheffield 220kV line, Hampshire link open, avoid O/L a Sheffield 220/110kV transformer for loss of the other Sheffield 220/110kV transformer | Outage | Tas
Q:N_NIL_OSC | $981 ($850) | 2.1 (24.6) | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL | Qld
F_T+NIL_WN_TG_R6 | $963 ($2,942) | 33.5 (15.2) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS | NIL | FCAS
S>>XSEVC2+CB_SETB1_4 | $956 (0) | 5.8 (0) | Out= South East #2 SVC and South East CB6607 & CB6611, avoid O/L Snuggery - Keith 132kV on trip of South East - Tailem Bend #1 275kV lines, Feedback | Outage | SA
F_T++FASH1_2C_TG_R6 | $952 (0) | 0.8 (0) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
T>T_FASH_3_N-2 | $931 ($432) | 1.0 (2.4) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Hampshire link closed, avoid O/L Waratah Tee to Hampshire to Burnie 110 kV line (flow to Burnie) for loss of both Farrell to Sheffield 220 kV lines | Outage | Tas
F_MAIN++NIL_DYN_RREG | $928 ($919) | 46.3 (38.2) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL | FCAS
T_X_GTSH_1 | $914 (0) | 2.9 (0) | Outage = Both Georgetown to Sheffield 220kV lines, limit West Coast + Sheffield generation <= West Coast + North West load + 10MW, limiting SH-PM line flow to 10 MW | Outage | Tas
F_T++NIL_WN_TG_R6 | $903 ($2,124) | 11.0 (36.8) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL | FCAS
V::N_MSUT_xxx | $898 ($777) | 17.4 (20.8) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
V::N_HYSE_xxx | $884 ($2,458) | 21.8 (42.0) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage | Vic
F_T+NIL_WF_TG_R6 | $877 (0) | 21.0 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
V^^S_MOTB_MAXG | $871 (0) | 14.7 (0) | Out= Mobilong - Tailem Bend 132kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage | SA
F_T+NIL_WN_TG_R5 | $865 ($202) | 36.6 (15.2) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS | NIL | FCAS
T>T_GTSH_IMP_4F | $865 ($129) | 5.0 (2.1) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow North) for trip of Hadspen to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
F_MAIN++ML_L6_0400 | $861 ($3,492) | 534.5 (1,300.8) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
F_MAIN+NIL_DYN_LREG | $855 ($3,082) | 67.3 (154.9) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink unable transfer FCAS | NIL | FCAS
N>>N-BYYS_4 | $851 (0) | 0.6 (0) | Out = Bannaby to Yass(61), avoid Marulan to Yass(4) O/L on Marulan-Yass(5) trip; Feedback | Outage | NSW
F_T++CSGO_TG_R60 | $842 (0) | 43.4 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage | FCAS
F_MAIN++APHY_L60 | $841 ($1,065) | 274.4 (205.8) | Out = Heywood to Alcoa Portland 500 kV line, lower 60 second requirement for the loss of the remaining Alcoa Portland to Heywood 500 kV line, Basslink able to transfer FCAS | Outage | FCAS
T>T_HAPM_2B | $839 (0) | 6.6 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow North) for trip of a Sheffield to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
TV_500 | $833 (0) | 10.8 (0) | Tas to Vic on Basslink upper limit of 500 MW | Outage | Tas
F_MAIN++ML_L60_0400 | $831 ($575) | 590.5 (279.8) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL | FCAS
N^^V_MSDD2 | $821 ($31) | 1.9 (2.4) | Out = Dederang to Murray 330 kV line, avoid voltage collapse for trip of the remaining Dederang to Murray 330 kV line | Outage | NSW
T>T_HAPM_5L | $756 (0) | 6.1 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L line terminal equipment of Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No. 2 220 kV line, feedback | Outage | Tas
F_T+NIL_WF_TG_R5 | $743 (0) | 20.7 (0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
N>>N-KVCW_9 | $743 (0) | 1.3 (0) | Out = KangarooValley to Capital(3W), avoid Yass to Canberra(9) O/L on Yass to Lower Tumut(3) trip; Feedback | Outage | NSW
S>>XSEVC1+CB_SETB2_4 | $736 (0) | 6.6 (0) | Out= South East #1 SVC and South East CB6606 & CB6610, avoid O/L Snuggery - Keith 132kV on trip of South East - Tailem Bend #2 275kV line, Feedback | Outage | SA
S_HALWF2_0 | $677 (0) | 0.4 (0) | Discretionary upper limit for Hallett 2 Wind Farm generation of 0 MW | Outage | SA
V>>S_NIL_KHTB2_KHTB1 | $642 ($12,760) | 3.3 (4.3) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV one trip of Keith - Tailem Bend #2 132kV line, Feedback | NIL | SA
T>T_GTHA_IMP_4L | $637 ($9,108) | 4.7 (33.1) | Out = Hadspen to Georgetown 220 kV line, avoid overloading Sheffield to Georgetown No.1 220 kV line (flow to Georgetown) for trip of Sheffield to Georgetown No.2 220 kV line with no NCSPS action | Outage | Tas
F_MAIN+ML_L6_0400 | $632 ($581) | 366.6 (342.6) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
T_V_NIL_FCSPS | $616 ($167) | 3.5 (2.0) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL | Tas
F_T++FARE_N-2_TG_R6 | $611 ($1) | 3.8 (0.7) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
N^N_CHLS_1 | $610 ($6) | 13.5 (0.5) | Out = Coffs Harbour to Lismore (89) 330 kV line, avoid voltage collapse on trip of Koolkhan to Lismore 132 kV line (967) | Outage | NSW
T>T_GTHA_1E | $599 (0) | 13.0 (0) | Out = Hadspen to George Town No. 2 220 kV line, avoid pre-contingent O/L of the Hadspen to George Town No. 1 220kV line (flow to George Town), feedback | Outage | Tas
F_Q++ARTW_L5 | $573 ($4,113) | 6.6 (55.3) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
V>>N_SMTXF2_2 | $565 (0) | 6.5 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Ballarat to Bendigo 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage | Vic
Q>>NIL_871_855_POST | $565 (0) | 2.1 (0) | Out = Nil, Post-8868 commissioning, avoid overload on Calvale to Stanwell (855) 275kV line on trip of Calvale to Wurdong (871) 275kV line, Feedback | NIL | Qld
T>T_HAGT_SHGT_N-2 | $559 (0) | 8.4 (0) | Out= NIL, Loss of both Sheffield to Georgetown 220kV lines declared credible, avoid O/L the Hadspen to Georgetown 220kV line for loss of both Sheffield to Georgetown 220kV lines, Feedback | Outage | Tas
F_T_GORDON_R6 | $556 (0) | 9.4 (0) | Out= NIL, Gordon R6 Requirement <= 0MW | Outage | FCAS
T>>T_GTHA_EXP_3GH | $538 (0) | 2.3 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Hadspen to George Town and Sheffield to George Town 220 kV line for trip of Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_PMSH_IMP_4D | $520 (0) | 0.3 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 2 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
CA_SPS_3FFA5B9A_01 | $501 (0) | 1.0 (0) | Constraint Automation, O/L BATS_BETS_220 @BATS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
T_T_BA_JB_RC2_250 | $489 (0) | 8.3 (0) | Discretionary 250 MW upper limit on Bastyan, John Butters and Reece 2 | Outage | Tas
QNTE_ROC | $488 ($2,053) | 11.6 (18.0) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL | Qld
N>N-CHKK_TE_1 | $486 ($471) | 0.2 (0.3) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
F_MAIN+ML_L60_0400 | $482 ($519) | 271.1 (258.8) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = 400, Basslink unable transfer FCAS | NIL | FCAS
T>T_NIL_BL_220_6B | $480 ($1,714) | 2.9 (14.8) | Outage = Nil, avoid overloading the Palmerston to Sheffield 220kV line (flow to South) for loss of a Sheffield to Georgetown 220kV line, feedback equation | NIL | Tas
V::S_XKHTB1+2_SETB | $478 (0) | 3.4 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S; Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage | SA
V::S_SEVC_MAXG_2 | $471 (0) | 2.3 (0) | Out= South East one SVC; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
TV_325 | $466 (0) | 5.5 (0) | Tas to Vic on Basslink upper limit of 325 MW | Outage | Tas
T>T_X_HAPM110_1 | $450 (0) | 2.1 (0) | Out= both Palmerston to Hadspen 110 kV lines, avoid O/L either Palmerston to Hadspen 220 kV line (flow to North) on trip of the parallel Palmerston to Hadspen 220 kV line, feedback | Outage | Tas
T>T_NIL_BL_IMP_6E | $433 ($65,499) | 5.8 (234.3) | Out = Nil, avoid overloading Sheffield to Georgetown No. 1 220 kV line (flow to Georgetown) on trip of the Sheffield to Georgetown No. 2 220 kV line with no SPS action | NIL | Tas
S>S_PAPG_PPLF_PSSB | $420 (0) | 6.1 (0) | Out= Para to Parafield Gardens West 275kV line, avoid O/L Parafield Gardens-Salisbury #1 66kV on trip of Pelican Point-Lefevre 275kV line, Feedback | Outage | SA
V>>SML_NIL_7C | $418 (0) | 1.3 (0) | Out = Nil, avoid O/L Arrarat to Stawell 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL | Vic
V>>N-NIL_HA | $416 ($944) | 3.1 (9.3) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL | Vic
V>V_DDMB_1 | $415 (0) | 0.8 (0) | Out= one Dederang to Mount Beauty 220 kV line, avoid O/L the remaining Dederang to Mount Beauty 220kV line on trip of the Eildon to Thomastown 220 kV line, feedback | Outage | Vic
V>>S_TB6125+28_KHTB1 | $411 (0) | 1.6 (0) | Out = Tailem Bend CBs 6125 and/or 6128 (both or either CB); Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend 132kV #1 line for loss of Tailem Bend transformer #4. | Outage | SA
V::S_MAXG_NPS_N-2 | $391 (0) | 4.2 (0) | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA with loss of both Northern Power Station units declared as credible. | Outage | SA
N^N-89_LSTX_SVC | $386 ($77) | 2.8 (3.4) | Out = Coffs Harbour to Lismore (89) 330 kV line and Lismore 330/132 kV transformer with Lismore SVC in reactive power control mode, avoid voltage collapse on trip of Koolkhan to Lismore (967) 132 kV line | Outage | NSW
V::S_TBCP_MAXG_2 | $382 (0) | 2.5 (0) | Out= Tailem Bend 275kV Cap Bank (Tungkillo 275kV Cap available); Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S) (Swamp out if SA demand less/equal to 3200MW) | Outage | SA
TV_410 | $373 (0) | 3.5 (0) | Tas to Vic on Basslink upper limit of 410 MW | Outage | Tas
T>>T_GTHA_EXP_3H | $351 (0) | 6.1 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
N^^Q_AR_VC_B1 | $341 (0) | 0.6 (0) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
V>>V_SMTXF2_4AR | $339 (0) | 5.3 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Richmond to Brunswick 220 kV cable on trip of Rowville A1 500/220 kV transformer | Outage | Vic
V::N_HWSM_xxx | $337 ($4,537) | 8.1 (48.0) | Out = Hazelwood to South Morang 500 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria for this outage and all the binding results have been combined. | Outage | Vic
V_T_NIL_FCSPS | $331 ($94,121) | 1.0 (325.4) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) This constraint equation binds when there is high import to Tasmania or a low amount of load is enabled for tripping. | NIL | Vic
F_Q++LDTW_L6 | $331 (0) | 9.7 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
T>T_CSNN_1 | $329 (0) | 0.4 (0) | Out = Chapel St to New Norfolk 110 kV line, avoid O/L the Lake Echo Tee to Waddamana No.1 line (flow to North) for loss of Creek Rd to New Norfolk 110kV line, feedback | Outage | Tas
F_Q++ARDM_L6 | $326 ($45) | 13.2 (2.5) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
CA_SPS_40381C26_01 | $324 (0) | 1.8 (0) | Constraint Automation, O/L MOBTAB_1 @T_BEND for CTG LSIQ on trip of CH_GDN - T_BEND 275KV LINE. Generated by STNET[MANFR] Host NOREEMP3(SP) | Outage | Constraint Automation
CA_SPS_41B92B29_02 | $323 (0) | 1.0 (0) | Constraint Automation, O/L 84 @LIDDELL for CTG LNPF on trip of LIDDELL-MUSBK330 83 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
T>>T_NIL_BL_EXP_3F | $321 (0) | 0.4 (0) | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
T_T_JB_RC1+2_TI_250 | $321 (0) | 0.3 (0) | Discretionary 250 MW upper limit on John Butters, Reece 1+2 and Tribute | Outage | Tas
F_T+NIL_WN_TG_R60 | $314 ($186) | 33.4 (15.1) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink unable to transfer FCAS | NIL | FCAS
F_MAIN+APHY_L60 | $312 ($273) | 88.4 (68.4) | Out=Heywood to Alcoa Portland 500kV line, Lower 60 sec Service Requirement for the loss of the remaining 500kV line, Basslink unable to transfer FCAS | Outage | FCAS
T>T_GTSH_2C | $307 ($432) | 6.0 (6.3) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
F_T+FASH_N-2_RREG | $304 ($96) | 18.5 (0.4) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Bastyan, John Butters, Reece 1 & 2, Mackintosh and Tribute Raise Regulation Requirement = 0, Note Farrell 220kV bus configured as Limits advice 7 June 2006 | Outage | FCAS
V::N_NIL_xxx | $302 ($21,337) | 10.6 (419.6) | Out = Nil, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line There are twelve constraint equations that make up the transient stability export limit from Victoria and all the binding results have been combined. | NIL | Vic
T>T_GTHA_1F | $294 (0) | 1.4 (0) | Out = Hadspen to George Town No. 1 220 kV line, avoid pre-contingent O/L of the Hadspen to George Town No. 2 220kV line (flow to George Town), feedback | Outage | Tas
F_S_NPS1_R6_ZERO | $291 (0) | 58.3 (0) | Out= NIL, Northern PS 1 R6 Requirement <= 0MW | Outage | FCAS
N^^Q_BCDM_B1 | $290 (0) | 3.8 (0) | Out = One Bulli Creek - Dumaresq (8L or 8M) 330 kV line, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
N>N-ARTW86_1B | $284 (0) | 1.0 (0) | Out = Armidale to Tamworth (86) 330 kV line, avoid overloading Tamworth to Armidale (85) 330 kV line on trip of largest Queensland generator | Outage | NSW
T>T_NIL_BL_5B | $280 (0) | 2.6 (0) | Out = Nil, avoid pre-contingent O/L of the Hadspen to Georgetown No. 2 220kV line (flow to North), feedback | NIL | Tas
V>>SML_BAML2_1 | $276 (0) | 0.3 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line (complete line or line sections), prevent overload of the Moorabool to Ballarat No. 1 220 kV line for trip of the Moorabool to Terang 220 kV line, feedback | Outage | Vic
Q_N_NIL-1078 | $266 ($9,318) | 0.3 (32.6) | Out = Nil, reduce QNI when it is over the 1078 MW limit by 1078 minus the MW over the 1078 MW limit (capped at 1000 MW) This constraint equation only operates when the NSW1-QLD1 interconnector flow is greater than 1103 MW from Queensland to NSW. It ensures that the interconnector flow does not excessively exceed the 1078 MW limit as a thermal overload limit exists at 1105 MW. | NIL | Qld
CA_MQS_416718EE_01 | $264 (0) | 0.3 (0) | Constraint Automation, O/L KEISNG_1 @SNUGGY for CTG TSIA on trip of S_EAST 2 275/132KV TX. Generated by STNET[MANBL] Host MANEEMP2(MQ) | Outage | Constraint Automation
TV_350 | $260 (0) | 1.3 (0) | Tas to Vic on Basslink upper limit of 350 MW | Outage | Tas
F_MAIN++NIL_BL_L60 | $259 ($9,376) | 53.9 (1,266.9) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL | FCAS
V::S_SESG_SETB | $250 (0) | 2.3 (0) | Out= South East-Snuggery 132kV (including line section connecting Lake Bonney WFs + Lake Bonney WFs O/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line (Note: with NPS and Playford PS assumed to be O/S). | Outage | SA
T_T_FASH_5_N-2 | $249 ($19) | 0.5 (0.2) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, Mackintosh P/S unavailable, Hampshire link open, limit Mackintosh + Tribute + Reece 1 <= 110% of West Coast load | Outage | Tas
N>N-GITN_TE_C1 | $246 ($3,770) | 8.7 (5.0) | Out = Glen Innes to Tenterfield (96R) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
S>>MOTB_TBTU_TBCG | $245 (0) | 2.7 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage | SA
V>V_NIL_ROYP56_R5_1 | $241 (0) | 1.2 (0) | Out = Nil, loss of Yallourn to Rowville No. 5 and No. 6 220 kV lines declared credible, avoid overloading YPS - HWPS No. 1 220 kV line for loss of YPS - ROTS No. 5 & No. 6 220 kV lines, radial mode, Yallourn W1 on 500 kV, feedback | NIL | Vic
N^^Q_ARDM_B1 | $241 ($1,443) | 3.3 (7.3) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage | NSW
V>>V_NIL_4C | $237 (0) | 0.1 (0) | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL | Vic
N^^V_LTUT_1 | $236 (0) | 1.7 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
T>T_FASH_2_N-2 | $236 (0) | 1.3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Farrell 220 kV bus split, avoid O/L Farrell 220/110kV No.2 transformer | Outage | Tas
Q>>NIL_MRTX5_MRTX4 | $235 ($1,011) | 0.2 (1.8) | Out = Nil, avoid overloading Middle Ridge No.4 330/275 kV transformer on trip of Middle Ridge No.5 330/275 kV transformer | NIL | Qld
T>T_HAPM_IMP_4D | $235 (0) | 1.3 (0) | Out = Hadspen to Palmerston No. 1 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow North) for trip of either Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
V>>V-HWLY_3 | $235 (0) | 3.9 (0) | Outage = Hazlewood to Loy Yang (HWTS-LYPS) No.3 500kV line, avoid overloading Hazelwood to Loy Yang No.1 or No.2 500kV line on trip of any of the remaining Hazelwood to Loy Yang 500kV line,feedback | Outage | Vic
T>T_PMSH_IMP_4A | $234 (0) | 3.8 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
TV_ZERO | $233 (0) | 0.8 (0) | Tas to Vic on Basslink upper limit of 0 MW | Outage | Tas
N>>N-NIL_1A_OPENED | $230 (0) | 1.3 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL | NSW
F_Q++LDTW_L60 | $228 (0) | 9.0 (0) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_I+ML_L6_APD | $227 ($379) | 153.3 (200.7) | Out = Nil, Lower 6 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
F_Q++LDTW_R6 | $226 ($38) | 11.0 (3.6) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage | FCAS
F_T++FASH_N-2_TG_R5 | $222 (0) | 10.5 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
V::N_SMF2_xxx | $203 (0) | 2.1 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage | Vic
F_V+NIL_PTH02_R5 | $199 ($286) | 14.3 (15.8) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
F_V+NIL_PTH01_R5 | $199 ($384) | 16.3 (19.3) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
F_T+NIL_WF_TG_R60 | $189 (0) | 21.0 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink unable to transfer FCAS | NIL | FCAS
T>T_HAPM_110_IMP_4B | $183 (0) | 4.9 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L a Palmerston to Hadspen No. 1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
N^^Q_ARTW_MPP_N-2 | $179 (0) | 2.4 (0) | Out = Armidale to Tamworth (85 or 86) and trip of both Millmerran units declare credible, avoid Voltage collapse on loss of both Millmerran units | Outage | NSW
N>>N-DP_TIETX_A | $179 (0) | 2.1 (0) | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (330 to 220 kV) on Kerang-Bendigo trip; Feedback | Outage | NSW
F_V+NIL_APD01_R5 | $178 ($219) | 12.4 (10.3) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
N^^V_MSUT_1 | $176 ($206) | 1.8 (1.6) | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink | Outage | NSW
T>>T_NIL_BL_EXP_7C | $172 ($53) | 0.5 (0.7) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL | Tas
V>>S_HYML_3 | $167 (0) | 2.4 (0) | Out = One Heywood 500/275 kV txfmr in service only, prevent overload of the in service 500/275 kV Heywood transformer for loss of Lake Bonney Wind Farm | Outage | SA
F_Q++ARTW_L6 | $167 ($3,215) | 10.4 (58.1) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement | Outage | FCAS
V>>N-WA_330_BUSB_2 | $158 (0) | 3.4 (0) | Out = Wagga 330kV B Bus(Wagga Bus B), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
F_Q++ARDM_L5 | $156 ($22) | 5.3 (2.0) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement | Outage | FCAS
N>>N-RGSW_A | $156 (0) | 2.3 (0) | Out = Regentville to Sydney West(38), avoid Bayswater to Liddell(34) O/L on Bayswater to Liddell(33) trip; Feedback | Outage | NSW
S>NIL_HUWT_STBG | $154 ($6,156) | 0.2 (6.9) | Out = Nil; Limit Snowtown WF generation to avoid Snowtown - Bungama line OL on loss of Hummocks - Waterloo line. | NIL | SA
T>T_HAPM_IMP_4C | $153 (0) | 1.6 (0) | Out = Hadspen to Palmerston No. 1 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow North) for trip of Palmerston to Sheffield 220 kV line with no NCSPS action, feedback | Outage | Tas
I_CTRL_ISSUE_TE | $153 (0) | 3.8 (0) | DC Link Control Issue Constraint for Terranora | Outage | Other
T>T_HAPM_1A | $144 (0) | 2.8 (0) | Out = Hadspen to Palmerston No. 2 220 kV line, avoid pre-contingent O/L of the Hadspen to Palmerston No. 1 220kV line (flow North), feedback | Outage | Tas
S>S_PAPG_PPLF_PGPS | $137 (0) | 0.2 (0) | Out= Para to Parafield Gardens West 275kV line, avoid O/L Parafield Gardens West-Parafield Gardens 66kV #1 line on trip of Pelican Point-Lefevre 275kV line, Feedback | Outage | SA
V>S_NIL_NIL_HYTX2 | $135 ($817) | 0.3 (30.4) | Out = NIL, avoid O/L Heywood M2 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL | Vic
V>>S_KHTB1_SETB_KHTB | $134 (0) | 2.3 (0) | Out = Keith - Tailem Bend #1 132 kV line. Prevent Keith - Tailem Bend #2 line OL for South East - Tailem Bend line trip. | Outage | SA
T>>T_GTHA_EXP_3G | $133 (0) | 0.4 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L remaining Hadspen to George Town 220 kV line (flow to George Town) for trip of a Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_NIL_BL_IMP_5H | $133 (0) | 1.4 (0) | Out = Nil, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow to North) for trip of either Sheffield to Georgetown 220 kV line with no SPS action, feedback | NIL | Tas
T>T_NIL_BL_IMP_3F | $131 ($70) | 5.2 (0.2) | Out = Nil, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220 kV line with no SPS action, feedback | NIL | Tas
T>T_PMSH_IMP_4C | $130 (0) | 0.6 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to George Town No. 1 220 kV line (flow to George Town) for trip of Hadspen to George Town No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
V::N_LTWG_xxx | $127 (0) | 2.1 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
T>T_NIL_BL_IMP_6EE | $126 ($0) | 1.8 (0.1) | Out = Nil, avoid O/L Sheffield to Georgetown No. 2 220 kV line (flow to Georgetown) for trip of the Sheffield to Georgetown No. 1 220 kV line with no SPS action, feedback | NIL | Tas
V>>S_KH_X_SETB_SETB | $124 (0) | 0.9 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East - Tailembend 275kV on trip of one South East - Tailembend 275kV line, Feedback | Outage | SA
F_Q++LDTW_R60 | $123 ($21) | 8.6 (2.4) | Out = Liddell to Tamworth (84) line, Qld Raise 60 sec Requirement | Outage | FCAS
N_MBTE1_A | $121 ($4) | 0.3 (0.2) | Out= one Directlink cable, NSW to Qld limit | Outage | NSW
F_V+NIL_PTH01_R6 | $118 ($300) | 16.4 (19.7) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
V>>V_SMTXF2_6 | $118 (0) | 1.4 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage | Vic
S>>X_TBTU+CB_CGTB_4 | $116 (0) | 4.3 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Mobilong - Tailem Bend 132kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | Outage | SA
F_V+NIL_APD02_R5 | $115 ($97) | 6.7 (4.8) | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
F_V+NIL_PTH02_R6 | $115 ($198) | 14.1 (15.8) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
V::S_HYSE | $114 ($6) | 3.2 (0.3) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of one NPS unit or South East-Tailem Bend 275 kV line. | Outage | SA
V::S_TBCB6594_MAXG_2 | $109 (0) | 0.8 (0) | Out = Tailem Bend CB6594 O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available) with NPS and Playford assumed to be OOS. | Outage | SA
V::S_NIL_TBSE | $108 (0) | 0.2 (0) | Out = Nil; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available) with NPS and Playford assumed to be OOS. | NIL | SA
F_V+NIL_APD01_R6 | $103 ($127) | 12.3 (9.8) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
F_MAIN++ML_L60_APD | $100 ($187) | 48.3 (51.5) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
F_S_NPS2_R6_ZERO | $99 (0) | 20.6 (0) | Out= NIL, Northern PS 2 R6 Requirement <= 0MW | Outage | FCAS
F_S_NPS1_RREG_ZERO | $99 (0) | 50.2 (0) | Out= NIL, Northern PS 1 RREG Requirement <= 0MW | Outage | FCAS
N>>N-NIL__2_15M | $92 (0) | 0.2 (0) | Out= NIL, avoid O/L Liddell to Tamworth (84) on trip of Liddell to Muswellbrook (83) line, Feedback | NIL | NSW
F_V+NIL_PTH01_R60 | $92 ($228) | 16.3 (19.1) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
V_APHY1_1 | $91 ($7,078) | 0.5 (30.6) | Out = Heywood to APD No. 1 500 kV line section & Heywood M2 500/275 kV txfmr, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage | Vic
F_T++NIL_WF_TG_R6 | $91 (0) | 5.2 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL | FCAS
F_V+NIL_PTH02_R60 | $90 ($163) | 13.8 (15.9) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
T_V_FCSPS_RAMP | $87 ($193) | 0.3 (0.7) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage | Tas
V^^S_TBCPTX_MAXG | $85 (0) | 2.3 (0) | Out= Tailem Bend 275/132kV transformer and Tailem Bend 100Mvar Cap Bank; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage | SA
N>Q-MUTW_2 | $85 (0) | 2.2 (0) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage | NSW
N>N-ARCH_87_TE_C1 | $83 (0) | 1.8 (0) | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage | NSW
F_V+NIL_APD01_R60 | $82 ($104) | 12.1 (10.0) | Out=Nil, limit APD01 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
T::T_NIL_5 | $81 (0) | 0.2 (0) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL | Tas
F_V+NIL_PTH03_R5 | $76 ($242) | 5.6 (9.9) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 5 Min service | NIL | FCAS
T^V_GTSH_1 | $76 (0) | 0.7 (0) | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse or voltage violations for trip of the remaining Sheffield to Georgetown 220 kV line | Outage | Tas
V>>N-WA_330_BUSB_1 | $75 (0) | 1.5 (0) | Out = Wagga 330kV B Bus(Wagga Bus B), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
TV_560 | $73 (0) | 0.8 (0) | Tas to Vic on Basslink upper limit of 560 MW | Outage | Tas
N>>N-WWSS+WWIG_3 | $71 (0) | 4.3 (0) | Out = Sydney South to Wallerawang & Ingleburn to Wallerawang(76 + 77), avoid Mt. Piper 500/330kV tie Tx overload on trip of the other; Feedback | Outage | NSW
N>>N-NIL__3_15M | $71 (0) | 0.3 (0) | Out= NIL, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL | NSW
F_T_REECE2_DS_R6 | $69 ($2) | 5.8 (0.9) | Determine upper limit for R6 FCAS enablement for Reece 2 based on FCAS Boost Mode status point for unit | NIL | FCAS
T>T_X_HAPM110_4 | $67 (0) | 0.3 (0) | Out= both Palmerston to Hadspen 110 kV lines, avoid O/L a Sheffield to Georgetown 220 kV line (flow to Georgetown) on trip of the parallel Sheffield to Georgetown 220 kV line, feedback | Outage | Tas
T>T_GTHA_IMP_4N | $66 ($12) | 0.3 (0.1) | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town No. 2 220 kV line (flow to George Town) for trip of Sheffield to George Town No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
N^^Q_LS_VC_B1 | $64 (0) | 0.2 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage | NSW
F_V+NIL_PTH01_L5 | $63 ($102) | 14.7 (19.3) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
N::Q_RGSW_KC | $61 (0) | 0.3 (0) | Out= Regentville - Sydney West (38), NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
V>>N_DDMS_2 | $60 ($442) | 2.8 (6.4) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Murray to Dederang 330 kV line, feedback | Outage | Vic
N>N-LSTN_TE_C1 | $60 ($99) | 0.8 (5.3) | Out = Lismore to Tenterfield (96L) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage | NSW
F_V+NIL_APD02_R6 | $59 ($51) | 6.5 (4.8) | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
F_ESTN++HYTR_L60 | $57 ($19) | 23.8 (9.0) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
CA_SPS_41B7F9D7_02 | $57 (0) | 0.4 (0) | Constraint Automation, O/L 84 @LIDDELL for CTG LNPF on trip of LIDDELL-MUSBK330 83 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
V^^S_SECP_MAXG | $56 (0) | 0.7 (0) | Out = South East 275 kV capacitor; Vic to SA Long Term Voltage Stability limit for loss of one NPS generator or the largest generation block in SA (Note: with NPS and Playford assumed I/S). | Outage | SA
F_I+ML_L60_APD | $55 ($132) | 82.9 (143.5) | Out = Nil, Lower 60 sec requirement for a NEM Load Event, ML = APD | Outage | FCAS
V>>N-JNWG_RADIAL_2 | $51 (0) | 0.8 (0) | Out = Jindera to Wagga(62), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
F_V+NIL_PTH02_L5 | $49 ($134) | 12.1 (15.0) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
T>T_NIL_NCSPS5_5FF | $46 (0) | 1.6 (0) | Out = Nil, avoid overloading the line terminal equipment of the Hadspen to Georgetown No. 2 220 kV line (flow to North) for trip of the Hadspen to Georgetown No. 1 220 kV line, feedback equation | NIL | Tas
F_S_NPS2_RREG_ZERO | $45 (0) | 18.6 (0) | Out= NIL, Northern PS 2 RREG Requirement <= 0MW | Outage | FCAS
F_ESTN++MLSY_L60 | $45 (0) | 12.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 60 sec Requirement | Outage | FCAS
F_Q++ARDM_L60 | $45 ($15) | 12.2 (2.5) | Out = one Armidale to Bulli Creek (8C, 8E, 8L or 8M) line, Qld Lower 60 sec Requirement | Outage | FCAS
T>T_HAPM_110_IMP_4A | $44 (0) | 0.8 (0) | Out = Hadspen to Palmerston No. 3 110 kV line, avoid O/L the Palmerston to Hadspen No.1 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 2 220kV line with no NCSPS action, feedback | Outage | Tas
T>T_GTSH_IMP_4H | $43 ($24) | 0.3 (0.5) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
F_V+NIL_APD02_R60 | $43 ($44) | 6.6 (4.8) | Out=Nil, limit APD02 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
V_APHY1_2_1 | $43 (0) | 0.1 (0) | Out = Heywood to APD No. 1 500 kV line section only, both Heywood 500/275 kV txfmrs in service, limit voltage unbalance at the APD 500 kV bus | Outage | Vic
CA_SPS_3FF8E592_08 | $42 (0) | 0.1 (0) | Constraint Automation, O/L ROTS_YPS7_220 @YPS for CTG LVCA on trip of ROTS-YPS6 220KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
F_T++FARE_N-2_TG_R60 | $41 ($0) | 8.1 (0.8) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS | Outage | FCAS
F_Q++ARTW_L60 | $41 ($1,091) | 9.7 (57.2) | Out = Armidale to Tamworth (85 or 86) line, Qld Lower 60 sec Requirement | Outage | FCAS
F_V+NIL_PTH03_R6 | $39 ($160) | 5.4 (9.8) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 6 sec service | NIL | FCAS
V^^S_SEVC_MAXG | $39 ($72) | 1.3 (4.2) | Out= South East one SVC; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage | SA
V::S_MOTB_MAXG_2 | $38 (0) | 0.2 (0) | Out= Mobilong - Tailem Bend 132kV line; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
TV_400 | $37 (0) | 0.2 (0) | Tas to Vic on Basslink upper limit of 400 MW | Outage | Tas
F_ESTN++HYTR_L5 | $37 ($26) | 15.3 (6.7) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage | FCAS
V>>S_KHKN_NIL_SGKH | $36 (0) | 0.1 (0) | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip. | NIL | SA
V^^S_CGMB_SECP_MAXG2 | $36 (0) | 0.3 (0) | Out = Cherry Gardens - Mt Barker 132kV line and South East 275 kV capacitor O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage | SA
N>N-KKLS_TE_2 | $35 ($33) | 0.7 (0.9) | Out = Koolkhan to Lismore (967) 132 kV line, avoid overloading the Armidale to Glen Innes (96T) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects that this constraint equation will continue to bind for a reasonable portion of any future outage times. | Outage | NSW
T>T_HAPM_220_5A | $35 (0) | 0.8 (0) | Out = Hadspen to Palmerston 220kV line, avoid O/L either Palmerston to Hadspen (No. 3 or No. 4) 110kV line (flow to North) for loss of the remaining Hadspen to Palmerston 220kV line, Feedback | Outage | Tas
V::S_SETB_SETB | $34 ($27,587) | 0.7 (85.7) | Out = South East to Tailem Bend 275 kV line, avoid transient instability for loss of the parallel South East to Tailem Bend 275 kV line | Outage | SA
V>>N-JNWG_RADIAL_1 | $34 (0) | 0.6 (0) | Out = Jindera to Wagga(62), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage | Vic
F_MAIN++NIL_DYN_LREG | $33 ($3,075) | 4.0 (133.3) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL | FCAS
F_I+TL_L5_0500 | $33 ($4) | 13.3 (1.3) | Lower 5 min Service Requirement for a NEM Network Event, TL = 500 | Outage | FCAS
V>>S_KHTB2_SETB_KHTB | $33 (0) | 0.2 (0) | Out = Keith - Tailem Bend #2 132 kV line. Prevent Keith - Tailem Bend #1 line OL on trip one of the South East - Tailem Bend lines. | Outage | SA
Q>>NIL_855_871_POST | $32 (0) | 0.8 (0) | Out = Nil, Post-8868 commissioning, avoid overload on Calvale to Wurdong (871) 275kV line on trip of Calvale to Stanwell (855) 275kV line, Feedback | NIL | Qld
F_V+NIL_APD01_L5 | $32 ($53) | 10.8 (10.1) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
CA_SPS_41B92B29_01 | $31 (0) | 0.1 (0) | Constraint Automation, O/L 83 @LIDDELL for CTG LNPA on trip of TAMWORTH-LIDDELL 84 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
F_MAIN+ML_L5_APD | $31 ($539) | 1.9 (26.0) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
T>T_PMSH_IMP_4B | $31 (0) | 0.6 (0) | Out = Palmerston to Sheffield 220 kV line, avoid O/L Hadspen to Palmerston No. 2 220 kV line (flow to Hadspen) for trip of Hadspen to Palmerston No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
F_ESTN++MLSY_L5 | $31 (0) | 9.3 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 5 min Requirement | Outage | FCAS
T>T_NIL_BL_IMP_7CC | $29 ($539) | 0.3 (4.8) | Out = Nil, avoid O/L Farrell to Sheffield No. 2 220 kV line for trip of the Farrell to Sheffield No. 1 220 kV line with no SPS action, feedback | NIL | Tas
F_V+NIL_PTH03_R60 | $29 ($121) | 5.4 (9.6) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Raise 60 sec service | NIL | FCAS
F_Q++LDMU_R6 | $28 (0) | 2.3 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage | FCAS
F_T++CSGO_TG_R5 | $28 (0) | 0.3 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage | FCAS
V>SMLHORC1 | $26 (0) | 0.3 (0) | Out = Horsham to Red Cliffs 220kV line, avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line | Outage | Vic
V::N_2RP_xxx | $25 (0) | 0.9 (0) | Out = 2 dynamic reactive plant from Vic metro or SESS SVC's, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
F_T++FASH_N-2_TG_R60 | $25 (0) | 5.6 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
S>>X_TBTU+CB_TBCG_2 | $24 (0) | 0.1 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Snuggery - Keith 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage | SA
F_I+TL_L5_0450 | $24 ($0) | 8.7 (0.5) | Lower 5 min Service Requirement for a NEM Network Event, TL = 450 | Outage | FCAS
F_Q_MK_33BUS_R5 | $23 (0) | 1.1 (0) | Out=T38 Mackay 33kV C Bus (R5 Requirement) | Outage | FCAS
T>T_NIL_LIPM_N-2_2B | $22 ($1,280) | 0.5 (4.9) | Outage = Nil, Loss of both Liapootah to Waddamana to Palmerston 220 kV lines declared credible, avoid overloading the Palmerston to Waddamana 110 kV line (flow to South) for loss of both Liapootah to Waddamana to Palmerston 220 kV lines, feedback | NIL | Tas
S>>V_NIL_TBSE_KHSG | $22 (0) | 0.1 (0) | Out= Nil, avoid O/L Keith - Snuggery 132 kV on trip of Tailem Bend - South East 275kV line, Feedback | NIL | SA
F_T++FASH1_2C_TG_R5 | $22 (0) | 4.8 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
N>N-CHLS_TE_A1 | $22 (0) | 0.8 (0) | Out = Coffs Harbour to Lismore (89) 330 kV line, avoid overloading Tenterfield to Lismore (96L) 132 kV line on trip of Koolkhan to Lismore (967) 132 kV line | Outage | NSW
F_MAIN++RREG_0300 | $20 ($21) | 0.4 (0.8) | Mainland Raise Regulation Requirement greater than 300 MW, Basslink able transfer FCAS | Outage | FCAS
F_T++BLSPS_EXP_L6_1 | $20 (0) | 0.7 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
CA_SPS_41B7F9D7_01 | $19 (0) | 0.3 (0) | Constraint Automation, O/L 83 @LIDDELL for CTG LNPA on trip of TAMWORTH-LIDDELL 84 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage | Constraint Automation
T>T_HAPM_IMP_4K | $19 (0) | 0.2 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Georgetown No. 2 220 kV line (flow North) for trip of Hadspen to Georgetown No. 1 220 kV line with no NCSPS action, feedback | Outage | Tas
F_T++BLSPS_EXP_L60_1 | $19 (0) | 0.7 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage | FCAS
SVML_010 | $19 (0) | 0.3 (0) | SA to Vic on ML upper transfer limit of 10 MW | Outage | SA
N>>N-CNUT_HA | $19 (0) | 0.4 (0) | Out = Canberra-UpperTumut(1), avoid Upper Tumut to Lower Tumut(64) O/L on Upper Tumut to Yass(2) trip; Feedback | Outage | NSW
NQ_450 | $18 (0) | 0.3 (0) | NSW to Qld on QNI upper transfer limit of 450 MW | Outage | NSW
F_T++NIL_WF_TG_R60 | $18 (0) | 5.2 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL | FCAS
V>>V_SMTXF2_3P | $18 (0) | 0.8 (0) | Out = South Morang F2 500/330 kV txfmr, avoid O/L Richmond to Brunswick 220 kV cable on NIL trip, 3/5 parallel mode, feedback | Outage | Vic
V>>S_KHKN_SETB_SGKH | $18 ($4,341) | 0.4 (29.8) | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line | Outage | SA
V::N_JNWG_xxx | $18 (0) | 0.6 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage | Vic
F_Q++LDMU_R60 | $18 (0) | 1.7 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 60 sec Requirement | Outage | FCAS
F_T+BL_650_R5 | $17 ($91) | 1.6 (9.2) | Tasmania Raise 5 min Requirement for loss of Basslink, FCSPS available, LoL = 650 ms | Outage | FCAS
F_T_REECE2_R6 | $17 (0) | 0.8 (0) | Out= NIL, Reece 2 R6 Requirement <= 0MW | Outage | FCAS
F_I+DD_N-2_MG_R5 | $17 (0) | 2.3 (0) | Out= Nil, loss of all Darling Downs units declared credible, Global Raise 5 Min requirement | Outage | FCAS
F_V+NIL_PTH03_L5 | $16 ($67) | 5.0 (9.5) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
F_T++NIL_WF_TG_R5 | $16 (0) | 6.0 (0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL | FCAS
F_T++FARE_N-2_TG_R5 | $16 (0) | 3.8 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS | Outage | FCAS
T>>T_HAPM_EXP_3A | $16 (0) | 0.1 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage | Tas
T>T_PM_TX_1A | $15 (0) | 0.3 (0) | Out= Palmerston 220/110kV transformer, prevent overload of either Palmerston to Hadspen 110kV line (flow to North) for trip of the parallel Palmerston to Hadspen 110 kV line, feedback | Outage | Tas
F_I+RREG_0300 | $15 ($14) | 0.4 (0.7) | NEM Raise Regulation Requirement greater than 300 MW | Outage | FCAS
V>>N-DDWO_RADIAL_2 | $15 (0) | 0.3 (0) | Out = Dederang to Wodonga, avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
F_T++FASH1_2C_TG_R60 | $14 (0) | 0.8 (0) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage | FCAS
F_Q++ARTW_R5 | $13 (0) | 3.7 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage | FCAS
V>>N-CNUT_HB_15M | $13 (0) | 0.1 (0) | Out = Canberra-UpperTumut(1), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage | Vic
F_V+NIL_APD02_L5 | $12 ($28) | 5.0 (4.8) | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 5 Min service | NIL | FCAS
F_T_GORDON_R5 | $12 (0) | 2.2 (0) | Out= NIL, Gordon R5 Requirement <= 0MW | Outage | FCAS
N^^V_LTMS | $12 (0) | 0.1 (0) | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse for trip of the largest Vic generating unit or Basslink | Outage | NSW
N::Q_30+38_KC | $12 (0) | 0.9 (0) | Out= Liverpool-SydWest(30) + Regentville-SydWest(38) 330kV lines, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage | NSW
V>>V_KTS_TX_A2_2_P | $12 (0) | 0.8 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage | Vic
F_T+BL_650_R6_1 | $12 ($336) | 1.3 (27.4) | Tasmania Raise 6 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage | FCAS
V^^S_TB6594_35_SETB | $11 (0) | 1.0 (0) | Out= Tailem Bend 275kV CB6594 OR CB6535 O/S; Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage | SA
V^^S_TBCP_SETB | $11 (0) | 0.1 (0) | Out= Tailem Bend 275kV Cap Bank (Tungkillo 275kV Cap available); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line (Note: with NPS and Playford PS assumed to be O/S) (Swamp out if SA demand less/equal to 3200MW) | Outage | SA
F_ESTN++HYTR_L6 | $10 (0) | 4.6 (0) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage | FCAS
F_I+DD_N-2_MG_R6 | $10 (0) | 2.3 (0) | Out= Nil, loss of all Darling Downs units declared credible, Global Raise 6 sec requirement | Outage | FCAS
F_I+DD_N-2_MG_R60 | $10 (0) | 2.3 (0) | Out= Nil, loss of all Darling Downs units declared credible, Global Raise 60 sec requirement | Outage | FCAS
F_QNV++HYMO_L60 | $9 ($29) | 2.8 (10.0) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_MAIN++NIL_BL_R60 | $9 ($1) | 4.0 (0.3) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL | FCAS
T>T_HAPM_IMP_4B | $8 (0) | 0.1 (0) | Out = Hadspen to Palmerston No. 2 220 kV line, avoid O/L Hadspen to Palmerston No. 1 220 kV line (flow North) for trip of either Sheffield to Georgetown 220 kV line with no NCSPS action, feedback | Outage | Tas
F_MAIN++ML_L6_APD | $7 ($87) | 4.6 (24.8) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage | FCAS
F_T+FASH_N-2_TG_R5 | $7 (0) | 0.3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink unable to transfer FCAS | Outage | FCAS
F_T++BLSPS_EXP_L6_2 | $7 (0) | 0.2 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage | FCAS
F_V+NIL_APD01_L6 | $7 ($2) | 3.6 (2.5) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_I+TL_L60_0450 | $7 ($0) | 2.8 (0.3) | Lower 60 sec Service Requirement for a NEM Network Event, TL = 450 | Outage | FCAS
F_Q++MUTW_R6 | $7 (0) | 1.1 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage | FCAS
V>>V_HWPS-RO_3-5_4 | $6 (0) | 0.3 (0) | Out = Hazelwood to Rowville No.1 or No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, void O/L Hazelwood #1 or #2 500/220kV transformer for loss of either transformer | Outage | Vic
N>N-X_8505_9U6_1 | $6 (0) | 1.0 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 66kV line between Mullumbimby and Ballina (8505,8508 or 8504), avoid O/L remaining 132kV line, NSW to Qld limit | Outage | NSW
F_T+CSGO_TG_R5 | $6 (0) | 0.8 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
F_V+NIL_APD01_L60 | $6 ($3) | 2.8 (2.4) | Out=Nil, limit APD01 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
N>>N-NIL_1A_CLOSED | $6 (0) | 0.2 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL | NSW
T>T_HAPM_110_IMP_4D | $6 (0) | 0.1 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L a Palmerston to Hadspen No. 2 220kV line (flow to North) for trip of the Palmerston to Hadspen No. 1 220kV line with no NCSPS action, feedback | Outage | Tas
N>N-LS_TX_TE_B | $6 (0) | 0.3 (0) | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. DS only | Outage | NSW
Q>CLWU_CLST | $6 (0) | 0.1 (0) | Constraint Automation, O/L 275KV_855 @H24_CALV for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage | Qld
F_T+BL_CO_N-2_L60 | $6 (0) | 13.4 (0) | Out= Nil, Tasmania Lower 60 second Requirement for loss of Basslink and a Comalco potline declared credible | Outage | FCAS
N_MBTE1_B | $5 ($10,412) | 0.3 (157.6) | Out = one Directlink cable, Queensland to NSW limit | Outage | NSW
Q>NIL_MUTE_757 & Q>NIL_MUTE_758 | $5 ($3,551) | 0.6 (90.0) | Out = Nil, avoid overloading a Mudgeeraba to Terranora (757 or 758) 110 kV line on no contingencies These constraint equations are dependent on the Terranora load as well as all 3 cables of Directlink being in service. In May 2011 the constraint equation Q>NIL_757+758_B was replaced with two constraint equations Q>NIL_MUTE_757 and Q>NIL_MUTE_758. The binding results for each have been combined. | NIL | Qld
V^SML_NIL_3 | $5 ($26) | 0.6 (0.2) | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW | NIL | Vic
F_MAIN+ML_L60_APD | $5 ($201) | 2.0 (26.0) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
F_V+NIL_PTH02_L6 | $5 ($9) | 3.8 (5.0) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_MAIN+ML_L6_APD | $5 ($160) | 2.0 (26.0) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink unable transfer FCAS | Outage | FCAS
T>T_HAPM_IMP_4H | $4 (0) | 0.1 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Georgetown No. 1 220 kV line (flow North) for trip of Hadspen to Georgetown No. 2 220 kV line with no NCSPS action, feedback | Outage | Tas
F_V+NIL_PTH01_L60 | $4 ($14) | 3.7 (8.1) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_V+NIL_PTH02_L60 | $4 ($24) | 3.2 (7.5) | Out=Nil, limit PTH02 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_I+TL_L60_0500 | $3 (0) | 6.3 (0) | Lower 60 sec Service Requirement for a NEM Network Event, TL = 500 | Outage | FCAS
F_T++NIL_BLSPS_L5 | $3 ($3) | 0.9 (1.0) | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL | FCAS
F_V+NIL_PTH01_L6 | $3 ($9) | 3.8 (7.1) | Out=Nil, limit PTH01 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_Q++MUTW_R60 | $3 (0) | 0.5 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 60 sec Requirement | Outage | FCAS
F_T_FISH_R6 | $2 (0) | 0.7 (0) | Out=Sheffield-Fisher 220KV line. R6 <= 0MW | Outage | FCAS
F_ESTN++MLSY_L6 | $2 (0) | 3.4 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 6 sec Requirement | Outage | FCAS
T>T_GTHA_2G | $2 (0) | 0.6 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L remaining Hadspen to George Town 220 kV line (flow to George Town) for trip of a Sheffield to George Town 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
V>>N-MSUT_2 | $2 (0) | 0.1 (0) | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage | Vic
V>>V_ROTS_TX_2_P | $2 (0) | 0.2 (0) | Out= Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage | Vic
F_QNV++HYTR_L60 | $2 ($0) | 1.7 (0.1) | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
V^^S_KHKN_MAXG | $2 ($724) | 0.2 (5.9) | Out= Keith - Kincraig 132 kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage | SA
F_NVS++ARTW_L60 | $2 (0) | 1.3 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_T++NIL_BB_TG_R6 | $2 (0) | 0.6 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS | NIL | FCAS
F_MAIN++TL_L5_0500 | $2 (0) | 1.5 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage | FCAS
F_T++NIL_BLSPS_L60_2 | $2 ($1) | 0.7 (0.8) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL | FCAS
F_T++COGT_TL_L60 | $2 ($5) | 3.5 (6.7) | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage | FCAS
N>N-NIL_TE_E2 | $2 (0) | 0.2 (0) | Out= Nil, avoid Koolkhan to Lismore (967) O/L on CoffsHarbour - Lismore (89) trip; Feedback, TG formulation in PD/ST | NIL | NSW
F_Q++LDMU_R5 | $2 (0) | 0.5 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage | FCAS
F_T+CSGO_TG_R6 | $1 (0) | 0.2 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink unable to transfer FCAS | Outage | FCAS
F_QNV++MLSY_L60 | $1 (0) | 0.6 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_ESTN++MLTR_L60 | $1 ($34) | 0.6 (8.9) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage | FCAS
F_T++BLSPS_EXP_L5 | $1 (0) | 0.7 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage | FCAS
F_ESTN++HYMO_L60 | $1 ($106) | 3.0 (69.8) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage | FCAS
F_T+BL_650_R60_1 | $1 ($88) | 0.4 (20.2) | Tasmania Raise 60 second Requirement for loss of Basslink, Segment 1, FCSPS available, LoL = 650 ms | Outage | FCAS
F_ESTN++MLTR_L5 | $1 ($46) | 0.3 (9.6) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Eastern Lower 5 min Requirement | Outage | FCAS
F_V+NIL_PTH03_L6 | $1 ($3) | 1.2 (3.8) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_T++COGT_TL_L6 | $1 ($1) | 3.5 (1.6) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage | FCAS
F_V+NIL_PTH03_L60 | $1 ($5) | 0.7 (4.3) | Out=Nil, limit PTH03 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_STHN++ARTW_L60 | $0 (0) | 1.4 (0) | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage | FCAS
V^^S_NIL_MAXG-10MW | $0 (0) | 0.1 (0) | System normal limit -10 MW offset; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. (South East Capacitor Available) | NIL | SA
F_T++NIL_WN_TG_R5 | $0 ($42) | 0.5 (5.6) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL | FCAS
F_QNV++HYMO_L5 | $0 ($42) | 0.1 (7.8) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_ESTN++HYMO_L5 | $0 ($120) | 0.1 (50.4) | Out = Heywood to Mortlake (HYTS-MOPS) line Eastern Lower 5 min Requirement | Outage | FCAS
N^^V_DDMB_1 | $0 ($169) | 0.1 (1.9) | Out = Dederang to Mt Beauty 220 kV line, avoid voltage collapse for trip of the largest Vic generating unit or Basslink | Outage | NSW
F_T++NIL_BLSPS_L60_1 | $0 ($0) | 0.4 (0.2) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL | FCAS
T>T_GTSH_2A | $0 ($98) | 0.1 (1.6) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen 220 kV line (flow North) for trip of other Palmerston to Hadspen 220 kV line considering NCSPS action, ensure sufficient NCSPS generation dispatched. | Outage | Tas
F_T++NIL_WN_TG_R60 | $0 ($174) | 1.7 (32.8) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL | FCAS
F_T+BL_CO_N-2_L5 | $0 (0) | 0.1 (0) | Out= Nil, Tasmania Lower 5 min Requirement for loss of Basslink and a Comalco potline declared credible | Outage | FCAS
F_QNV++MLTR_L60 | $0 (0) | 0.2 (0) | Out = Moorabool to Tarrone (MLTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage | FCAS
F_V+NIL_APD02_L6 | $0 (0) | 0.3 (0) | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 6 sec service | NIL | FCAS
F_T++NIL_ML_L60 | $0 ($0) | 0.1 (0.3) | Out = Nil, Lower 60 sec requirement for a Tasmania Load Event, Basslink able to transfer FCAS | NIL | FCAS
F_V+NIL_APD02_L60 | $0 (0) | 0.2 (0) | Out=Nil, limit APD02 to zero MW when potline is tripped for Lower 60 sec service | NIL | FCAS
F_T_GORDON_R60 | $0 (0) | 0.4 (0) | Out= NIL, Gordon R60 Requirement <= 0MW | Outage | FCAS
F_STHN++LDTW_L60 | $0 ($0) | 0.2 (1.4) | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage | FCAS
F_QNV++MLSY_L5 | $0 (0) | 0.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage | FCAS
T>T_NIL_BL_IMP_7C | $0 ($20,781) | 0.1 (63.9) | Out = Nil, avoid overloading Farrell to Sheffield No.1 220 kV line for trip of the Farrell to Sheffield No.2 220 kV line with no SPS action | NIL | Tas
F_NVS+ARTW_L60 | $0 (0) | 0.3 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage | FCAS
T>T_HAPM_110_IMP_4P | $0 (0) | 0.1 (0) | Out = Hadspen to Palmerston No. 4 110 kV line, avoid O/L of Palmerston to Hadspen No. 3 110 kV line (flow to North) for trip of the Palmerston 220/110 kV transformer with no NCSPS action, feedback | Outage | Tas
F_T++NIL_BB_TG_R60 | $0 (0) | 0.1 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS | NIL | FCAS

## Interconnector Binding 2013
Interconnector Direction | Constraint Equation ID | 2013 Hours (2012 Hours) | Description | Type
N-Q-MNSP1 Export | N_X_MBTE_3A | 1429.3 (42.3) | Out = all three Directlink cables, NSW to Queensland limit All three Directlink cables was out for 158.1 days in 2013 compared to 20.9 days in 2012 | Outage
N-Q-MNSP1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 194.4 (66.9) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
N-Q-MNSP1 Export | N>N-NIL_LSDU | 122.7 (53.9) | Out = Nil, avoid overloading Lismore to Dunoon line (9U6 or 9U7) 132 kV line on trip of the other Lismore to Dunoon line (9U7 or 9U6) 132 kV line | NIL
N-Q-MNSP1 Export | N_X_MBTE2_A | 121.5 (43.2) | Out = two Directlink cables, NSW to Queensland limit Two Directlink cables was out for 214.9 days in 2013 compared to 60.0 days in 2012 | Outage
N-Q-MNSP1 Export | N^N_KKLS_1 | 74.3 (18.0) | Out = Koolkhan to Lismore (967) 132 kV line, avoid voltage collapse on trip of Coffs Harbour to Lismore (89) 330 kV line Tripping of 89 line only leaves Lismore connected by the Tenterfield to Lismore (96L) 132 kV line. 96L is the weaker of the 2 lines into Lismore and support is usually required from Terranora interconnector. AEMO expects this constraint equation will continue bind for a reasonable portion of any future outage times. The Koolkhan to Lismore (967) 132 kV line was out for 3.8 days in 2013 compared to 9.1 days in 2012 | Outage
N-Q-MNSP1 Export | N^Q_NIL_A | 21.5 (0) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
N-Q-MNSP1 Export | F_Q++ARTW_R6 | 17.6 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement The Armidale to Tamworth (86) 330 kV line was out for 4.7 days in 2013 compared to 2.0 days in 2012 | Outage
N-Q-MNSP1 Export | NQTE_ROC | 16.4 (25.0) | Out = Nil, rate of change (NSW to Queensland) limit (80 MW / 5 minute) for Terranora interconnector | NIL
N-Q-MNSP1 Export | N^N_CHLS_1 | 13.5 (0.5) | Out = Coffs Harbour to Lismore (89) 330 kV line, avoid voltage collapse on trip of Koolkhan to Lismore 132 kV line (967) The Coffs Harbour to Lismore (89) 330 kV line was out for 2.2 days in 2013 compared to 1.3 days in 2012 | Outage
N-Q-MNSP1 Export | N>N-EWMB_TE_A | 12.9 (32.3) | Out = Ballina to Lennox Head 66 kV line, avoid overloading Lismore to Dunoon 132 kV line on trip of the other Lismore to Dunoon 132 kV line One Ballina to Lennox Head to Ewingsdale to Mullumbimby 66 kV line (8504, 8505 or 8508) or Mullumbimby 132/66 kV transformer was out for 15.9 days in 2013 compared to 58.3 days in 2012 | Outage
N-Q-MNSP1 Export | N^^Q_MPP_N-2 | 12.6 (0) | Out = Nil, avoid Voltage Collapse on trip of Millmerran 1 & 2 declared credible | Outage
N-Q-MNSP1 Export | F_Q++LDTW_R6 | 10.8 (1.8) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
N-Q-MNSP1 Export | N>N-GITN_TE_C1 | 7.8 (5.0) | Out = Glen Innes to Tenterfield (96R) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | I_CTRL_ISSUE_TE | 3.8 (0) | DC Link Control Issue Constraint for Terranora | Outage
N-Q-MNSP1 Export | N>N-ARGI_TE_C1 | 3.7 (0) | Out= Armidale to Glen Innes (96T), avoid O/L Koolkhan to Lismore (967) on trip of Coffs Harbour to Lismore (89), Swamp out when all 3 Directlink cable O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | N^Q_ARTW_1 | 3.2 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator | Outage
N-Q-MNSP1 Export | N^^Q_BCDM_B1 | 3.1 (0) | Out = One Bulli Creek - Dumaresq (8L or 8M) 330 kV line, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | N^N-89_LSTX_SVC | 2.8 (3.4) | Out = Coffs Harbour to Lismore (89) 330 kV line and Lismore 330/132 kV transformer with Lismore SVC in reactive power control mode, avoid voltage collapse on trip of Koolkhan to Lismore (967) 132 kV line | Outage
N-Q-MNSP1 Export | N>Q_LSLS_9U8 | 2.7 (8.9) | Out = one Lismore 330 to Lismore 132 lines (9U8 or 9U9 or 9W1) 132 kV lines, avoid overloading on one Lismore 330 to Lismore 132 line on loss of the remaining line | Outage
N-Q-MNSP1 Export | N>Q-MUTW_2 | 2.2 (0) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage
N-Q-MNSP1 Export | N^^Q_ARTW_MPP_N-2 | 2.0 (0) | Out = Armidale to Tamworth (85 or 86) and trip of both Millmerran units declare credible, avoid Voltage collapse on loss of both Millmerran units | Outage
N-Q-MNSP1 Export | F_Q++LDMU_R6 | 1.9 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-ARCH_87_TE_C1 | 1.5 (0) | Out= Armidale - Coffs Harbour (87), avoid O/L Armidale to Koolkhan (966) on trip of Armidale to Coffs Harbour (96C), swamp out when all 3 directlink O/S, Feedback, TG formulation in PD/ST | Outage
N-Q-MNSP1 Export | #N-Q-MNSP1_I_E | 1.2 (6.3) | Quick constraint equation applied to Terranora Interconnector at various levels | Outage
N-Q-MNSP1 Export | F_Q++ARTW_R5 | 1.2 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | N>N-X_8505_9U6_1 | 1.0 (0) | Out= one of Lismore 132 to Dunoon 132kV line (9U6 or 9U7) and one 66kV line between Mullumbimby and Ballina (8505,8508 or 8504), avoid O/L remaining 132kV line, NSW to Qld limit | Outage
N-Q-MNSP1 Export | N::Q_30+38_KC | 0.9 (0) | Out= Liverpool-SydWest(30) + Regentville-SydWest(38) 330kV lines, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
N-Q-MNSP1 Export | N>>N-NIL_1A_OPENED | 0.9 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
N-Q-MNSP1 Export | N>N-ARTW86_1B | 0.9 (0) | Out = Armidale to Tamworth (86) 330 kV line, avoid overloading Tamworth to Armidale (85) 330 kV line on trip of largest Queensland generator | Outage
N-Q-MNSP1 Export | N>N-CHLS_TE_A1 | 0.8 (0) | Out = Coffs Harbour to Lismore (89) 330 kV line, avoid overloading Tenterfield to Lismore (96L) 132 kV line on trip of Koolkhan to Lismore (967) 132 kV line | Outage
N-Q-MNSP1 Export | N>N-LSTN_TE_C1 | 0.8 (5.3) | Out = Lismore to Tenterfield (96L) 132 kV line, avoid overloading Koolkhan to Lismore (967) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | F_NVS++ARTW_L60 | 0.8 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
N-Q-MNSP1 Export | N>>N-RGSW_A | 0.7 (0) | Out = Regentville to Sydney West(38), avoid Bayswater to Liddell(34) O/L on Bayswater to Liddell(33) trip; Feedback | Outage
N-Q-MNSP1 Export | N>N-KKLS_TE_2 | 0.7 (1.0) | Out = Koolkhan to Lismore (967) 132 kV line, avoid overloading the Armidale to Glen Innes (96T) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | #R008110_001_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Export | #R008129_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008357_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | N>LSDU9U6_LSDU9U7 | 0.6 (0) | Constraint Automation, O/L 9U7/L @LISM132 for CTG LN9X on trip of LISM132-DUNOON 9U6/L 132KV LINE. Generated by RTCA[EMS] | Outage
N-Q-MNSP1 Export | #R008345_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008633_003_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N^N_CHLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008881_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 03/01/2008, Version: 1 | Outage
N-Q-MNSP1 Export | F_Q++MUTW_R6 | 0.5 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-NIL__4_15M | 0.5 (1.2) | Out = Nil, avoid overloading Muswellbrook to Tamworth (88) 330 kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL
N-Q-MNSP1 Export | #R008660_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N-89_LSTX_SVC, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008708_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008735_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008757_002_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008345_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008357_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008599_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008615_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 01/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008653_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^^Q_ARTW_MPP_N-2, Effective Date: 07/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008668_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N-89_LSTX_SVC, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008685_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 09/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008705_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008735_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008757_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008992_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Export | #R009021_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Export | F_Q++LDMU_R5 | 0.3 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage
N-Q-MNSP1 Export | F_STHN++ARTW_L60 | 0.3 (0) | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage
N-Q-MNSP1 Export | #R008422_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 03/01/2008, Version: 1 | Outage
N-Q-MNSP1 Export | #R008609_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008619_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N>>N-RGSW_A, Effective Date: 06/05/2011, Version: 2 | Outage
N-Q-MNSP1 Export | #R008619_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>>N-RGSW_A, Effective Date: 06/05/2011, Version: 2 | Outage
N-Q-MNSP1 Export | #R008633_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N_CHLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008642_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 01/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008660_001_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^N-89_LSTX_SVC, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008747_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | F_NVS+ARTW_L60 | 0.3 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
N-Q-MNSP1 Export | N>N-CHKK_TE_1 | 0.3 (0.4) | Out = Coffs Harbour to Koolkhan (96H) 132 kV line, avoid overloading Armidale to Koolkhan (966) 132 kV line on trip of Coffs Harbour to Lismore (89) 330 kV line | Outage
N-Q-MNSP1 Export | N_MBTE1_A | 0.3 (0.2) | Out= one Directlink cable, NSW to Qld limit | Outage
N-Q-MNSP1 Export | #R008129_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N>N-LSTN_TE_C1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008320_005_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^Q_ARTW_1, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008562_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Export | #R008599_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008653_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^^Q_ARTW_MPP_N-2, Effective Date: 07/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008683_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N>N-GITN_TE_C1, Effective Date: 25/03/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008708_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008746_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 03/01/2008, Version: 1 | Outage
N-Q-MNSP1 Export | #R008900_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N:Q_LDTW_1, Effective Date: 14/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008900_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N:Q_LDTW_1, Effective Date: 14/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | N>N-LS_TX_TE_B | 0.2 (0) | Out= Lismore No.1 or No.2 330/132 Transformer, avoid O/L Koolkhan to Lismore (967) on trip of remaining Lismore 330/132kV transformer, Feedback. DS only | Outage
N-Q-MNSP1 Export | N^^Q_LS_VC_B1 | 0.2 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
N-Q-MNSP1 Export | #R008291_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Export | #R008409_005_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^Q_LS_VC_B3, Effective Date: 03/01/2008, Version: 1 | Outage
N-Q-MNSP1 Export | #R008415_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 03/01/2008, Version: 1 | Outage
N-Q-MNSP1 Export | #R008417_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>Q_LSLS_9U8, Effective Date: 10/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008422_003_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 03/01/2008, Version: 1 | Outage
N-Q-MNSP1 Export | #R008609_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 08/03/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008615_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 01/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008642_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 01/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008685_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N>N-KKLS_TE_2, Effective Date: 09/05/2013, Version: 1 | Outage
N-Q-MNSP1 Export | #R008705_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^N_KKLS_1, Effective Date: 14/02/2012, Version: 1 | Outage
N-Q-MNSP1 Export | #R008992_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3A, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Export | F_STHN++LDTW_L60 | 0.1 (0.1) | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage
N-Q-MNSP1 Export | N>N-NIL_TE_E2 | 0.1 (0) | Out= Nil, avoid Koolkhan to Lismore (967) O/L on CoffsHarbour - Lismore (89) trip; Feedback, TG formulation in PD/ST | NIL
N-Q-MNSP1 Import | N_X_MBTE_3B | 2343.7 (460.8) | Out = all three Directlink cables, Queensland to NSW limit All three Directlink cables was out for 158.1 days in 2013 compared to 20.9 days in 2012 | Outage
N-Q-MNSP1 Import | N_X_MBTE2_B | 74.7 (439.8) | Out = two Directlink cables, Queensland to NSW limit Two Directlink cables was out for 214.9 days in 2013 compared to 60.0 days in 2012 | Outage
N-Q-MNSP1 Import | NRM_QLD1_NSW1 | 28.4 (16.6) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL
N-Q-MNSP1 Import | QNTE_ROC | 11.9 (18.3) | Out = Nil, Rate of Change (Qld to NSW) constraint (80 MW / 5 Min) for Terranora Interconnector | NIL
N-Q-MNSP1 Import | Q_CS_1100 | 8.8 (0) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer The Calvale to Tarong 275 kV line was out for 36.0 days in 2013 compared to 10.5 days in 2012 | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L6 | 7.2 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L6 | 6.4 (31.1) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement The Armidale to Tamworth (86) 330 kV line was out for 4.7 days in 2013 compared to 2.0 days in 2012 | Outage
N-Q-MNSP1 Import | F_Q++ARTW_L5 | 3.0 (26.3) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement The Armidale to Tamworth (86) 330 kV line was out for 4.7 days in 2013 compared to 2.0 days in 2012 | Outage
N-Q-MNSP1 Import | F_Q++LDTW_L5 | 2.5 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
N-Q-MNSP1 Import | #N-Q-MNSP1_RAMP_I_F | 0.8 (1.2) | Quick interconnector ramping constraint equation applied to Terranora Interconnector at various levels | Outage
N-Q-MNSP1 Import | N_MBTE1_B | 0.6 (157.8) | Out = one Directlink cable, Queensland to NSW limit | Outage
N-Q-MNSP1 Import | #R008992_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 21/03/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R008110_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Import | #R008291_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Import | #R009021_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 21/03/2013, Version: 1 | Outage
N-Q-MNSP1 Import | #R008291_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 20/12/2011, Version: 1 | Outage
N-Q-MNSP1 Import | #R008562_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 21/03/2013, Version: 1 | Outage
N-Q-MNSP1 Import | Q>>NIL_MRTX5_MRTX4 | 0.2 (1.8) | Out = Nil, avoid overloading Middle Ridge No.4 330/275 kV transformer on trip of Middle Ridge No.5 330/275 kV transformer | NIL
N-Q-MNSP1 Import | #R009021_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N_X_MBTE_3B, Effective Date: 21/03/2013, Version: 1 | Outage
NSW1-QLD1 Export | N^^Q_NIL_B1, 2, 3, 4, 5, 6 & N^Q_NIL_B | 516.8 (99.5) | Out = Nil, avoid voltage collapse for loss of the largest Queensland generator | NIL
NSW1-QLD1 Export | Q>>NIL_855_871 | 267.3 (276.2) | Out = Nil, avoid overload on Calvale to Wurdong (871) 275 kV line on trip of Calvale to Stanwell (855) 275 kV line | NIL
NSW1-QLD1 Export | N^Q_NIL_A | 32.7 (0.1) | Out = Nil, avoid Voltage Collapse on loss of Liddell to Muswellbrook (83) 330 kV line | NIL
NSW1-QLD1 Export | F_Q++ARTW_R6 | 22.5 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland raise 6 second requirement The Armidale to Tamworth (86) 330 kV line was out for 9.4 days in 2013 compared to 4.0 days in 2012 | Outage
NSW1-QLD1 Export | Q>>NIL_871_855 | 20.2 (98.3) | Out = Nil, avoid overload on Calvale to Stanwell (855) 275 kV line on trip of Calvale to Wurdong (871) 275 kV line | NIL
NSW1-QLD1 Export | N^^Q_MPP_N-2 | 16.0 (0) | Out = Nil, avoid Voltage Collapse on trip of Millmerran 1 & 2 declared credible | Outage
NSW1-QLD1 Export | N^Q_ARTW_1 | 12.8 (0) | Out = Armidale to Tamworth (85 or 86) 330 kV line, avoid voltage collapse on trip of largest Queensland generator The Armidale to Tamworth (85) 330 kV line was out for 9.7 days in 2013 compared to 4.7 days in 2012 | Outage
NSW1-QLD1 Export | F_Q++LDTW_R6 | 10.8 (1.3) | Out = Liddell to Tamworth (84) 330 kV line, Queensland raise 6 second requirement | Outage
NSW1-QLD1 Export | N^^Q_BCDM_B1 | 3.8 (0) | Out = One Bulli Creek - Dumaresq (8L or 8M) 330 kV line, avoid Voltage Collapse on loss of Kogan Creek One Bulli Creek to Dumaresq 330 kV line was out for 1.1 days in 2013 compared to 0 days in 2012 | Outage
NSW1-QLD1 Export | N::Q_BWMP_KC | 3.4 (0) | Out = Bayswater to Mt Piper(5A3) 500 kV line or Bayswater to Wollar(5A4) 500 kV line or Wollar to Mt. Piper (5A5) 500 kV line, NSW to Qld Transient Stability Limit for trip of Kogan Creek The Bayswater to Mt. Piper or Bayswater to Wollar or Wollar to Mt. Piper 500 kV line was out for 2.5 days in 2013 compared to 0.2 days in 2012 | Outage
NSW1-QLD1 Export | N^^Q_ARDM_B1 | 3.3 (7.3) | Out = one Armidale to Dumaresq 330 kV line, avoid voltage collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | N>N-NIL__4_15M | 2.8 (1.2) | Out = Nil, avoid overloading Muswellbrook to Tamworth (88) 330 kV line on trip of Liddell to Tamworth (84) 330 kV line | NIL
NSW1-QLD1 Export | N^^Q_ARTW_MPP_N-2 | 2.4 (0) | Out = Armidale to Tamworth (85 or 86) and trip of both Millmerran units declare credible, avoid Voltage collapse on loss of both Millmerran units | Outage
NSW1-QLD1 Export | N>Q-MUTW_2 | 2.1 (0) | Out= Muswellbrook-Tamworth(88), avoid Liddell->Tamworth(84) OL on trip of QLD largest generation; Fb | Outage
NSW1-QLD1 Export | Q>>NIL_871_855_POST | 2.1 (0) | Out = Nil, Post-8868 commissioning, avoid overload on Calvale to Stanwell (855) 275kV line on trip of Calvale to Wurdong (871) 275kV line, Feedback | NIL
NSW1-QLD1 Export | F_Q++LDMU_R6 | 1.9 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | Q>>BRTR_MRTX5_MRTX4 | 1.9 (0) | Out = Braemar to Tarong (8814 or 8815) 275 kV line, avoid overloading Middle Ridge 330/275 kV No.4 transformer, on trip of Middle Ridge 330/275 kV No.5 transformer | Outage
NSW1-QLD1 Export | #NSW1-QLD1_E_E | 1.7 (0) | NSW1-QLD1.ENERGY * 1 <= 125 (Wt = 20) | Outage
NSW1-QLD1 Export | F_Q++ARTW_R5 | 1.2 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | N>>N-RGSW_A | 1.2 (0) | Out = Regentville to Sydney West(38), avoid Bayswater to Liddell(34) O/L on Bayswater to Liddell(33) trip; Feedback | Outage
NSW1-QLD1 Export | CA_SPS_41B92B29_02 | 1.0 (0) | Constraint Automation, O/L 84 @LIDDELL for CTG LNPF on trip of LIDDELL-MUSBK330 83 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
NSW1-QLD1 Export | N::Q_30+38_KC | 0.9 (0) | Out= Liverpool-SydWest(30) + Regentville-SydWest(38) 330kV lines, NSW to Qld Transient Stability Limit for trip of Kogan Creek. | Outage
NSW1-QLD1 Export | N>N-ARTW86_1B | 0.9 (0) | Out = Armidale to Tamworth (86) 330 kV line, avoid overloading Tamworth to Armidale (85) 330 kV line on trip of largest Queensland generator | Outage
NSW1-QLD1 Export | #NSW1-QLD1_I_E | 0.8 (0) | NSW1-QLD1.ENERGY * -1 >= 100 (Wt = 20) | Outage
NSW1-QLD1 Export | N>>N-NIL_1A_OPENED | 0.8 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
NSW1-QLD1 Export | Q>>NIL_855_871_POST | 0.8 (0) | Out = Nil, Post-8868 commissioning, avoid overload on Calvale to Wurdong (871) 275kV line on trip of Calvale to Stanwell (855) 275kV line, Feedback | NIL
NSW1-QLD1 Export | F_NVS++ARTW_L60 | 0.8 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
NSW1-QLD1 Export | #R008653_002_RAMP_F | 0.7 (0) | Hard Ramping constraint for constraint N^^Q_ARTW_MPP_N-2, Effective Date: 07/05/2013, Version: 1 | Outage
NSW1-QLD1 Export | F_Q++MUTW_R6 | 0.6 (0) | Out = Muswellbrook to Tamworth (88) line, Qld Raise 6 sec Requirement | Outage
NSW1-QLD1 Export | N^^Q_AR_VC_B1 | 0.6 (0) | Out= Armidale SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | #R008881_002_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | CA_SPS_41B7F9D7_02 | 0.4 (0) | Constraint Automation, O/L 84 @LIDDELL for CTG LNPF on trip of LIDDELL-MUSBK330 83 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
NSW1-QLD1 Export | #R009462_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^Q_ARTW_1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R009462_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^Q_ARTW_1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | CA_SPS_41B7F9D7_01 | 0.3 (0) | Constraint Automation, O/L 83 @LIDDELL for CTG LNPA on trip of TAMWORTH-LIDDELL 84 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
NSW1-QLD1 Export | F_Q++LDMU_R5 | 0.3 (0) | Out = Liddell to Muswellbrook (83) line, Qld Raise 5 min Requirement | Outage
NSW1-QLD1 Export | F_STHN++ARTW_L60 | 0.3 (0) | Out = Armidale to Tamworth (85 or 86) line, Southern Lower 60 sec Requirement | Outage
NSW1-QLD1 Export | NQ_450 | 0.3 (0) | NSW to Qld on QNI upper transfer limit of 450 MW | Outage
NSW1-QLD1 Export | #R008422_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | #R008619_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N>>N-RGSW_A, Effective Date: 06/05/2011, Version: 2 | Outage
NSW1-QLD1 Export | #R008619_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>>N-RGSW_A, Effective Date: 06/05/2011, Version: 2 | Outage
NSW1-QLD1 Export | #R008746_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | F_NVS+ARTW_L60 | 0.3 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink unable to transfer FCAS | Outage
NSW1-QLD1 Export | N>>N-NIL__3_15M | 0.3 (0) | Out= NIL, avoid O/L Liddell to Muswellbrook (83) on trip of Liddell to Tamworth (84) line, Feedback | NIL
NSW1-QLD1 Export | #R008320_005_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^Q_ARTW_1, Effective Date: 08/03/2012, Version: 1 | Outage
NSW1-QLD1 Export | #R008409_005_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^^Q_LS_VC_B3, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | #R008415_003_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^^Q_LS_VC_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | #R008422_003_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^^Q_AR_VC_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | #R008653_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N^^Q_ARTW_MPP_N-2, Effective Date: 07/05/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R008900_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N:Q_LDTW_1, Effective Date: 14/05/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R008900_001_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint N:Q_LDTW_1, Effective Date: 14/05/2013, Version: 1 | Outage
NSW1-QLD1 Export | #R009480_005_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint N^Q_ARTW_1, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | N>>N-NIL__2_15M | 0.2 (0) | Out= NIL, avoid O/L Liddell to Tamworth (84) on trip of Liddell to Muswellbrook (83) line, Feedback | NIL
NSW1-QLD1 Export | N^^Q_LS_VC_B1 | 0.2 (0) | Out= Lismore SVC, avoid Voltage Collapse on loss of Kogan Creek | Outage
NSW1-QLD1 Export | #R008746_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | #R008753_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^Q_BCDM_B1, Effective Date: 03/01/2008, Version: 1 | Outage
NSW1-QLD1 Export | #R009426_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N::Q_BWMP_KC, Effective Date: 21/08/2013, Version: 1 | Outage
NSW1-QLD1 Export | CA_SPS_41B92B29_01 | 0.1 (0) | Constraint Automation, O/L 83 @LIDDELL for CTG LNPA on trip of TAMWORTH-LIDDELL 84 330KV LINE. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
NSW1-QLD1 Export | F_Q++ARTW_R60 | 0.1 (0) | Out = Armidale to Tamworth (85 or 86) line, Qld Raise 60 sec Requirement | Outage
NSW1-QLD1 Export | F_STHN++LDTW_L60 | 0.1 (0.2) | Out = Liddell to Tamworth (84) line, Southern Lower 60 sec Requirement | Outage
NSW1-QLD1 Export | N>>N-NIL_1A_CLOSED | 0.1 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
NSW1-QLD1 Export | Q>CLWU_CLST | 0.1 (0) | Constraint Automation, O/L 275KV_855 @H24_CALV for CTG LQIV on trip of 871 H24_CALV - H40_WURD 275KV. Generated by RTCA[EMS] | Outage
NSW1-QLD1 Import | NRM_QLD1_NSW1 | 30.3 (19.4) | Negative Residue Management constraint equation for QLD to NSW flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL
NSW1-QLD1 Import | F_Q++ARDM_L6 | 10.7 (1.6) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 6 second requirement One Bulli Creek to Dumaresq 330 kV line - FCAS Requirements was out for 2.2 days in 2013 compared to 0 days in 2012 | Outage
NSW1-QLD1 Import | Q_CS_1100 | 8.7 (0) | Discretionary limit of 1100 MW on Qld Central to Qld South transfer The Calvale to Tarong 275 kV line was out for 18.0 days in 2013 compared to 5.3 days in 2012 | Outage
NSW1-QLD1 Import | F_Q++LDTW_L6 | 7.1 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 6 second requirement | Outage
NSW1-QLD1 Import | F_Q++ARTW_L6 | 6.9 (31.2) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 6 second requirement The Armidale to Tamworth (86) 330 kV line was out for 9.4 days in 2013 compared to 4.0 days in 2012 | Outage
NSW1-QLD1 Import | Q:N_NIL_BCK2L-G | 4.4 (113.5) | Out = Nil, avoid transient instability for a 2 phase to ground fault on a Bulli Creek to Dumaresq 330 kV line at Bulli Creek For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_OSC will bind. | NIL
NSW1-QLD1 Import | F_Q++ARTW_L5 | 3.0 (26.3) | Out = Armidale to Tamworth (85 or 86) 330 kV line, Queensland lower 5 minute requirement The Armidale to Tamworth (86) 330 kV line was out for 9.4 days in 2013 compared to 4.0 days in 2012 | Outage
NSW1-QLD1 Import | F_Q++ARDM_L5 | 2.5 (0.9) | Out = One Armidale to Bulli Creek (8C, 8E, 8L or 8M) 330 kV line, Queensland lower 5 minute requirement One Bulli Creek to Dumaresq 330 kV line - FCAS Requirements was out for 2.2 days in 2013 compared to 0 days in 2012 | Outage
NSW1-QLD1 Import | F_Q++LDTW_L5 | 2.5 (0) | Out = Liddell to Tamworth (84) 330 kV line, Queensland lower 5 minute requirement | Outage
NSW1-QLD1 Import | Q:N_NIL_OSC | 2.1 (22.7) | Out = Nil, Queensland to NSW oscillatory stability limit This constraint equation sets the upper limit from Queensland to NSW to 1078 MW. For high flows from Queensland to NSW either this constraint equation or Q:N_NIL_BI_POT or Q:N_NIL_BCK2L-G will bind. | NIL
NSW1-QLD1 Import | #NSW1-QLD1_RAMP_I_F | 0.8 (3.3) | NSW1-QLD1 >= MIN(-130, InitialFlow + 200) (Wt=20) | Outage
NSW1-QLD1 Import | Q_N_NIL-1078 | 0.3 (30.4) | Out = Nil, reduce QNI when it is over the 1078 MW limit by 1078 minus the MW over the 1078 MW limit (capped at 1000 MW) | NIL
NSW1-QLD1 Import | #R008176_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYSEQD_R, Effective Date: 16/02/2012, Version: 1 | Outage
NSW1-QLD1 Import | F_Q++LDTW_L60 | 0.1 (0) | Out = Liddell to Tamworth (84) line, Qld Lower 60 sec Requirement | Outage
T-V-MNSP1 Export | F_T++NIL_TL_L60 | 1927.7 (1465.3) | Tasmania lower 60 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_TL_L6 | 1441.2 (951.2) | Tasmania lower 6 second requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R60 | 454.8 (432.5) | Mainland raise 60 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R5 | 368.1 (461.6) | Mainland raise 5 minute requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_MG_R6 | 342.5 (534.4) | Mainland raise 6 second requirement for a mainland generation event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_T++NIL_TL_L5 | 260.8 (113.1) | Tasmania lower 5 minute requirement for loss of 2 Comalco potlines, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 171.5 (149.6) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
T-V-MNSP1 Export | T^V_NIL_BL_6 | 86.8 (0) | Out = Nil, prevent transient over-voltage (TOV) at Georgetown 220 kV bus for loss of Basslink | NIL
T-V-MNSP1 Export | F_MAIN++MPP_TGR60N-2 | 70.0 (0) | Out = Nil, loss of all Millmerran units declared credible as a generation event, Mainland raise 60 second requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++LREG_0050 | 57.0 (64.7) | Tasmania lower regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | F_MAIN++MPP_TGR5_N-2 | 44.8 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 5 Min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++MPP_TGR6_N-2 | 22.8 (0) | Out= Nil, loss of all Millmerran units declared credible as a generation event, Mainland Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | T^V_NIL_8 | 13.9 (0) | Out = Nil, Tamar Valley Combined Cycle GT OOS, prevent voltage collapse at Georgetown 220 kV bus for loss of a Sheffield to George Town 220 kV line, swamped if TVCC in service | NIL
T-V-MNSP1 Export | TVBL_ROC | 12.8 (15.8) | Out = Nil, rate of change (Tasmania to Victoria) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Export | TV_315 | 12.3 (0) | Tas to Vic on Basslink upper limit of 315 MW | Outage
T-V-MNSP1 Export | TV_500 | 10.8 (0) | Tas to Vic on Basslink upper limit of 500 MW | Outage
T-V-MNSP1 Export | TV_325 | 5.5 (0) | Tas to Vic on Basslink upper limit of 325 MW | Outage
T-V-MNSP1 Export | V>>N_SMTXF2_2 | 5.0 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Ballarat to Bendigo 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage
T-V-MNSP1 Export | CA_SPS_40D62A5B_01 | 4.5 (0) | During the outage of Hazelwood A2 500/220kV transformer with the Victorian network configured in 3/5 Parallel at Hazelwood four Yallourn units tripped. RTCA (Real Time Contingency Analysis) indicated that trip of Hazelwood to Yallourn No.1 or No.2 would cause overload on the remaining line. Constraint Automation was used to manage this issue. | Outage
T-V-MNSP1 Export | T_V_NIL_BL1 | 4.3 (15.1) | Out = Nil, Basslink no go zone limits Tasmania to Victoria | NIL
T-V-MNSP1 Export | V>>V_SMTXF2_4AR | 4.3 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Richmond to Brunswick 220 kV cable on trip of Rowville A1 500/220 kV transformer | Outage
T-V-MNSP1 Export | TV_410 | 3.5 (0) | Tas to Vic on Basslink upper limit of 410 MW | Outage
T-V-MNSP1 Export | V>>V-HWLY_3 | 3.3 (0) | Outage = Hazlewood to Loy Yang (HWTS-LYPS) No.3 500kV line, avoid overloading Hazelwood to Loy Yang No.1 or No.2 500kV line on trip of any of the remaining Hazelwood to Loy Yang 500kV line,feedback | Outage
T-V-MNSP1 Export | T_V_NIL_FCSPS | 3.1 (1.3) | Basslink limit from Tas to Vic for generation enabled for FCSPS | NIL
T-V-MNSP1 Export | F_MAIN++NIL_DYN_RREG | 2.1 (1.8) | Mainland Raise Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error below -1.5s, Basslink able transfer FCAS | NIL
T-V-MNSP1 Export | NC_T_BLNKTAS | 2.0 (0) | Non Conformance Constraint for Basslink from Tas to Vic | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L60 | 1.9 (5.8) | Out = one Comalco to George Town line, Tasmania Lower 60 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_T++COGT_TL_L6 | 1.5 (0.9) | Out = one Comalco to George Town line, Tasmania Lower 6 sec requirement for the loss of the remaining Comalco to George Town line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Export | F_MAIN++NIL_BL_R60 | 1.3 (0.1) | Mainland Raise 60 second Requirement for loss of Basslink, Basslink flow into Vic | NIL
T-V-MNSP1 Export | TV_350 | 1.3 (0) | Tas to Vic on Basslink upper limit of 350 MW | Outage
T-V-MNSP1 Export | TV_ZERO | 0.8 (0.1) | Tas to Vic on Basslink upper limit of 0 MW | Outage
T-V-MNSP1 Export | V>>V_SMTXF2_3P | 0.8 (0) | Out = South Morang F2 500/330 kV txfmr, avoid O/L Richmond to Brunswick 220 kV cable on NIL trip, 3/5 parallel mode, feedback | Outage
T-V-MNSP1 Export | #T-V-MNSP1_E_E | 0.8 (0) | T-V-MNSP1. * 1 <= 290 (Wt = 35) | Outage
T-V-MNSP1 Export | TV_560 | 0.8 (0) | Tas to Vic on Basslink upper limit of 560 MW | Outage
T-V-MNSP1 Export | T^V_GTSH_1 | 0.7 (0) | Out = Sheffield to Georgetown 220 kV line, prevent voltage collapse or voltage violations for trip of the remaining Sheffield to Georgetown 220 kV line | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L6_2 | 0.5 (0.3) | Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Export | V>>V_KTS_TX_A2_2_P | 0.5 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
T-V-MNSP1 Export | #R008672_052_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint T^V_GTSH_1, Effective Date: 03/05/2012, Version: 1 | Outage
T-V-MNSP1 Export | #R009382_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint TV_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Export | T_V_FCSPS_RAMP | 0.3 (0.7) | Ramp down (200 MW per DI) Basslink (Tas to Vic) for outage of FCSPS | Outage
T-V-MNSP1 Export | #R009530_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint TV_315, Effective Date: 07/11/2013, Version: 1 | Outage
T-V-MNSP1 Export | #T-V-MNSP1_RAMP_E_F | 0.3 (0) | T-V-MNSP1 <= MAX(160, InitialFlow - 200) (Wt=35) | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L5 | 0.3 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 5 min Requirement for loss of Basslink | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_1 | 0.3 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L60_1 | 0.2 (0) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1, FCSPS unavailable | NIL
T-V-MNSP1 Export | TV_400 | 0.2 (0) | Tas to Vic on Basslink upper limit of 400 MW | Outage
T-V-MNSP1 Export | #R009507_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_SMTXF2_3P, Effective Date: 03/12/2012, Version: 1 | Outage
T-V-MNSP1 Export | #R009530_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint TV_315, Effective Date: 07/11/2013, Version: 1 | Outage
T-V-MNSP1 Export | #R009560_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint TV_315, Effective Date: 07/11/2013, Version: 1 | Outage
T-V-MNSP1 Export | F_MAIN++RREG_0300 | 0.1 (0) | Mainland Raise Regulation Requirement greater than 300 MW, Basslink able transfer FCAS | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L60_1 | 0.1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 1 | Outage
T-V-MNSP1 Export | F_T++BLSPS_EXP_L6_2 | 0.1 (0) | Limit Basslink export to levels where no FCSPS action is required for loss of Basslink, Tasmania Lower 6 sec Requirement for loss of Basslink, Segment 2 | Outage
T-V-MNSP1 Export | F_T++NIL_BLSPS_L5 | 0.1 (0.6) | Tasmania Lower 5 min Requirement for loss of Basslink, FCSPS unavailable | NIL
T-V-MNSP1 Export | F_T++NIL_BLSPS_L60_2 | 0.1 (0.1) | Tasmania Lower 60 sec Requirement for loss of Basslink, Segment 2, FCSPS unavailable | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_0400 | 372.1 (586.1) | Mainland lower 5 minute requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L60_0400 | 275.6 (82.7) | Mainland lower 60 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R6 | 154.8 (74.2) | Tasmania raise 6 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APHY_L5 | 142.4 (241.9) | Out = Alcoa Portland to Heywood 500 kV line, Mainland lower 5 minute requirement for the loss of the remaining Alcoa Portland to Heywood 500 kV line, Basslink able to transfer FCAS The Heywood to Alcoa Portland 500 kV line was out for 87.7 days in 2013 compared to 75.4 days in 2012 | Outage
T-V-MNSP1 Import | F_T++NIL_MG_R60 | 101.2 (69.4) | Tasmania raise 60 second requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++APHY_L60 | 97.1 (54.0) | Out = Heywood to Alcoa Portland 500 kV line, lower 60 second requirement for the loss of the remaining Alcoa Portland to Heywood 500 kV line, Basslink able to transfer FCAS The Heywood to Alcoa Portland 500 kV line was out for 87.7 days in 2013 compared to 75.4 days in 2012 | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_6E | 73.0 (0) | Out = Nil, avoid overloading a Sheffield to Georgetown 220 kV line for trip of the parallel Sheffield to Georgetown 220 kV line considering NCSPS action | NIL
T-V-MNSP1 Import | F_T++NIL_MG_R5 | 67.9 (13.3) | Tasmania raise 5 minute requirement for a Tasmania generation event, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++RREG_0050 | 58.9 (75.2) | Tasmania raise regulation requirement greater than 50 MW, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_MAIN++ML_L6_0400 | 46.8 (159.4) | Mainland lower 6 second requirement for a mainland load event, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_5F | 42.4 (0.9) | Out = Nil, avoid overloading a Hadspen to George Town 220 kV line for trip of the other Hadspen to George Town 220 kV line considering NCSPS action | NIL
T-V-MNSP1 Import | F_MAIN++ML_L5_APD | 39.6 (33.6) | Out = Nil, Lower 5 min requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_MAIN++ML_L60_APD | 23.0 (19.4) | Out = Nil, Lower 60 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R60 | 22.6 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 60 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R6 | 20.4 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 6 sec requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_HYSE_xxx | 19.8 (34.6) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
T-V-MNSP1 Import | V::N_MSUT_xxx | 17.3 (12.9) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
T-V-MNSP1 Import | VTBL_ROC | 14.8 (22.0) | Out = Nil, rate of change (Victoria to Tasmania) limit (200 MW / 5 minute) for Basslink | NIL
T-V-MNSP1 Import | T_ROCOF_1 | 9.3 (0) | Out = NIL, limit delayed rate of change of frequency in TAS to 1.076 Hz per sec following line fault and trip of Tamar CCGT. Swamped if Tamar CCGT OOS. | NIL
T-V-MNSP1 Import | V::N_NILxxx | 8.9 (240.7) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
T-V-MNSP1 Import | VT_ZERO | 7.8 (0.3) | Victoria to Tasmania on Basslink upper transfer limit of 0 MW | Outage
T-V-MNSP1 Import | V_T_NIL_BL1 | 6.8 (47.9) | Out=Nil, Basslink no go zone limits Victoria to Tasmania | NIL
T-V-MNSP1 Import | V::N_HWSM_V1 | 6.3 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
T-V-MNSP1 Import | T>>T_GTHA_EXP_3H | 6.1 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Sheffield to George Town 220 kV line (flow to George Town) for trip of other Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R5 | 5.0 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R60 | 4.6 (0.4) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 60 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_GTSH_EXP_3H | 4.6 (1.2) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Sheffield 220 kV line (flow to Palmerston) on trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload | Outage
T-V-MNSP1 Import | F_MAIN++NIL_BL_L60 | 4.3 (221.1) | Mainland lower 60 second requirement for loss of Basslink, Basslink flow into Tasmania, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R5 | 3.0 (0) | Out = either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 5 min requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R60 | 2.3 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R5 | 2.3 (0) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_GTSH_EXP_3FH | 2.1 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown and Palmerston to Sheffield 220 kV line for trip of Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overloads. | Outage
T-V-MNSP1 Import | V::N_SMF2_S1 | 2.1 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink TAS to VIC, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
T-V-MNSP1 Import | T>>T_GTHA_EXP_3GH | 2.0 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L Hadspen to George Town and Sheffield to George Town 220 kV line for trip of Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | V::N_LTWG_xxx | 2.0 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_QNV++HYTR_L60 | 1.8 (0.1) | Out = Heywood to Tarrone (HYTS-TRTS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH_N-2_TG_R6 | 1.6 (0) | Out = Nil, loss of both Farrell to Sheffield lines declared credible, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R60 | 1.6 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++NIL_WN_TG_R6 | 1.6 (4.8) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R5 | 1.5 (0) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 5 min requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | CA_SPS_41CE7351_01 | 1.3 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
T-V-MNSP1 Import | F_MAIN++TL_L5_0500 | 1.3 (0) | Out = Nil, Lower 5 min Service Requirement for a Mainland Network Event, TL = 500, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_1B | 1.2 (0) | Out = Nil, avoid O/L a Gordon to Chapel St 220 kV line for trip of the parallel line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_2RP_xxx | 0.9 (0) | Out = 2 dynamic reactive plant from Vic metro or SESS SVC's, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | F_T++FARE_N-2_TG_R6 | 0.8 (0.1) | Out = Nil, loss of both Farrell to Reece lines declared credible, Tasmania Raise 6 sec requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_WF_TG_R6 | 0.8 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Smithton to Woolnorth or Norwood to Scotsdale tee Derby line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_GTSH_EXP_3C | 0.8 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Palmerston to Hadspen No. 1 220 kV line (flow North) for trip of remaining Sheffield to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage
T-V-MNSP1 Import | V_T_NIL_FCSPS | 0.8 (230.8) | Basslink limit from Victoria to Tasmania for load enabled for the Basslink frequency control special protection scheme (FCSPS) | NIL
T-V-MNSP1 Import | F_QNV++HYMO_L60 | 0.6 (4.8) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | V::N_JNWG_xxx | 0.6 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
T-V-MNSP1 Import | #R008638_023_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | F_MAIN++ML_L6_APD | 0.5 (2.1) | Out = Nil, Lower 6 sec requirement for a Mainland Load Event, ML = APD, Basslink able transfer FCAS | Outage
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R6 | 0.5 (0) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 6 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_7C | 0.5 (0.7) | Out = Nil, avoid O/L a Farrell to Sheffield 220 kV line for trip of the parallel Farrell to Sheffield 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | V::N_BYPASS_HW_SY_VE | 0.5 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
T-V-MNSP1 Import | #R008438_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008596_011_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008605_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008664_020_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008664_020_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R009476_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009525_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | F_NVS++ARTW_L60 | 0.4 (0) | Out = Armidale to Tamworth (85 or 86) line, NSW, Snowy, Vic and SA Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_BB_TG_R6 | 0.4 (0) | Out= Nil, Tasmania Raise 6 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | #R008596_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008605_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008638_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008648_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_2RPVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008658_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008793_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009491_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | F_T++NIL_WN_TG_R5 | 0.3 (1.4) | Out= Nil, Tasmania Raise 5 min requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T>>T_GTHA_EXP_3G | 0.3 (0) | Out = Hadspen to George Town 220 kV line, avoid O/L remaining Hadspen to George Town 220 kV line (flow to George Town) for trip of a Sheffield to George Town 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
T-V-MNSP1 Import | T>>T_GTSH_EXP_3D | 0.3 (0) | Out = Sheffield to Georgetown 220 kV line, avoid O/L Hadspen to Georgetown 220 kV line (flow North) for trip of other Hadspen to Georgetown 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action to remove overload. | Outage
T-V-MNSP1 Import | #R009203_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | F_T++NIL_WN_TG_R60 | 0.3 (4.1) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Smithton to Woolnorth line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | V>>V_HWPS-RO_3-5_4 | 0.3 (0) | Out = Hazelwood to Rowville No.1 or No.2 220kV line, 3-5 Parallel, Jeeralang split with JLGS A connected to Hazelwood #1 or #2 220kV bus, void O/L Hazelwood #1 or #2 500/220kV transformer for loss of either transformer | Outage
T-V-MNSP1 Import | #R008648_009_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_2RPVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008658_023_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R009170_019_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | F_MAIN++NIL_DYN_LREG | 0.2 (7.8) | Mainland Lower Regulation Requirement, Feedback in Dispatch, increase by 60 MW for each 1s of time error above 1.5s, Basslink able transfer FCAS | NIL
T-V-MNSP1 Import | F_T++FASH1_2C_TG_R60 | 0.2 (0) | Out =either Farrell to Sheffield (1 or 2) line with John Butters, Tribute & Reece 1,2 supplying Sheffield, Tasmania Raise 60 sec requirement for loss of the remaining Farrell to Sheffield line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | T>>T_NIL_BL_EXP_3F | 0.2 (0) | Out = Nil, avoid O/L a Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of the other Hadspen to Palmerston 220 kV line considering NCSPS action, ensure Basslink can fully compensate NCSPS action. | NIL
T-V-MNSP1 Import | #R008176_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYSEQD_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008648_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_2RPVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008658_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_LTWGVA_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008664_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MSUTVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
T-V-MNSP1 Import | #R008793_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009048_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009048_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009141_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009191_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009203_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009476_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009525_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009601_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | #R009601_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
T-V-MNSP1 Import | F_QNV++MLSY_L5 | 0.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 5 min Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_QNV++MLSY_L60 | 0.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++CSGO_TG_R5 | 0.1 (0) | Out = one Chapel St to Gordon line, Tasmania Raise 5 min requirement for loss of the remaining Chapel St to Gordon line, Basslink able to transfer FCAS | Outage
T-V-MNSP1 Import | F_T++NIL_BB_TG_R60 | 0.1 (0) | Out= Nil, Tasmania Raise 60 sec requirement for loss of a Bell Bay to George Town line, Basslink able to transfer FCAS | NIL
T-V-MNSP1 Import | T::T_NIL_5 | 0.1 (0) | Out = NIL, prevent poorly damped TAS North - South oscillations following fault and trip of Palmerston to Sheffield 220 kV line, Tamar CCGT OOS. Swamped if Tamar CCGT in service | NIL
T-V-MNSP1 Import | T>>T_HAPM_EXP_3A | 0.1 (0) | Out = Hadspen to Palmerston 220 kV line, avoid O/L Hadspen to Palmerston 220 kV line (flow to Hadspen) for trip of Palmerston to Sheffield 220 kV line considering NCSPS action, ensure Basslink can compensate NCSPS action. | Outage
V-S-MNSP1 Export | VSML_ZERO | 423.9 (33.3) | Victoria to South Australia on Murraylink upper transfer limit of 0 MW | Outage
V-S-MNSP1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 184.0 (157.3) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-S-MNSP1 Export | VSML_220 | 68.1 (5.2) | Upper transfer limit of 220 MW on VIC to SA on Murraylink | NIL
V-S-MNSP1 Export | V>>SML_NIL_7A | 64.9 (13.6) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line This constraint equation only binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for high flows on Murraylink into SA. | NIL
V-S-MNSP1 Export | V^SML_NSWRB_2 | 53.8 (11.6) | Out = NSW Murraylink runback scheme, avoid voltage collapse for trip of Darlington Point to Buronga (X5) 220 kV line This constraint equation is currently part of the Victorian system normal constraint set, as the NSW Murraylink runback scheme has not been commissioned. | NIL
V-S-MNSP1 Export | V>SMLBAHO4 | 41.6 (11.7) | Out = Ballarat to Horsham or Bendigo to Kerang line, avoid overloading Buronga to Redcliffs (0X1) line for trip of Bendigo to Kerang, or Ballarat to Horsham line The Bendigo to Kerang 220 kV line was out for 8.2 days in 2013 compared to 0 days in 2012 | Outage
V-S-MNSP1 Export | V>>V-MSUT_1 | 39.5 (0) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line The Murray to Upper Tumut (65) 330 kV line was out for 18.0 days in 2013 compared to 9.0 days in 2012 | Outage
V-S-MNSP1 Export | V>S_NWRB2_NWRB1 | 34.2 (0) | Out = North West Bend to Robertstown No.2 132 kV line, avoid overloading North West Bend to Robertstown No.1 132 kV line The North West Bend to Robertstown No.2 132 kV line was out for 31.8 days in 2013 compared to 11.6 days in 2012 | Outage
V-S-MNSP1 Export | V>>V_NIL1A_R | 30.2 (44.8) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line This constraint equation only binds for high flows from Victoria to NSW | NIL
V-S-MNSP1 Export | V>>SML_NIL_8 | 27.9 (0.3) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
V-S-MNSP1 Export | N^^V_NIL_2 | 20.8 (5.2) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL
V-S-MNSP1 Export | V::N_HYSE_xxx | 19.2 (27.7) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line One Heywood to South East 275 kV line was out for 45.1 days in 2013 compared to 68.3 days in 2012 | Outage
V-S-MNSP1 Export | V>>SML_NIL_7B | 17.9 (2.8) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
V-S-MNSP1 Export | V::N_MSUT_xxx | 13.9 (15.4) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-S-MNSP1 Export | V>SML_BUDP_2 | 13.1 (32.7) | Out = Buronga to Balranald to Darlington Pt. (X5) 220 kV line, avoid overloading on Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line | Outage
V-S-MNSP1 Export | V>>SML_NIL_1 | 11.9 (2.3) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line | NIL
V-S-MNSP1 Export | V::N_NILxxx | 8.4 (362.3) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
V-S-MNSP1 Export | V::N_HWSM_V1 | 6.3 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-S-MNSP1 Export | V>>N_SMTXF2_2 | 6.2 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Ballarat to Bendigo 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage
V-S-MNSP1 Export | V>SMLBAHO1 | 5.9 (4.6) | Out = Ballarat to Horsham, or Bendigo to Kerang line, avoid overloading or voltage collapse on Buronga to Balranald to Darlington Point (X5) line for trip of Bendigo to Kerang or Ballarat to Horsham line | Outage
V-S-MNSP1 Export | V>>V_NIL_5 | 5.3 (6.8) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
V-S-MNSP1 Export | V>>N-NIL_HA | 2.9 (1.5) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL
V-S-MNSP1 Export | V>>N_DDMS_2 | 2.8 (4.3) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Murray to Dederang 330 kV line, feedback | Outage
V-S-MNSP1 Export | V::N_SMF2_S1 | 1.9 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink TAS to VIC, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-S-MNSP1 Export | V::N_LTWG_xxx | 1.8 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | N>>N-DP_TIETX_A | 1.8 (0) | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (330 to 220 kV) on Kerang-Bendigo trip; Feedback | Outage
V-S-MNSP1 Export | NRM_VIC1_SA1 | 1.6 (0) | Negative Residue Management constraint for VIC to SA flow | NIL
V-S-MNSP1 Export | V>>V_SMTXF2_6 | 1.4 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage
V-S-MNSP1 Export | V>>SML_NIL_7C | 1.2 (0) | Out = Nil, avoid O/L Arrarat to Stawell 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
V-S-MNSP1 Export | V>SMLBSRC2 | 1.2 (0) | Out = Buronga to Redcliffs (0X1) 220 kV line, avoid O/L Horsham to Waubra 220 kV line section on trip of Bendigo to Kerang 220 kV line, feedback | Outage
V-S-MNSP1 Export | CA_SPS_3FFA5B9A_01 | 1.0 (0) | Constraint Automation, O/L BATS_BETS_220 @BATS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-S-MNSP1 Export | #V-S-MNSP1_E_E | 0.9 (0) | V-S-MNSP1.ENERGY * 1 = 6 (Wt = 20) | Outage
V-S-MNSP1 Export | N^^V_LTUT_2 | 0.8 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | Outage
V-S-MNSP1 Export | V>>V_KTS_TX_A2_2_P | 0.8 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
V-S-MNSP1 Export | CA_SPS_41C52A3F_01 | 0.7 (0) | Constraint Automation, O/L DDTS_SHTS_220 @DDTS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-S-MNSP1 Export | V^SML_NIL_3 | 0.6 (0.2) | Out = Nil, avoid voltage collapse for loss of Bendigo to Kerang 220kV line, swamped if Murraylink VFRB enabled and Murraylink > 25MW | NIL
V-S-MNSP1 Export | #R008583_029_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 22/09/2009, Version: 1 | Outage
V-S-MNSP1 Export | V::N_JNWG_xxx | 0.5 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | #R008414_026_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V_SMTXF2_6, Effective Date: 03/12/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008438_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008583_029_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 22/09/2009, Version: 1 | Outage
V-S-MNSP1 Export | #R008596_011_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008605_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008638_023_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008664_020_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008664_020_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R009476_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009491_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009525_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R008206_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>SMLBAHO4, Effective Date: 26/11/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008414_026_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_SMTXF2_6, Effective Date: 03/12/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008596_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008638_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008658_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008793_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-S-MNSP1 Export | N>>N-CNUT_HA | 0.3 (0) | Out = Canberra-UpperTumut(1), avoid Upper Tumut to Lower Tumut(64) O/L on Upper Tumut to Yass(2) trip; Feedback | Outage
V-S-MNSP1 Export | V::N_2RP_xxx | 0.3 (0) | Out = 2 dynamic reactive plant from Vic metro or SESS SVC's, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-S-MNSP1 Export | V>>SML_BAML2_1 | 0.3 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line (complete line or line sections), prevent overload of the Moorabool to Ballarat No. 1 220 kV line for trip of the Moorabool to Terang 220 kV line, feedback | Outage
V-S-MNSP1 Export | #R008565_032_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>SML_BUDP_2, Effective Date: 05/04/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R008605_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R009203_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009425_002_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | V>SMLHORC1 | 0.3 (0) | Out = Horsham to Red Cliffs 220kV line, avoid overloading Balranald to Darlington Pt (X5/1) 220kV line for trip of Bendigo to Kerang line | Outage
V-S-MNSP1 Export | #R008206_002_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V>SMLBAHO4, Effective Date: 26/11/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008648_008_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_2RPVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008648_009_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_2RPVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R009170_019_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009507_024_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_SMTXF2_6, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009601_009_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009645_002_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint VSML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | V>>V_NIL_4A | 0.2 (0.1) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. | NIL
V-S-MNSP1 Export | V>>V_ROTS_TX_2_P | 0.2 (0) | Out= Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
V-S-MNSP1 Export | #R008176_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYSEQD_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008651_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VSML_000, Effective Date: 05/08/2008, Version: 1 | Outage
V-S-MNSP1 Export | #R008658_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_LTWGVA_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008664_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MSUTVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R008793_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009048_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009048_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009141_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009191_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009203_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009221_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2_P, Effective Date: 03/12/2012, Version: 1 | Outage
V-S-MNSP1 Export | #R009476_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009525_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | #R009601_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Export | V>>N-CNUT_HB_15M | 0.1 (0) | Out = Canberra-UpperTumut(1), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage
V-S-MNSP1 Export | V>>N-MSUT_2 | 0.1 (0) | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage
V-S-MNSP1 Export | V>>V_NIL_4C | 0.1 (0) | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL
V-S-MNSP1 Import | SVML_ZERO | 173.7 (281.6) | Upper transfer limit of 0 MW on SA to VIC on Murraylink | Outage
V-S-MNSP1 Import | S>V_NWRB2_RBNW1 | 85.6 (15.3) | Out = North West Bend to Robertstown No.2 line, avoid overloading on Robertstown to North West Bend No.1 132 kV line | Outage
V-S-MNSP1 Import | S>V_NIL_NIL_RBNW | 51.7 (72.5) | Out = Nil, avoid overloading the North West Bend to Robertstown 132 kV line on no line trips | NIL
V-S-MNSP1 Import | N>>V_DBUSS_1 | 29.0 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line DBUSS - line is a control scheme that splits Dederang 330 kV bus on trip of a Murray to Dederang line. This was implemented to allows higher NSW to Vic interconnector capability. For a number of outages in southern NSW and northern Victoria either the line or transformer control schemes are also taken out of service. The Dederang DBUSS-Line control scheme was out for 465.9 days in 2013 compared to 112.2 days in 2012 | Outage
V-S-MNSP1 Import | V>>V_NIL_1B | 13.7 (6.8) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line This constraint equation binds for high transfers from NSW to Victoria with the DBUSS (Dederang bus splitting scheme) active. | NIL
V-S-MNSP1 Import | S>>V_NIL_NOTI_NOTI_3 | 12.0 (0) | Out = Nil with Torrens Island 66kV CB6W2, CB6W3 & CB6E6 open; avoid O/L of Torrens Island - New Osborne 66kV No.4 line on trip of Torrens Island - New Osborne 66kV No.3 line | NIL
V-S-MNSP1 Import | S>>V_NIL_RBTXW_RBTX1 | 5.6 (46.8) | Out = Nil, avoid overloading Robertstown No.1 275/132 kV transformer on trip of the Robertstown No.2 275/132 kV transformer This constraint equation normally binds when there is high generation from Northern, Hallett GT and the wind farms connected to the 275 kV between Robertstown and Davenport. | NIL
V-S-MNSP1 Import | V>>V_SMTXF2_4AR | 5.3 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Richmond to Brunswick 220 kV cable on trip of Rowville A1 500/220 kV transformer | Outage
V-S-MNSP1 Import | CA_SPS_40D62A5B_01 | 4.1 (0) | During the outage of Hazelwood A2 500/220kV transformer with the Victorian network configured in 3/5 Parallel at Hazelwood four Yallourn units tripped. RTCA (Real Time Contingency Analysis) indicated that trip of Hazelwood to Yallourn No.1 or No.2 would cause overload on the remaining line. Constraint Automation was used to manage this issue. The Constraint Automation Set. Generated by STNET[NORFL] Host NOREEMP3(SP) was out for 0.4 days in 2013 compared to 0 days in 2012 | Outage
V-S-MNSP1 Import | V>>V_NIL_3 | 1.3 (0.2) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL
V-S-MNSP1 Import | V>>V_SMTXF2_3P | 0.8 (0) | Out = South Morang F2 500/330 kV txfmr, avoid O/L Richmond to Brunswick 220 kV cable on NIL trip, 3/5 parallel mode, feedback | Outage
V-S-MNSP1 Import | S>>V_NIL_NOTI_NOTI_4 | 0.6 (0) | Out = Nil with Torrens Island 66kV CB6W2, CB6W3 & CB6E6 open; avoid O/L of Torrens Island - New Osborne 66kV No.3 line on trip of Torrens Island - New Osborne No.4 | NIL
V-S-MNSP1 Import | #R008313_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint SVML_000, Effective Date: 05/08/2008, Version: 1 | Outage
V-S-MNSP1 Import | #R009353_001_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R008651_001_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint SVML_000, Effective Date: 05/08/2008, Version: 1 | Outage
V-S-MNSP1 Import | SVML_010 | 0.3 (0) | SA to Vic on ML upper transfer limit of 10 MW | Outage
V-S-MNSP1 Import | #V-S-MNSP1_E_E | 0.3 (0) | V-S-MNSP1.ENERGY * 1 = 6 (Wt = 20) | Outage
V-S-MNSP1 Import | #R008313_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint SVML_000, Effective Date: 05/08/2008, Version: 1 | Outage
V-S-MNSP1 Import | #R009353_001_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | S>>V_NIL_NIL_HUWT | 0.2 (1.8) | Out = Nil, avoid overloading Hummocks to Waterloo 132 kV line for no contingencies | NIL
V-S-MNSP1 Import | #R009425_001_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint SVML_ZERO, Effective Date: 21/08/2013, Version: 1 | Outage
V-S-MNSP1 Import | #R009507_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_SMTXF2_3P, Effective Date: 03/12/2012, Version: 1 | Outage
V-SA Export | V>>S_NIL_SETB_SGKH | 648.6 (0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV line on trip of a South East to Tailem Bend 275 kV line | NIL
V-SA Export | V>S_460 | 300.3 (15.1) | VIC to SA on Heywood upper transfer limit of 460 MW | NIL
V-SA Export | V>S_NIL_HYTX_HYTX | 249.7 (12.7) | Out = Nil, avoid overloading the remaining Heywood 275/500 kV transformer on trip of one Heywood 275/500 kV transformer | NIL
V-SA Export | V^^S_NIL_MAXG_xxx | 208.3 (220.5) | Out = Nil, Victoria to SA long term voltage stability limit for loss of the largest credible generation contingency in SA, South East capacitor bank on / off | NIL
V-SA Export | V>>S_HYML_1 | 82.7 (96.9) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 1 One Heywood 500/275 kV (M1 or M2) transformer was out for 21.6 days in 2013 compared to 28.5 days in 2012 | Outage
V-SA Export | V::S_NIL_MAXG_xxx | 78.3 (4.3) | Out = Nil, Vic to SA Transient Stability limit for loss of the largest generation unit in SA There are two constraint equations that make up the transient stability export limit from Victoria to South Australia and all the binding results have been combined. | NIL
V-SA Export | V>>S_PWSE_SETB_SGKH | 40.3 (0) | Out = Penola West to South East 132 kV line, avoid overloading Snuggery to Keith 132 kV line on trip of South East to Tailem Bend 275 kV line The Penola West to South East 132 kV line was out for 4.4 days in 2013 compared to 11.5 days in 2012 | Outage
V-SA Export | V>>S_NIL_PWKN_SGKH | 40.2 (0) | Out = Nil, avoid overloading Snuggery to Keith 132 kV on trip of Penola West to Kincraig 132kV line | NIL
V-SA Export | V^^S_PAVC_MAXG | 36.1 (14.1) | Out = Para one SVC, VIC to SA Voltage Stability limit for loss of the largest generation unit in SA One Para SVC was out for 6.9 days in 2013 compared to 1.8 days in 2012 | Outage
V-SA Export | VS_250 | 26.3 (33.6) | Victoria to South Australia on Heywood upper transfer limit of 250 MW This constraint equation is included in a number of constraint sets which are used for outages of the 500 kV lines in from Sydenham to Heywood and the 275 kV lines from Heywood to South East. One Heywood to South East 275 kV line was out for 22.6 days in 2013 compared to 34.1 days in 2012 | Outage
V-SA Export | V^^S_TBTX4_MAXG | 26.2 (0) | Out =Tailem Bend 275/132 kV transformer #4; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S) | Outage
V-SA Export | V>>S_NIL_SETB_KHTB | 26.0 (13.1) | Out = Nil, avoid overloading Keith to Tailem Bend No.1 132 kV line for trip of South East to Tailem Bend 275 kV line | NIL
V-SA Export | S>>NIL_SETB_KHTB2 | 16.9 (0) | Out= NIL, avoid O/L Keith - Tailem Bend #2 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL
V-SA Export | V>>S_HYML_2 | 16.4 (25.3) | Out = Heywood to Moorabool to Alcoa Portland 500 kV line, avoid overloading Heywood 500/275 kV (M1 or M2) transformer for trip of Northern Power Station unit 2 The Heywood to Tarrone 500 kV line was out for 23.8 days in 2013 compared to 29.5 days in 2012 | Outage
V-SA Export | V::N_HYSE_xxx | 15.9 (33.1) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line One Heywood to South East 275 kV line was out for 22.6 days in 2013 compared to 34.1 days in 2012 | Outage
V-SA Export | V^^S_MOTB_MAXG | 14.7 (0) | Out= Mobilong - Tailem Bend 132kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage
V-SA Export | V^^S_PWSE_MAXG | 13.8 (2.1) | Out= Penola West - South East 132 kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage
V-SA Export | F_ESTN++HYTR_L60 | 12.6 (3.1) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 60 sec Requirement | Outage
V-SA Export | V^^S_MOTB+PAVC_MAXG | 9.6 (0) | Out= Mobilong - Tailem Bend 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage
V-SA Export | V>>S_KNPW_SETB_SGKH | 8.9 (1.6) | Out= Kincraig - Penola West 132kV line, avoid O/L Snuggery - Keith 132kV on trip of one South East - Tailem Bend 275kV line, Feedback | Outage
V-SA Export | V>>S_NIL_NIL_SGKHC | 7.3 (14.8) | Out= Nil, avoid O/L Snuggery - Keith 132 kV on Nil trip, Feedback | NIL
V-SA Export | S>>XSEVC1+CB_SETB2_4 | 6.6 (0) | Out= South East #1 SVC and South East CB6606 & CB6610, avoid O/L Snuggery - Keith 132kV on trip of South East - Tailem Bend #2 275kV line, Feedback | Outage
V-SA Export | V>>S_TBTU_TBCG_TBMO | 6.3 (0) | Out= Tailem Bend - Tungkillo 275kV line, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V::N_NILxxx | 6.2 (348.9) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
V-SA Export | S>>XSEVC2+CB_SETB1_4 | 5.8 (0) | Out= South East #2 SVC and South East CB6607 & CB6611, avoid O/L Snuggery - Keith 132kV on trip of South East - Tailem Bend #1 275kV lines, Feedback | Outage
V-SA Export | S>>X_TBTU+CB_TBCG_1 | 5.8 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Tailem Bend - Mobilong 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V::N_HWSM_V1 | 4.8 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
V-SA Export | V::S_MAXG_NPS_N-2 | 4.2 (0) | Out = Nil; Vic to SA Transient Stability limit for loss of the largest generation block in SA with loss of both Northern Power Station units declared as credible. | Outage
V-SA Export | V^^S_MTSE+PAVC_MAXG | 3.9 (0) | Out= Mt Gambier - South East 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage
V-SA Export | V>S_NIL_NIL_HYTX1 | 3.5 (0.4) | Out = NIL, avoid O/L Heywood M1 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL
V-SA Export | V::N_MSUT_xxx | 3.4 (14.6) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line | Outage
V-SA Export | V::S_XKHTB1+2_SETB | 3.4 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S; Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line | Outage
V-SA Export | V>>S_NIL_KHTB2_KHTB1 | 3.1 (4.3) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV one trip of Keith - Tailem Bend #2 132kV line, Feedback | NIL
V-SA Export | V>>S_HYML_4 | 3.0 (37.3) | Out = one Heywood 500/275 kV transformer, avoid overloading remaining Heywood 500/275 kV transformer for loss of a Pelican Point GT and consequent offloading of Pelican Point ST | Outage
V-SA Export | V::S_HYSE | 2.9 (0.3) | Out = One South East - Heywood 275 kV line; Vic to SA Stability limit for loss of one NPS unit or South East-Tailem Bend 275 kV line. | Outage
V-SA Export | F_ESTN++HYTR_L5 | 2.8 (1.6) | Out = Heywood to Tarrone (HYTS-TRTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V^^S_KNPW+PAVC_MAXG | 2.8 (0) | Out= Kincraig - Penola West 132kV line and Para SVC 1 or 2 O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage
V-SA Export | S>>MOTB_TBTU_TBCG | 2.7 (0) | Out= Mobilong - Tailem Bend 132kV line, avoid O/L Tailem Bend - Cherry Gardens 275kV on trip of Tailem Bend - Tungkillo 275kV line, Feedback | Outage
V-SA Export | V::S_TBCP_MAXG_2 | 2.5 (0) | Out= Tailem Bend 275kV Cap Bank (Tungkillo 275kV Cap available); Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S) (Swamp out if SA demand less/equal to 3200MW) | Outage
V-SA Export | V::S_SESG_SETB | 2.3 (0) | Out= South East-Snuggery 132kV (including line section connecting Lake Bonney WFs + Lake Bonney WFs O/S); Vic to SA Transient Stability limit for the loss of one South East-Tailembend 275kV line (Note: with NPS and Playford PS assumed to be O/S). | Outage
V-SA Export | V>>S_KHTB1_SETB_KHTB | 2.3 (0) | Out = Keith - Tailem Bend #1 132 kV line. Prevent Keith - Tailem Bend #2 line OL for South East - Tailem Bend line trip. | Outage
V-SA Export | V^^S_TBCPTX_MAXG | 2.3 (0) | Out= Tailem Bend 275/132kV transformer and Tailem Bend 100Mvar Cap Bank; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (Note: NPS and Playford PS assumed I/S). | Outage
V-SA Export | V::S_SEVC_MAXG_2 | 2.2 (0) | Out= South East one SVC; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage
V-SA Export | V::N_SMF2_S1 | 2.1 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink TAS to VIC, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
V-SA Export | F_ESTN++HYMO_L60 | 1.9 (34.7) | Out = Heywood to Mortlake 500 kV line, Eastern lower 60 second requirement | Outage
V-SA Export | V::N_LTWG_xxx | 1.9 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | CA_SPS_40381C26_01 | 1.8 (0) | Constraint Automation, O/L MOBTAB_1 @T_BEND for CTG LSIQ on trip of CH_GDN - T_BEND 275KV LINE. Generated by STNET[MANFR] Host NOREEMP3(SP) | Outage
V-SA Export | F_QNV++HYMO_L60 | 1.8 (1.6) | Out = Heywood to Mortlake (HYTS-MOPS) line, Qld, NSW and Vic Lower 60 sec Requirement, Basslink able to transfer FCAS | Outage
V-SA Export | V>>S_HYML_3 | 1.8 (0) | Out = One Heywood 500/275 kV txfmr in service only, prevent overload of the in service 500/275 kV Heywood transformer for loss of Lake Bonney Wind Farm | Outage
V-SA Export | V>>S_TB6125+28_KHTB1 | 1.6 (0) | Out = Tailem Bend CBs 6125 and/or 6128 (both or either CB); Limit SE generation and Vic-SA to avoid OL Keith-Tailem Bend 132kV #1 line for loss of Tailem Bend transformer #4. | Outage
V-SA Export | V_HYMO2_1 | 1.5 (2.8) | Out = Heywood to Mortlake No.2 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage
V-SA Export | NRM_VIC1_SA1 | 1.4 (0) | Negative Residue Management constraint for VIC to SA flow | NIL
V-SA Export | CA_SPS_41CE7351_01 | 1.3 (0) | Constraint Automation, O/L HWTS TRANSF A4TR_500 for CTG MVPN on trip of ROTS-YPS 220KV LINES 5 & 6. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-SA Export | V^^S_SEVC_MAXG | 1.3 (3.9) | Out= South East one SVC; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be I/S). | Outage
V-SA Export | #R008231_008_RAMP_F | 1.2 (0) | Hard Ramping constraint for constraint V>>S_TBTU_TBCG_TBMO, Effective Date: 01/01/2012, Version: 1 | Outage
V-SA Export | VS_150 | 1.2 (0) | Victoria to SA on VicSA upper transfer limit of 150 MW | Outage
V-SA Export | F_ESTN++MLSY_L60 | 1.1 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 60 sec Requirement | Outage
V-SA Export | V_HYML1_5 | 1.1 (0) | Out = Heywood to Tarrone, or Tarrone to Moorabool No. 1 500 kV line, limit voltage unbalance at the APD 500 kV bus, two Mortlake units in service | Outage
V-SA Export | V^^S_TB6594_35_SETB | 1.0 (0) | Out= Tailem Bend 275kV CB6594 OR CB6535 O/S; Vic to SA Long Term Voltage Stability limit for loss of one South East - Tailem Bend 275 kV line. | Outage
V-SA Export | V>>S_KH_X_SETB_SETB | 0.9 (0) | Out= Keith - Tailem Bend 132kV #1 & #2 lines O/S, avoid O/L the remaining South East - Tailembend 275kV on trip of one South East - Tailembend 275kV line, Feedback | Outage
V-SA Export | V::S_TBCB6594_MAXG_2 | 0.8 (0) | Out = Tailem Bend CB6594 O/S; Vic to SA Transient Stability limit for loss of the largest generation block in SA (South East Capacitor Available) with NPS and Playford assumed to be OOS. | Outage
V-SA Export | V_HYML1_4 | 0.8 (0.5) | Out = Heywood to Tarrone, or Tarrone to Moorabool No.1 500 kV line, limit voltage unbalance at the APD 500 kV bus, one Mortlake unit in service | Outage
V-SA Export | V::N_2RP_xxx | 0.7 (0) | Out = 2 dynamic reactive plant from Vic metro or SESS SVC's, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | V^^S_SECP_MAXG | 0.7 (0) | Out = South East 275 kV capacitor; Vic to SA Long Term Voltage Stability limit for loss of one NPS generator or the largest generation block in SA (Note: with NPS and Playford assumed I/S). | Outage
V-SA Export | V::S_SETB_SETB | 0.7 (81.3) | Out = South East to Tailem Bend 275 kV line, avoid transient instability for loss of the parallel South East to Tailem Bend 275 kV line | Outage
V-SA Export | V::N_JNWG_xxx | 0.6 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
V-SA Export | #R008638_023_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #V-SA_RAMP_E_F | 0.5 (4.8) | V-SA <= MAX(86, InitialFlow - 30) (Wt=35) | Outage
V-SA Export | V::N_BYPASS_HW_SY_VE | 0.5 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
V-SA Export | #R008231_008_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>S_TBTU_TBCG_TBMO, Effective Date: 01/01/2012, Version: 1 | Outage
V-SA Export | #R008302_002_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>S_HYML_1, Effective Date: 21/08/2012, Version: 1 | Outage
V-SA Export | #R008664_020_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008664_020_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008887_005_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V>>S_KHTB2_SETB_KHTB, Effective Date: 05/06/2013, Version: 1 | Outage
V-SA Export | #R009035_008_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>S_TBTU_TBCG_TBMO, Effective Date: 07/08/2013, Version: 1 | Outage
V-SA Export | #R009166_023_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V_HYML1_4, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009476_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009491_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009525_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | V>>S_KHKN_SETB_SGKH | 0.4 (29.8) | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line OL on trip of South East - Tailem Bend 275 kV line | Outage
V-SA Export | #R008436_002_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>S_HYML_1, Effective Date: 21/08/2012, Version: 1 | Outage
V-SA Export | #R008438_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 13/04/2010, Version: 1 | Outage
V-SA Export | #R008596_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008638_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008658_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008793_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-SA Export | #R008887_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>S_KHTB2_SETB_KHTB, Effective Date: 05/06/2013, Version: 1 | Outage
V-SA Export | #R009035_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>S_TBTU_TBCG_TBMO, Effective Date: 07/08/2013, Version: 1 | Outage
V-SA Export | #R009039_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>S_TBTU_TBCG_TBMO, Effective Date: 07/08/2013, Version: 1 | Outage
V-SA Export | #R009183_024_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V_HYML1_5, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009347_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>S_KNPW_SETB_SGKH, Effective Date: 08/10/2013, Version: 1 | Outage
V-SA Export | #R009361_007_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>S_PWSE_SETB_SGKH, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009725_004_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | CA_SPS_41C52A3F_01 | 0.3 (0) | Constraint Automation, O/L DDTS_SHTS_220 @DDTS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-SA Export | F_ESTN++MLSY_L5 | 0.3 (0) | Out = one Moorabool to Sydenham (MLTS-SYTS) line Eastern Lower 5 min Requirement | Outage
V-SA Export | V^^S_CGMB_SECP_MAXG2 | 0.3 (0) | Out = Cherry Gardens - Mt Barker 132kV line and South East 275 kV capacitor O/S; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage
V-SA Export | #R008302_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V>>S_HYML_2, Effective Date: 21/08/2012, Version: 1 | Outage
V-SA Export | #R008442_015_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 13/04/2010, Version: 1 | Outage
V-SA Export | #R008605_010_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMBVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008605_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008974_003_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V^^S_TBTX4_MAXG, Effective Date: 13/05/2013, Version: 1 | Outage
V-SA Export | #R009137_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::S_XKHTB1+2_SETB, Effective Date: 26/08/2013, Version: 1 | Outage
V-SA Export | #R009159_023_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V_HYML1_4, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009159_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V_HYML1_4, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009199_024_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V_HYML1_5, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009203_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009710_004_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint S>>X_TBTU+CB_TBCG_1, Effective Date: 02/12/2013, Version: 1 | Outage
V-SA Export | #R009710_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint S>>X_TBTU+CB_TBCG_1, Effective Date: 02/12/2013, Version: 1 | Outage
V-SA Export | #R009715_006_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V^^S_PAVC_MAXG, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009725_004_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | V>S_NIL_NIL_HYTX2 | 0.3 (29.9) | Out = NIL, avoid O/L Heywood M2 500/275 kV transformer for NIL trip, flow from VIC to SA, feedback | NIL
V-SA Export | #R008605_011_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008648_008_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_2RPVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008658_023_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008974_003_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V^^S_TBTX4_MAXG, Effective Date: 13/05/2013, Version: 1 | Outage
V-SA Export | #R009119_006_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009194_024_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V_HYML1_5, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009347_010_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>S_KNPW_SETB_SGKH, Effective Date: 08/10/2013, Version: 1 | Outage
V-SA Export | #R009352_008_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>S_KNPW_SETB_SGKH, Effective Date: 08/10/2013, Version: 1 | Outage
V-SA Export | #R009601_009_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009715_006_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V^^S_PAVC_MAXG, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #V-SA_RAMP_I_F | 0.2 (2.8) | V-SA >= MIN(-70, InitialFlow + 50) (Wt=35) | Outage
V-SA Export | F_ESTN++HYTR_L6 | 0.2 (0) | Out = Heywood to Tarrone (HYTS-TRTS) line, Eastern Lower 6 sec Requirement | Outage
V-SA Export | S>>NIL_SETB_KHTB1 | 0.2 (0) | Out = Nil, avoid O/L Keith - Tailem Bend #1 132kV on trip of South East - Tailem Bend 275kV line, Feedback | NIL
V-SA Export | V::S_MOTB_MAXG_2 | 0.2 (0) | Out= Mobilong - Tailem Bend 132kV line; Vic to SA Transient Stability limit for loss of the largest generator in SA (NOTE: NPS and Playford PS assumed to be O/S). | Outage
V-SA Export | V>>S_KHTB2_SETB_KHTB | 0.2 (0) | Out = Keith - Tailem Bend #2 132 kV line. Prevent Keith - Tailem Bend #1 line OL on trip one of the South East - Tailem Bend lines. | Outage
V-SA Export | V^^S_KHKN_MAXG | 0.2 (5.9) | Out= Keith - Kincraig 132 kV line; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. | Outage
V-SA Export | #R008176_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYSEQD_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008302_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>S_HYML_1, Effective Date: 21/08/2012, Version: 1 | Outage
V-SA Export | #R008438_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008441_002_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>S_HYML_1, Effective Date: 21/08/2012, Version: 1 | Outage
V-SA Export | #R008604_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 13/04/2010, Version: 1 | Outage
V-SA Export | #R008648_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_2RPVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008658_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_LTWGVA_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008664_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MSUTVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
V-SA Export | #R008793_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-SA Export | #R009003_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::S_TBCB6594_MAXG_2, Effective Date: 26/07/2013, Version: 1 | Outage
V-SA Export | #R009039_008_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V>>S_TBTU_TBCG_TBMO, Effective Date: 07/08/2013, Version: 1 | Outage
V-SA Export | #R009048_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
V-SA Export | #R009119_006_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009166_023_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V_HYML1_4, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009177_024_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V_HYML1_5, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009177_024_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V_HYML1_5, Effective Date: 05/09/2012, Version: 1 | Outage
V-SA Export | #R009191_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009203_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009361_007_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>S_PWSE_SETB_SGKH, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009476_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009525_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009601_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | #R009627_006_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint VS_250, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Export | S>>X_TBTU+CB_TBCG_2 | 0.1 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Snuggery - Keith 132kV on trip of Tailem Bend - Cherry Gardens 275kV line, Feedback | Outage
V-SA Export | V::S_NIL_TBSE | 0.1 (0) | Out = Nil; Vic to SA Transient Stability limit for loss of one of the Tailembend-South East 275kV lines (South East Capacitor Available) with NPS and Playford assumed to be OOS. | NIL
V-SA Export | V>>S_KHKN_NIL_SGKH | 0.1 (0) | Out = Keith - Kincraig 132 kV line; avoid Snuggery - Keith line (continuous rating) OL on nil trip. | NIL
V-SA Export | V^^S_NIL_MAXG-10MW | 0.1 (0) | System normal limit -10 MW offset; Vic to SA Long Term Voltage Stability limit for loss of the largest generation block in SA. (South East Capacitor Available) | NIL
V-SA Export | V^^S_TBCP_SETB | 0.1 (0) | Out= Tailem Bend 275kV Cap Bank (Tungkillo 275kV Cap available); Vic to SA Long Term Voltage Stability limit for loss of South East-Tailembend 275kV line (Note: with NPS and Playford PS assumed to be O/S) (Swamp out if SA demand less/equal to 3200MW) | Outage
V-SA Import | S>>V_NIL_SETX_SETX | 445.7 (422.3) | Out = Nil, avoid overloading a South East 275/132 kV transformer on trip of the remaining South East 275/132 kV transformer | NIL
V-SA Import | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 183.0 (149.3) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
V-SA Import | F_S++HYSE_L60 | 58.4 (135.3) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 60 second requirement | Outage
V-SA Import | S>>V_NIL_NOTI_NOTI_3 | 15.1 (0) | Out = Nil with Torrens Island 66kV CB6W2, CB6W3 & CB6E6 open; avoid O/L of Torrens Island - New Osborne 66kV No.4 line on trip of Torrens Island - New Osborne 66kV No.3 line | NIL
V-SA Import | F_S++HYML_L60 | 10.7 (40.2) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 60 second requirement | Outage
V-SA Import | S>>V_KNPW_SETX_SETX | 7.5 (1.8) | Out = Kincraig to Penola West 132 kV line, avoid overloading the remaining South East 275/132kV transformer on trip of one South East 275/132kV transformer The Out= Kincraig - Penola West 132 kV line was out for 0.6 days in 2013 compared to 10.9 days in 2012 | Outage
V-SA Import | F_S++HYSE_L5 | 6.3 (26.8) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 5 minute requirement One Heywood to South East 275 kV line was out for 22.6 days in 2013 compared to 34.1 days in 2012 | Outage
V-SA Import | V>>N_SMTXF2_2 | 6.3 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Ballarat to Bendigo 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage
V-SA Import | F_S++HYSE_L6 | 5.7 (27.8) | Out = one Heywood to South East 500 kV line or one Heywood 500/275 kV (M1 or M2) transformer, SA lower 6 second requirement One Heywood to South East 275 kV line was out for 22.6 days in 2013 compared to 34.1 days in 2012 | Outage
V-SA Import | V>>V_SMTXF2_4AR | 5.3 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Richmond to Brunswick 220 kV cable on trip of Rowville A1 500/220 kV transformer | Outage
V-SA Import | CA_SPS_40D62A5B_01 | 4.8 (0) | During the outage of Hazelwood A2 500/220kV transformer with the Victorian network configured in 3/5 Parallel at Hazelwood four Yallourn units tripped. RTCA (Real Time Contingency Analysis) indicated that trip of Hazelwood to Yallourn No.1 or No.2 would cause overload on the remaining line. Constraint Automation was used to manage this issue. The Constraint Automation Set. Generated by STNET[NORFL] Host NOREEMP3(SP) was out for 0.4 days in 2013 compared to 0 days in 2012 | Outage
V-SA Import | S>>X_TBTU+CB_CGTB_4 | 4.3 (0) | Out= Tailem Bend - Tungkillo 275kV line and Tailem Bend CB6594 & CB6595, avoid O/L Mobilong - Tailem Bend 132kV on trip of Cherry Gardens - Tailem Bend 275kV line, Feedback | Outage
V-SA Import | F_S++HYML_L6 | 2.2 (15.2) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 6 second requirement The Heywood to Mortlake No.2 500 kV line was out for 3.1 days in 2013 compared to 7.5 days in 2012 | Outage
V-SA Import | #V-SA_RAMP_I_F | 1.8 (4.6) | V-SA >= MIN(-70, InitialFlow + 50) (Wt=35) | Outage
V-SA Import | SV_200 | 1.2 (0) | SA to Victoria on VicSA upper transfer limit of 200 MW | Outage
V-SA Import | CA_SPS_3FFA5B9A_01 | 1.0 (0) | Constraint Automation, O/L BATS_BETS_220 @BATS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
V-SA Import | #R009347_004_RAMP_F | 0.8 (0) | Hard Ramping constraint for constraint S>>V_KNPW_SETX_SETX, Effective Date: 08/10/2013, Version: 1 | Outage
V-SA Import | F_S++HYML_L5 | 0.8 (15.8) | Out = one Heywood to Moorabool 500 kV line or one Moorabool to Sydenham 500 kV line, SA lower 5 minute requirement | Outage
V-SA Import | V>>V_KTS_TX_A2_2_P | 0.8 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
V-SA Import | V>>V_SMTXF2_3P | 0.8 (0) | Out = South Morang F2 500/330 kV txfmr, avoid O/L Richmond to Brunswick 220 kV cable on NIL trip, 3/5 parallel mode, feedback | Outage
V-SA Import | #R009193_002_RAMP_F | 0.6 (0) | Hard Ramping constraint for constraint SV_200, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Import | S>>V_NIL_NOTI_NOTI_4 | 0.6 (0) | Out = Nil with Torrens Island 66kV CB6W2, CB6W3 & CB6E6 open; avoid O/L of Torrens Island - New Osborne 66kV No.3 line on trip of Torrens Island - New Osborne No.4 | NIL
V-SA Import | #R009158_002_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint SV_200, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Import | #R009165_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint SV_200, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Import | #R009176_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint SV_200, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Import | #R009182_002_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint SV_200, Effective Date: 21/08/2013, Version: 1 | Outage
V-SA Import | #R009221_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2_P, Effective Date: 03/12/2012, Version: 1 | Outage
V-SA Import | #R009347_004_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint S>>V_KNPW_SETX_SETX, Effective Date: 08/10/2013, Version: 1 | Outage
V-SA Import | #R009507_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_SMTXF2_3P, Effective Date: 03/12/2012, Version: 1 | Outage
V-SA Import | S>>V_NIL_TBSE_KHSG | 0.1 (0) | Out= Nil, avoid O/L Keith - Snuggery 132 kV on trip of Tailem Bend - South East 275kV line, Feedback | NIL
V-SA Import | V_APHY1_2_1 | 0.1 (0) | Out = Heywood to APD No. 1 500 kV line section only, both Heywood 500/275 kV txfmrs in service, limit voltage unbalance at the APD 500 kV bus | Outage
VIC1-NSW1 Export | V>>V_NIL_2A_R & V>>V_NIL_2B_R & V>>V_NIL_2_P | 188.0 (161.0) | Out = Nil, avoid overloading the South Morang 500/330 kV (F2) transformer for no contingencies, for radial/parallel modes and Yallourn W1 on the 500 or 220 kV | NIL
VIC1-NSW1 Export | V>>SML_NIL_7A | 71.5 (13.6) | Out = Nil, avoid overloading Ballarat North to Buangor 66 kV line on trip of the Ballarat to Waubra to Horsham 220 kV line | NIL
VIC1-NSW1 Export | V>>V-MSUT_1 | 40.8 (0) | Out = Murray to Upper Tumut (65) 330 kV line, avoid overloading Dederang to Wodonga 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | Outage
VIC1-NSW1 Export | V>>V_NIL1A_R | 30.1 (46.0) | Out = Nil, avoid overloading a South Morang to Dederang 330 kV line for trip of the parallel line | NIL
VIC1-NSW1 Export | V>>SML_NIL_8 | 28.8 (0.3) | Out = Nil, avoid overloading Ballarat to Bendigo 220 kV line for loss of Shepparton to Bendigo 220 kV line | NIL
VIC1-NSW1 Export | V::N_HYSE_xxx | 21.0 (38.8) | Out = Heywood to South East 275 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line One Heywood to South East 275 kV line was out for 67.7 days in 2013 compared to 102.4 days in 2012 | Outage
VIC1-NSW1 Export | V>>SML_NIL_7B | 18.2 (2.8) | Out = Nil, avoid overloading Buangor to Arrarat 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
VIC1-NSW1 Export | V::N_MSUT_xxx | 15.8 (15.4) | Out = Upper Tumut to Murray 330 kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500 kV line The Murray to Upper Tumut (65) 330 kV line was out for 18.0 days in 2013 compared to 9.0 days in 2012 | Outage
VIC1-NSW1 Export | V>>SML_NIL_1 | 13.1 (3.3) | Out = Nil, avoid overloading Ballarat to Moorabool No.1 220 kV line on trip of parallel No.2 line This constraint equation binds during periods of high demands in the Victorian state grid (220 kV system in northern western Victoria) and for periods when Murraylink is constrained from Vic to SA (mainly due to S>V_NIL_NIL_RBNW). AEMO expects this constraint equation to bind during summer until the regional Victorian thermal upgrade is completed. | NIL
VIC1-NSW1 Export | V::N_NILxxx | 9.0 (364.0) | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | NIL
VIC1-NSW1 Export | V::N_HWSM_V1 | 6.3 (0) | Out = Hazelwood to South Morang 500 kV line, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, VIC accelerates, Basslink TAS to VIC, Yallourn W Unit 1 on 220 kV. | Outage
VIC1-NSW1 Export | V>>N_SMTXF2_2 | 6.2 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Ballarat to Bendigo 220 kV line on trip of Ballarat to Waubra to Horsham 220 kV line | Outage
VIC1-NSW1 Export | V>>V_NIL_5 | 5.1 (6.8) | Out = Nil, avoid overloading either Mount Beauty to Dederang 220 kV line (flow to North) for trip of the other Mount Beauty to Dederang 220 kV line | NIL
VIC1-NSW1 Export | V>>N-NIL_HA | 2.9 (9.3) | Out = Nil, avoid overload on Murray to Upper Tumut (65) 330 kV line on trip of Murray to Lower Tumut (66) 330 kV line | NIL
VIC1-NSW1 Export | V>>N_DDMS_2 | 2.7 (4.9) | Out = Dederang to Murray 330 kV line, avoid O/L Dederang to Wodonga 330 kV line (flow North) for trip the remaining Murray to Dederang 330 kV line, feedback | Outage
VIC1-NSW1 Export | N>>N-RGSW_A | 2.1 (0) | Out = Regentville to Sydney West(38), avoid Bayswater to Liddell(34) O/L on Bayswater to Liddell(33) trip; Feedback | Outage
VIC1-NSW1 Export | V::N_LTWG_xxx | 2.0 (0) | Out = Lower Tumut to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V::N_SMF2_S1 | 1.9 (0) | Out = South Morang F2 500/330 kV txfmr, prevent transient instability for fault and trip of a Hazelwood to South Morang 500 kV line, SA accelerates, Basslink TAS to VIC, YWG1 220 kV. Limit only applied during Heywood flow from SA to VIC | Outage
VIC1-NSW1 Export | NRM_VIC1_NSW1 | 1.8 (4.6) | Negative Residue Management constraint equation for VIC to NSW flow | NIL
VIC1-NSW1 Export | V>>SML_NIL_7C | 1.3 (0) | Out = Nil, avoid O/L Arrarat to Stawell 66kV line for loss of the Ballarat to Waubra to Horsham 220kV line | NIL
VIC1-NSW1 Export | V>>V_SMTXF2_6 | 1.3 (0) | Out = South Morang F2 500/220 kV txfmr, avoid O/L of a Thomastown to South Morang 220 kV line for trip of the parallel Thomastown to South Morang 220 kV line, feedback | Outage
VIC1-NSW1 Export | N>>N-NIL_1A_OPENED | 1.2 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
VIC1-NSW1 Export | CA_SPS_3FFA5B9A_01 | 1.0 (0) | Constraint Automation, O/L BATS_BETS_220 @BATS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
VIC1-NSW1 Export | V::N_2RP_xxx | 0.9 (0) | Out = 2 dynamic reactive plant from Vic metro or SESS SVC's, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | V>>V_KTS_TX_A2_2_P | 0.8 (0) | Out = Keilor A2 or A4 500/220 kV txfmr, avoid pre-contingent O/L of South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
VIC1-NSW1 Export | V>>N-JNWG_RADIAL_1 | 0.6 (0) | Out = Jindera to Wagga(62), avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback | Outage
VIC1-NSW1 Export | #R008583_029_RAMP_F | 0.5 (0) | Hard Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 22/09/2009, Version: 1 | Outage
VIC1-NSW1 Export | V::N_BYPASS_HW_SY_VE | 0.5 (0) | Out = Three SMTS 500kV CBs for HWTS and SYTS line (No.1 or No.2), temporary bypass for HWTS to SYTS direct line, avoid trans. instability for fault and trip of a HWTS-SYTS or HWTS-SMTS 500kV line, Basslink VIC to TAS, VIC accelerates, segment 2 | Outage
VIC1-NSW1 Export | #R008414_026_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V_SMTXF2_6, Effective Date: 03/12/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008438_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HYSEVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008583_029_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V>>V-MSUT_1, Effective Date: 22/09/2009, Version: 1 | Outage
VIC1-NSW1 Export | #R008596_011_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008605_011_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008638_023_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008664_020_RAMP_F | 0.4 (0) | Hard Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008664_020_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_MSUTVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R009476_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009491_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009525_009_RAMP_V | 0.4 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | N>>N-CNUT_HA | 0.4 (0) | Out = Canberra-UpperTumut(1), avoid Upper Tumut to Lower Tumut(64) O/L on Upper Tumut to Yass(2) trip; Feedback | Outage
VIC1-NSW1 Export | V::N_JNWG_xxx | 0.4 (0) | Out = Jindera to Wagga 330kV line, avoid transient instability for fault and trip of a Hazelwood to South Morang 500kV line, Basslink TAS to VIC, VIC accelerates, segment 1 | Outage
VIC1-NSW1 Export | #R008414_026_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V>>V_SMTXF2_6, Effective Date: 03/12/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008596_011_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008638_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008648_008_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_2RPVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008658_023_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008793_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
VIC1-NSW1 Export | V>>SML_BAML2_1 | 0.3 (0) | Out = Moorabool to Elaine to Ballarat 220 kV line (complete line or line sections), prevent overload of the Moorabool to Ballarat No. 1 220 kV line for trip of the Moorabool to Terang 220 kV line, feedback | Outage
VIC1-NSW1 Export | #R008605_011_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint V::N_EPMBVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008619_005_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N>>N-RGSW_A, Effective Date: 06/05/2011, Version: 2 | Outage
VIC1-NSW1 Export | #R008619_005_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint N>>N-RGSW_A, Effective Date: 06/05/2011, Version: 2 | Outage
VIC1-NSW1 Export | #R009203_009_RAMP_V | 0.3 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R008648_009_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_2RPVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008658_023_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_LTWGVB_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R009170_019_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V::N_BUDPVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009507_024_RAMP_V | 0.2 (0) | Soft Ramping constraint for constraint V>>V_SMTXF2_6, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009601_009_RAMP_F | 0.2 (0) | Hard Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | V>>V_ROTS_TX_2_P | 0.2 (0) | Out= Rowville A1 or A2 500/220 kV txfmr, avoid pre-contingent overload of the South Morang F2 500/330 kV txfmr, parallel mode, feedback | Outage
VIC1-NSW1 Export | #R008176_005_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HYSEQD_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008423_050_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>N-WA_330_BUSB_1, Effective Date: 13/04/2010, Version: 1 | Outage
VIC1-NSW1 Export | #R008648_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_2RPVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008658_022_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_LTWGVA_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008664_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_MSUTVC_R, Effective Date: 16/02/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R008793_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009048_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009048_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 05/04/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009141_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009191_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009203_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009221_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_KTS_TX_A2_2_P, Effective Date: 03/12/2012, Version: 1 | Outage
VIC1-NSW1 Export | #R009476_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009525_009_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V::N_HWSM_V1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | #R009601_009_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint V::N_SMCSVB_R, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Export | N>>N-NIL_1A_CLOSED | 0.1 (0) | Out=Nil, avoid Bayswater to Liddell (33 or 34) O/L on loss of other Bayswater to Liddell (34 or 33), Feedback | NIL
VIC1-NSW1 Export | V>>N-CNUT_HB_15M | 0.1 (0) | Out = Canberra-UpperTumut(1), avoid Murray to Lower Tumut(66) O/L on Murray to Upper Tumut(65) trip; Feedback | Outage
VIC1-NSW1 Export | V>>N-MSUT_2 | 0.1 (0) | Out = Murray to Upper Tumut(65), avoid Murray to Lower Tumut(66) O/L on Nil trip; Feedback | Outage
VIC1-NSW1 Import | N^^V_NIL_1 | 102.1 (108.1) | Out = Nil, avoid voltage collapse for loss of the largest Victorian generating unit | NIL
VIC1-NSW1 Import | N>>V_DBUSS_1 | 34.7 (0) | Out = Dederang DBUSS - line control scheme, avoid overload of a Murray to Dederang line for trip of the remaining Murray to Dederang line | Outage
VIC1-NSW1 Import | N^^V_NIL_2 | 21.0 (4.9) | Out = Nil, avoid voltage collapse for loss of a Dederang to Murray 330 kV line | NIL
VIC1-NSW1 Import | V>>V_NIL_1B | 13.5 (7.3) | Out = Nil, avoid overloading Dederang to Murray No.2 330 kV line for trip of the Dederang to Murray No.1 330 kV line | NIL
VIC1-NSW1 Import | V>>V_SMTXF2_4AR | 5.3 (0) | Out = South Morang F2 500/330 kV transformer, avoid overloading Richmond to Brunswick 220 kV cable on trip of Rowville A1 500/220 kV transformer | Outage
VIC1-NSW1 Import | CA_SPS_40D62A5B_01 | 4.6 (0) | During the outage of Hazelwood A2 500/220kV transformer with the Victorian network configured in 3/5 Parallel at Hazelwood four Yallourn units tripped. RTCA (Real Time Contingency Analysis) indicated that trip of Hazelwood to Yallourn No.1 or No.2 would cause overload on the remaining line. Constraint Automation was used to manage this issue. The Constraint Automation Set. Generated by STNET[NORFL] Host NOREEMP3(SP) was out for 0.6 days in 2013 compared to 0 days in 2012 | Outage
VIC1-NSW1 Import | NRM_NSW1_VIC1 | 3.6 (1.8) | Negative Residue Management constraint equation for NSW to VIC flow This constraint equation is part of the automated negative residue process which was implemented in July 2012. | NIL
VIC1-NSW1 Import | N^^V_MSDD2 | 1.9 (2.4) | Out = Dederang to Murray 330 kV line, avoid voltage collapse for trip of the remaining Dederang to Murray 330 kV line One Dederang to Murray (67 or 68) 330 kV line was out for 1.5 days in 2013 compared to 9.2 days in 2012 | Outage
VIC1-NSW1 Import | N^^V_MSUT_1 | 1.8 (1.6) | Out = Murray to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink The Murray to Upper Tumut (65) 330 kV line was out for 9.0 days in 2013 compared to 4.5 days in 2012 | Outage
VIC1-NSW1 Import | N^^V_LTUT_1 | 1.7 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for trip of the largest Victorian generating unit or Basslink The Lower Tumut to Upper Tumut (64) 330 kV line was out for 22.2 days in 2013 compared to 2.5 days in 2012 | Outage
VIC1-NSW1 Import | N^^V_LTUT_2 | 1.4 (0) | Out = Lower Tumut to Upper Tumut 330 kV line, avoid voltage collapse for loss of a Dederang to Murray 330 kV line The Lower Tumut to Upper Tumut (64) 330 kV line was out for 44.4 days in 2013 compared to 5.0 days in 2012 | Outage
VIC1-NSW1 Import | V>>V_NIL_3 | 1.3 (0.3) | Out = Nil, avoid overloading either Dederang to South Morang 330 kV line for trip of the parallel line | NIL
VIC1-NSW1 Import | N>>N-DP_TIETX_A | 1.1 (0) | Out= DarlingtonPt tie Tx(#3 or #4), avoid the remaining tie Tx O/L (330 to 220 kV) on Kerang-Bendigo trip; Feedback | Outage
VIC1-NSW1 Import | N>>N-KVCW_9 | 1.1 (0) | Out = KangarooValley to Capital(3W), avoid Yass to Canberra(9) O/L on Yass to Lower Tumut(3) trip; Feedback | Outage
VIC1-NSW1 Import | N>>V-NIL_O | 1.1 (0.1) | Out = Nil, avoid overloading Upper Tumut to Murray (65) 330 kV line on trip of Lower Tumut to Wagga (051) 330 kV line and subsequent tripping of 970, 990 and 99M (out of Yass) 132 kV lines This constraint equation models a control scheme for the 132 kV lines between Wagga and Yass. These lines are consecutively tripped if they overload on trip of 051 line (unless the Wagga to Yass 132 kV network is radialised under high import into NSW from Victoria). | NIL
VIC1-NSW1 Import | V>>V_SMTXF2_3P | 0.8 (0) | Out = South Morang F2 500/330 kV txfmr, avoid O/L Richmond to Brunswick 220 kV cable on NIL trip, 3/5 parallel mode, feedback | Outage
VIC1-NSW1 Import | CA_SPS_41C52A3F_01 | 0.7 (0) | Constraint Automation, O/L DDTS_SHTS_220 @DDTS for CTG MVPF on trip of DDTS-GNTS #1 & #3 220KV LINES. Generated by STNET[NORFL] Host NOREEMP3(SP) | Outage
VIC1-NSW1 Import | N>>N-BYYS_4 | 0.6 (0) | Out = Bannaby to Yass(61), avoid Marulan to Yass(4) O/L on Marulan-Yass(5) trip; Feedback | Outage
VIC1-NSW1 Import | V>>V_NIL_4A | 0.5 (0.1) | Out = Nil, avoid overloading Dederang No.1 330/220 kV transformer for no contingencies, DBUSS - Transformer control scheme armed. | NIL
VIC1-NSW1 Import | #R008882_010_RAMP_F | 0.3 (0) | Hard Ramping constraint for constraint N^^V_LTMS, Effective Date: 06/07/2012, Version: 1 | Outage
VIC1-NSW1 Import | #R008727_018_RAMP_V | 0.1 (0) | Soft Ramping constraint for constraint N^^V_LTUT_1, Effective Date: 06/07/2012, Version: 1 | Outage
VIC1-NSW1 Import | #R008875_010_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^V_LTMS, Effective Date: 06/07/2012, Version: 1 | Outage
VIC1-NSW1 Import | #R009364_001_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint N^^V_DDMB_1, Effective Date: 21/08/2013, Version: 1 | Outage
VIC1-NSW1 Import | #R009507_021_RAMP_F | 0.1 (0) | Hard Ramping constraint for constraint V>>V_SMTXF2_3P, Effective Date: 03/12/2012, Version: 1 | Outage
VIC1-NSW1 Import | N>>V-NIL_N | 0.1 (0) | Out= Nil, avoid LowerTumut to Murray (66) O/L on LowerTumut-Wagga (051) + 970,990,99M ex_Yass lines trips; Feedback | NIL
VIC1-NSW1 Import | N^^V_DDMB_1 | 0.1 (1.9) | Out = Dederang to Mt Beauty 220 kV line, avoid voltage collapse for trip of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | N^^V_LTMS | 0.1 (0) | Out = Lower Tumut to Murray 330 kV line, avoid voltage collapse for trip of the largest Vic generating unit or Basslink | Outage
VIC1-NSW1 Import | V>>V_NIL_4C | 0.1 (0) | Out = Nil, avoid pre-contingent O/L of the Dederang H3 330/220kV transformer, DBUSS-Transformer control scheme armed, feedback | NIL

## Outages 2013
Constraint Set ID | 2013 DAYS (2012 DAYS) | Description
V-DBUSS_L | 233.0 (56.1) | Dederang DBUSS-Line control scheme
N-X_MBTE_2 | 214.9 (60.0) | Two Directlink cables
N-X_MBTE_3 | 158.1 (20.9) | All three Directlink cables
F-V-APHY_ONE | 87.7 (75.4) | Heywood to Alcoa Portland 500 kV line
T-MRWF_100 | 73.6 (0) | Discretionary 100 MW upper limit on Musselroe Wind Farm
S-NWRB2 | 31.8 (11.6) | North West Bend to Robertstown No.2 132 kV line
I-ML_ZERO | 27.2 (13.8) | Limit Murraylink to zero in either direction
I-HYSE | 22.6 (34.1) | One Heywood to South East 275 kV line
N-LTUT_64_15M | 22.2 (2.5) | Lower Tumut to Upper Tumut (64) 330 kV line
V-HYTX | 21.6 (28.5) | One Heywood 500/275 kV (M1 or M2) transformer
Q-CLTR_8810 | 18.0 (5.3) | Calvale to Tarong 275 kV line
N-EWMB_8505 | 15.9 (58.3) | One Ballina to Lennox Head to Ewingsdale to Mullumbimby 66 kV line (8504, 8505 or 8508) or Mullumbimby 132/66 kV transformer
T-MRWF_120 | 14.0 (0) | Discretionary 120 MW upper limit on Musselroe Wind Farm
I-MSUT | 9.0 (4.5) | Murray to Upper Tumut (65) 330 kV line
V-BEKG | 8.2 (0) | Bendigo to Kerang 220 kV line
S-PA_VC_1 | 6.4 (1.8) | One Para SVC
N-EWMB_9G5 | 6.1 (0) | One Ballina to Lennox Head to Sufolk Park to Ewingsdale to Mullumbimby 132 kV line
N-ARTW_86 | 4.7 (2.0) | Armidale to Tamworth (86) 330 kV line
S-BNMT | 4.5 (0.9) | Blanche to Mt Gambier 132 kV line
S-PWSE | 4.4 (11.5) | Penola West to South East 132 kV line
N-KKLS_967 | 3.8 (9.1) | Koolkhan to Lismore (967) 132 kV line
V-SMTXF2 | 2.7 (0.2) | South Morang 500/330 kV (F2) transformer
V-HWSM | 2.5 (1.7) | Hazelwood to South Morang 500 kV line
N-BWMP_ONE | 2.5 (0.2) | Bayswater to Mt. Piper or Bayswater to Wollar or Wollar to Mt. Piper 500 kV line
N-CHLS_89 | 2.2 (1.3) | Coffs Harbour to Lismore (89) 330 kV line
V-HYTR | 2.1 (1.0) | Heywood to Tarrone 500 kV line
V-DDMS | 1.5 (9.2) | One Dederang to Murray (67 or 68) 330 kV line
NSA-Q_BARCALDN | 1.2 (1.1) | Clermont to Lilyvale (7153) 132 kV line, Network Support Agreement for Barcaldine GT to meet local islanded demand at Clermont and Barcaldine This NSA constraint set is included as it is only invoked under outage conditions
V-HWCB4 | 1.2 (1.6) | Hazelwood to Cranbourne No.4 500 kV line
V-EPTT_R | 1.2 (16.1) | Eildon to Thomastown 220 kV line
F-N-ARDM_ONE | 1.1 (0.8) | One Armidale to Dumaresq (8C or 8E) 330 kV line
I-BCDM_ONE | 1.1 (0) | One Bulli Creek to Dumaresq 330 kV line
F-I-BCDM_ONE | 1.1 (0) | One Bulli Creek to Dumaresq 330 kV line - FCAS Requirements
N-ARTW_MPP_N-2 | 1.0 (0) | Armidale to Tamworth 330 kV line
V-HWRO3 | 1.0 (2.1) | Hazelwood to Rowville No.3 500 kV line
S-LB3_0 | 0.9 (0.8) | Discretionary upper limit for Lake Bonney 3 generation of 0 MW
V-HYMO | 0.9 (6.5) | Heywood to Mortlake No.2 500 kV line
S-X_MTSE+PAVC_1 | 0.7 (0) | Mt. Gambier to South East 132 kV line and Para SVC 1 or Para SVC 2
S-SESG | 0.6 (0) | South East to Snuggery 132 kV line
S-PA_WEST_BUS_R | 0.5 (0) | Para 275 kV West Bus Right Section
Q-HACL | 0.5 (0) | Out= 8810 or 8811 H24 Calvale to S2 Halys 275 kV feeder
S-KNPW | 0.5 (10.9) | Out= Kincraig - Penola West 132 kV line
S-BNSG | 0.3 (0.3) | Out = Blanche - Snuggery 132 kV line
N-ARTW_85 | 0.3 (0.7) | Armidale to Tamworth (85) 330 kV line
V-MLTR | 0.3 (0.6) | Moorabool to Tarrone No.1 500 kV line
CA_SPS_40D62A5B | 0.2 (0) | Constraint Automation Set. Generated by STNET[NORFL] Host NOREEMP3(SP)
V-BAHO | 0.2 (3.0) | Out = Ballarat to Waubra to Horsham 220kV line
S-X_KNPW+PAVC_1 | 0.1 (0) | Out= Kincraig - Penola West 132kV line and Para SVC 1 or 2 O/S
S-MYTX1_44248OPEN | 0.1 (0) | Out = Mayura No.1 132/33kV transformer O/S (with 33kV bus tie isolator 44248 open)

## Outage stats 2013
TNSP | Unplanned | Short Notice | ≤ 30 days | > 30 days
APT 2009 | 14 | 33 | 5 | 4
2010 | 25 | 40 | 6 | 2
2011 | 15 | 31 | 5 | 4
2012 | 15 | 23 | 2 | 1
2013 | 10 | 7 | 0 | 1
ElectraNet 2009 | 51 | 145 | 186 | 154
2010 | 104 | 226 | 186 | 226
2011 | 59 | 201 | 364 | 186
2012 | 240 | 457 | 582 | 424
2013 | 200 | 435 | 874 | 136
Essential E 2009 | 2 | 35 | 72 | 5
2010 | 5 | 34 | 62 | 11
2011 | 3 | 58 | 127 | 1
2012 | 15 | 83 | 177 | 0
2013 | 19 | 41 | 81 | 0
Powerlink 2009 | 136 | 455 | 767 | 4
2010 | 88 | 451 | 832 | 32
2011 | 114 | 445 | 722 | 12
2012 | 317 | 885 | 1219 | 26
2013 | 301 | 812 | 1183 | 96
SPAusNet 2009 | 152 | 970 | 893 | 66
2010 | 158 | 817 | 757 | 38
2011 | 147 | 794 | 650 | 11
2012 | 234 | 972 | 738 | 36
2013 | 146 | 895 | 502 | 56
Transend 2009 | 40 | 138 | 122 | 47
2010 | 41 | 143 | 112 | 62
2011 | 17 | 115 | 97 | 92
2012 | 57 | 279 | 250 | 83
2013 | 111 | 550 | 496 | 281
TransGrid 2009 | 138 | 668 | 792 | 279
2010 | 123 | 816 | 782 | 384
2011 | 129 | 602 | 873 | 534
2012 | 198 | 533 | 900 | 629
2013 | 251 | 452 | 849 | 590