## Existing SWIS SPS (hidden)
Existing SWIS Special Protection Schemes
No | Name of Scheme | Location - substation or line | Area | Type of scheme |  | Description of what it protects against and why | Settings (stage 1/2/3 voltage, thermal, delays and triggers) | Status (Active/Inactive/Not sure) | Date installed | Control Room Instruction | DM/other source references | Name of person (not initials)
|  |  |  | Tx | Dx
1 | Modification of SLOR S of Walkaway Windfarm's runback scheme | KRA,GPA,Telsa PPG | NC | Thermal |  | • If LinesMUC-MOR 81 or TS-ENB81 are overloaded and power is flowing in the north direction, the Karara Load Shedding Scheme should be initiated. • Tesla PPG should be to curtail/trip the PPG under the same conditions as when Walkaway Windfarm would be runback . • When the line is overloaded on MUC-MOR or ENB-TS in the north direction, the GPA load should be shed (via tripping RAN304) | DM# 8667045 | Active | 2012 |  | DM #7296274 DM# 2227648 DM# 1909475 DM# 9163872 DM# 9031214 DM# 9526883 DM# 9780313 DM #7296274 DM# 2227648 DM# 1909475 DM# 9163872 | Sunny Zafar
2 | Top Iron Load Management | Top Iton Mine | NC | Thermal
3 | Newmont Load Management
4 | KRA Load Shedding Scheme | KRA, NBT, TST | NC | Thermal |  | Stage 1: For a reactive power treshold of greater than 70 MVAr, KRA sheds load to 50 MW |  | Inactive | When MWEP 1 commissions |  | DM 7296274 | JN
5 | KRA Load Shedding Scheme | KRA, NBT, TST | NC | Thermal |  | Stage 2:For a loss of NBT-NT 91 DUE TO FAULT, KRA sheds load to 30 MW. |  | Inactive | When MWEP 1 commissions |  | DM 7296274 | JN
6 | KRA UVLS | KRA | NC | Voltage |  | If votlage doesn't recover to above 0.8 for 1100 ms, KRA sheds load to 30 MW, 1 x KRA reactor close. |  | Inactive | When MWEP 1 commissions |  | DM 7296274 | JN
7 | KRA UVLS | KRA | NC | Voltage |  | If the TST 330 kV is not recovered to 0.85 pu after 2200 ms, TST-KRA line will trip from TST |  | Inactive | When MWEP 1 commissions |  | DM 7296274 | JN
8 | KRA OVPS 1 | KRA | NC | Voltage |  | Stage 1:Ifgreater than 1.2 pu at TST 330 kV, TST 22 kV reactor close 1s later. |  |  |  |  | DM 7296274 | JN
9 | KRA OVPS 1 | KRA | NC | Voltage |  | Stage 2: If greater than 1.1 pu, operate another TST 22 kV reactor 9s later. | [5 empty] | JN
10 | KRA OVPS 2 | KRA | NC | Voltage |  | If total load rejection occures, trips off TST-KRA 330 Kv within 110 ms. Total load rejection are: tripping of TST-KRA 91 from KRA, tripping of both transformer (either HV or LV breakers simultaneously) |  | Inactive | When MWEP 1 commissions |  | DM 7296274 | JN
11 | TST 330/132 kV transformer AVR Blocking | TST | NC | Voltage |  | In th event of NBT-TST 91 tripping, transformer AVR turn to manual controlling mode (OLTC off) to avoid unncessary tapping of transformer |  | Inactive | When MWEP 1 commissions |  | 10049322 | JN
12 | TST 330/132 kV transformer AVR Blocking | TST | NC | Voltage |  | If the voltage at TST 132 KV busbar is lower than 0.9 PU, AVR blocking activates 10s later |  | Inactive | When MWEP 1 commissions |  | 10049322 | JN
13 | EMD VRRS |  |  |  |  | Already in registers
14 | MBA and MGA DSOC sharing |  |  |  |  | Already in registers
15 | GTN GT and GRS sharing |  |  |  |  | Already in registers
16 | Islanding scheme at Three Springs | TS | NC | Load monitoring |  | Islanding MGA PS against synch. Instability | DM# 612163 | ? | 2000 |  | DM# 544246, 861864 | Henry Saffron
17 | IPP's islanding scheme at WKT | WKT | EGF | APLD relay |  | Islanding of IPP networks with unstable generation | Ask D. Tong | Yes | 1996 |  | Obsolete original in DM# 417544 and DM# 1505215 - Section 2.5.2 | Henry Saffron
18 | Sub-synchronous Instability Detectors | MRT & WKT | EGF | Detecting subharmonic resonance |  | against subharmonic resonance |  |  |  |  | DM# 1505215 - Section 2.5.5
19 | 220 KV AUTOMATIC VOLTAGE CONTROL SCHEME AT MUJA TERMINAL | MU | MU, EGF | adjust V for power transfer levels |  | 220 KV AUTOMATIC VOLTAGE CONTROL SCHEME AT MUJA TERMINAL | DM# 471314 | ? | 2000 |  | DM# 471314 | Henry Saffron
20 | UVLS | UVLS | NC | Voltage |  | UVLS | DM# 697359 | Yes | 2000 |  | DM# 703106 | Henry Saffron
21 | UVLS | UVLS | EC & EGF | Voltage |  | UVLS | DM# 2267471 |  | 2005 |  | DM# 2267471 & 1642020 | Henry Saffron
22 | OVER-VOLTAGE SCHEME AT MUNGARRA SUBSTATION | O/V | NC | Voltage |  | O/V | DM# 935938 | ? | 2001 |  | DM# 935938, 1404157 | Henry Saffron
23 | U/V scheme | NOR | EC | Voltage |  | trips NOR-MRT line for loss of MU-MRT | DM# 1182600 | ? | 2002 |  | DM# 1182600 - Section 3.3.1 | Henry Saffron
24 | Out-of-step Protection Scheme | WKT | EGF | out-of-step protectin scheme islanding IPP generation |  | Out-of-step Protection Scheme | WKT | ? | 2003 |  | DM# 1505215 - Section 2.5.3 | Henry Saffron
25 | Distribution Voltage Regulator Over Voltage Protection | Country | Country |  | Voltage | Downstream of voltage regulators sometimes a recloser is used to protect against over voltage, most common when a few VR's are in series. This can happen due to a VR's in boost configuration and load rejection occurs. If applied there should be a GUOI. | ? | ? | ? | ? | ? | Ashley O'Keeffe
26 | Distribution Negative Phase Sequence Protection | Country | Country |  | NPS | Low fault levels on 3phase lines can be mitigated by applying Negative Phase Sequence protection. If applied there should be a GUOI. | ? | ? | ? | ? | ? | Ashley O'Keeffe
27 | Distribution Negative Phase Sequence Protection - Isolation Transformers | Country | Country |  | NPS | Investigation into using NPS protection to provide backup on single phase lines downstream of isolation transformers. Note that this NPS is used to protect against earth fault and as such should be held to the same standard as EF. If applied there should be a GUOI. | ? | ? | ? | ? | ? | Ashley O'Keeffe
28 | Distribution Backup Protection | Country (see FZ596/1 or FZ597 as an example) | Country |  | ALL | If another recloser cannot be installed to provide appropriate backup protection, another recloser could be installed in series with the same settings but with an additional time. If applied there should be a GUOI. | ? | ? | ? | ? | ? | Ashley O'Keeffe
29 | Auto-Close | NT | NT |  | Auto-Close | If either of the NT T1 or T2 transformers trip (or directly connected bus sections) the auto-close scheme will close the other transformer onto the healthy bus. This may mitigate some overloads. | ? | Active | 2012 | ? | DM# 11715224 - Memo, DM# 10244579 - Close out, DM# 9704895 - Planning | Ashley O'Keeffe
23

## RCM Version history
Special schemes applicable to 2025 RCM
Version History | Date | Details
0 | 2025-05-30 | Align with Special Protection Scheme Register V7.6
Authorisation
| Date | Title | Name
Approver | 2025-05-30 | Principal Planning Engineer | Huuson Nguyen

## Scheme
Special schemes applicable to 2025 RCM
# | Name | Contingency/Trigger | Scheme response/ Outcome
1 | MARNET | ENT-YDT 91 is part of contingency | intertrip WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect WARRADARGE_WF1
|  | NBT-YDT 91 is part of contingency | intertrip ENT-YDT 91 & WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect YANDIN_WF1 and WARRADARGE_WF1
|  | NBT-NT 91 is part of contingency | intertrip NBT-YDT 91, ENT-YDT 91 & WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect YANDIN_WF1 and WARRADARGE_WF1
|  | ENT-TST 91 is part of contingency | runback KRA to 10.0MW | MRS, MDP, King Rocks wf, Kondinin wf
2 | 220kV inter-trip (some of listed generators will be disconnected by their anti-islanding protection) | CGT-YLN-WKT X1 | Disconnect CGW & King Rocks windfarm. Island EGF
|  | MRT-CGT X1 | Disconnect CGW & King Rocks windfarm. Intertrip CGT-YLN-WKT line. Island EGF
|  | KDN-MRT X1 | Disconnect MDP, CGW, MRS, MRT BESS & King Rocks windfarm. Intertrip MRT-CGT & CGT-YLN-WKT lines. Island EGF
|  | MU-NGS-KDN X1 | Disconnect MDP, CGW, MRS, MRT BESS, KDN windfarm & King Rocks windfarm. Intertrip MRT-CGT & CGT-YLN-WKT lines. Island EGF
3 | BGM runback (after connection of onsite generation) | PMT-WLT 91 | Run back the export from BGM to 160MW (=90% of operational summer rating (179MVA) of WLT-GLT 81) following loss of the WLT 330kV line; and Run back the import from BGM to 60MW following loss of the WLT 330kV line . After 1min (say), if any of these above fails, BGM will be disconnected almost immediately
4 | MRT-CNS-NOR decouple | MRT-CNS-NOR 81 overload (measured at MRT & NOR taking into account losses on NOR-CNS/MRT section) | Open MRT CB of MRT-CNS-NOR 81 line
5 | APJ | SNR-APJ/WGP overload (measured in to SNR) | Run back ALINTA_PNJ_U1 to 83.0MW first, if overload remains, disconnect this unit.
6 | WWF runback | HBK-MUC 81 overloaded (measured at both MUC and HBK ends) | Disconnect TESLA_GERALDTON_G1 then runback Alinta_WWF, if overload remains, disconnect Alinta_WWF
MOR-MUC 81 is overloaded (measured at MOR of MOR to MUC flow)
ENB-TS 81 is overloaded (measured at TS of TS to ENB flow)
MOR-TS 81 is overloaded (measured at both TS and MOR ends)
MGA-TS 81 is overloaded (measured at MGA of MGA to TS flow)
MGA-MBA 81 is overloaded (measured at MGA of MGA to MBA flow)
TS-MBA 81 is overloaded (measured at MBA of MBA to TS flow)
TST-TS 81 or 82 overloaded (measured at TS of TS to TST flow)
7 | TS bus coupler | TS806 overload (measured at TS of MGA to TS and MBA to TS flow) & GRSF ≥ 10MW | Run back GRSF first, if overload remains, disconnect this unit.
8 | NT 132kV bus coupler | A forced outage of one of NT 330kV transformers | NT 132kV bus couplers will close to re-mesh NT 132kV buses
9 | PIC-MRR intertrip | PIC-MRR overload (measured at PIC of PIC to MRR flow) | Disconnect MRR 526, 512 & 531 feeders
10 | PJR-YP manual intertrip | PJR-YP 81 overloaded (measured at PJR of PJR to YP flow) & NBT T2 oos under a defined system configuration | Manually take JDP-WNO 81 out of service
11 | KEM-MRR 81/82 manual intertrip | KEM-MRR 81 or 82 overloaded (measured at KEM of KEM to MRR flow) under a defined system configuration | Manually take MRR-PIC 81 out of service
12 | WGP manual intertrip | APJ-PNJ 81 overloaded (measured at APJ of APJ to PNJ flow) under a defined system configuration | Open WGP circuit breaker of WGP-APJ-SNR 81 line
CT-MSS-PNJ 81 overloaded (measured at PNJ of PNJ to T point flow) under a defined system configuration
PNJ-MH 81 overloaded (measured at PNJ of PNJ to MH flow) under a defined system configuration
13 | MUL-PBY manual intertrip | NT-BCT 81 overloaded (measured at NT of NT to BCT flow) under a defined system configuration | Take MUL-PBY 81 line out of service
14 | MU BTT2/BTT3 runback | MU BTT2 transfromer overloaded | Disconnect some East region generators to reduce transformer loading
MU BTT3 transfromer overloaded
15 | MRT T1/T2 runback | MRT T1 or T2 transformer overloaded under a defined system configuration | Disconnect Merrdin BESS
16 | AGL runback | KW-SF 82 overloaded (measured at KW of KW to SF flow) under a defined system configuration | Disconnect AGL's new units at KND
KW-BIB 81 overloaded (measured at KW of KW to BIB flow) under a defined system configuration
MSR-OFE/WM 81 overloaded (measured at MSR of MSR to OFE/WM flow) under a defined system configuration
WM-MSR/OFE 81 overloaded (measured at WM of MSR/OFE to WM flow) under a defined system configuration