## RCM Version history
Special schemes applicable to 2026 RCM - Draft
Draft Version History | Date | Details
0 | 2026-05-27 | Align with Special Protection Scheme Register V7.9

## Scheme
Special schemes applicable to 2025 RCM
# | Name | Contingency/Trigger | Scheme response/ Outcome
1 | MARNET | ENT-YDT 91 is part of contingency | intertrip WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect WARRADARGE_WF1
|  | NBT-YDT 91 is part of contingency | intertrip ENT-YDT 91 & WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect YANDIN_WF1 and WARRADARGE_WF1
|  | NBT-NT 91 is part of contingency | intertrip NBT-YDT 91, ENT-YDT 91 & WDW-ENT 91 line. Run back KRA to 10.0MW. Disconnect YANDIN_WF1 and WARRADARGE_WF1
|  | ENT-TST 91 is part of contingency | runback KRA to 10.0MW | MRS, MDP, King Rocks wf, Kondinin wf
2 | 220kV inter-trip (some of listed generators will be disconnected by their anti-islanding protection) | CGT-YLN-WKT X1 | Disconnect CGW & King Rocks windfarm. Island EGF
|  | MRT-CGT X1 | Disconnect CGW & King Rocks windfarm. Intertrip CGT-YLN-WKT line. Island EGF
|  | KDN-MRT X1 | Disconnect MDP, CGW, MRS, MRT BESS & King Rocks windfarm. Intertrip MRT-CGT & CGT-YLN-WKT lines. Island EGF
|  | MU-NGS-KDN X1 | Disconnect MDP, CGW, MRS, MRT BESS, KDN windfarm & King Rocks windfarm. Intertrip MRT-CGT & CGT-YLN-WKT lines. Island EGF
3 | BGM runback (after connection of onsite generation) | PMT-WLT 91 | Run back the export from BGM to 160MW (=90% of operational summer rating (179MVA) of WLT-GLT 81) following loss of the WLT 330kV line; and Run back the import from BGM to 60MW following loss of the WLT 330kV line . After 1min (say), if any of these above fails, BGM will be disconnected almost immediately
4 | MRT-CNS-NOR decouple | MRT-CNS-NOR 81 overload (measured at MRT & NOR taking into account losses on NOR-CNS/MRT section) | Open MRT CB of MRT-CNS-NOR 81 line
5 | APJ | SNR-APJ/WGP overload (measured in to SNR) | Run back ALINTA_PNJ_U1 to 83.0MW first, if overload remains, disconnect this unit.
6 | WWF runback | HBK-MUC 81 overloaded (measured at both MUC and HBK ends) | Disconnect TESLA_GERALDTON_G1 then runback Alinta_WWF, if overload remains, disconnect Alinta_WWF
MOR-MUC 81 is overloaded (measured at MOR of MOR to MUC flow)
ENB-TS 81 is overloaded (measured at TS of TS to ENB flow)
MOR-TS 81 is overloaded (measured at both TS and MOR ends)
MGA-TS 81 is overloaded (measured at MGA of MGA to TS flow)
MGA-MBA 81 is overloaded (measured at MGA of MGA to MBA flow)
TS-MBA 81 is overloaded (measured at MBA of MBA to TS flow) MBA-CRY 81 is overloaded (measured at MBA of MBA to CRY flow)
TST-TS 81 or 82 overloaded (measured at TS of TS to TST flow)
7 | TS bus coupler | TS806 overload (measured at TS of MGA to TS and MBA to TS flow) & GRSF ≥ 10MW | Run back GRSF first, if overload remains, disconnect this unit.
8 | NT 132kV bus coupler | A forced outage of one of NT 330kV transformers | NT 132kV bus couplers will close to re-mesh NT 132kV buses
9 | PIC-MRR intertrip | PIC-MRR overload (measured at PIC of PIC to MRR flow) | Disconnect MRR 526, 512 & 531 feeders
10 | PJR-YP manual intertrip | PJR-YP 81 overloaded (measured at PJR of PJR to YP flow) & NBT T2 oos under a defined system configuration | Manually take JDP-WNO 81 out of service
11 | KEM-MRR 81/82 manual intertrip | KEM-MRR 81 or 82 overloaded (measured at KEM of KEM to MRR flow) under a defined system configuration | Manually take MRR-PIC 81 out of service
12 | WGP manual intertrip | APJ-PNJ 81 overloaded (measured at APJ of APJ to PNJ flow) under a defined system configuration | Open WGP circuit breaker of WGP-APJ-SNR 81 line
CT-MSS-PNJ 81 overloaded (measured at PNJ of PNJ to T point flow) under a defined system configuration
PNJ-MH 81 overloaded (measured at PNJ of PNJ to MH flow) under a defined system configuration
13 | MUL-PBY manual intertrip | NT-BCT 81 overloaded (measured at NT of NT to BCT flow) under a defined system configuration | Take MUL-PBY 81 line out of service
14 | MU BTT2/BTT3 runback | MU BTT2 transfromer overloaded | Disconnect some East region generators to reduce transformer loading
MU BTT3 transfromer overloaded
15 | MRT T1/T2 runback | MRT T1 or T2 transformer overloaded under a defined system configuration | Disconnect Merrdin BESS
16 | AGL runback | KW-SF 82 overloaded (measured at KW of KW to SF flow) | Disconnect AGL's new units at KND
KW-BIB 81 overloaded (measured at KW of KW to BIB flow)
MSR-OFE/WM 81 overloaded (measured at MSR of MSR to OFE/WM flow)
WM-MSR/OFE 81 overloaded (measured at WM of MSR/OFE to WM flow)
17 | Waroona/Tesla Kemerton runback | PNJ-KEM/PIC/BSN 81 section overloaded (measured at PNJ of PNJ to the T point flow) under a defined system configuration | Disconnect Waroona solarfarm and Tesla generators (MRR)
18 | Milyeannup windfarm run back | MU-BTN-MJP 82 overloaded (measured at MJP of MJP to MU/BTN flow | Disconnect Milyeannup windfarm
19 | Palmer BESS | WLT-GLT 81 overloaded (measured at WLT of WLT to GLT flow) | Disconnect Palmer BESS
20 | Muchea BESS | MUC-PNJ 81 or 82 overloaded (measured at MUC of MUC to PNJ flow) | Disconnect Muchea BESS