## Authorisation
Draft 2026 RCM - Peak demand and block loads
Draft Version # | Date | Summary of change
0 | 2026-05-22 | Original version
1 | 2026-05-27 | add % of system load
Authorisation
| Date | Title | Name
Approver
VOLT#

## Proposed Electrical Location
Table 1 1. The estimated zone substation load (%) and Block loads (MW) are based on information from the applicable SWIS Base Model for the relevant reserve capacity cycle. 2. Connection points expected to export MW into the grid during the system coincident peak demand are excluded.
Capacity Year (3rd year of a Reserve Capacity Cycle) | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34
Estimated peak demand from WEM ESOO
Table 2 1. The demand at the following Electrical Locations are given as percentages, up to 2 decimal places. 2. Where an Electrical Location has one or more block loads, as specified in Table 3, the demand in Table 2 is the net demand at the Electrical Location, that is, the total load demand at the Electrical Location minus the total load demand of the block loads at the Electrical Location. 3. The estimated proportion of peak demand at an Electrical Connection is the net demand at that location divided by the sum of the demand at all Electrical Locations in the SWIS (=Western Power peak demand forecast for SWIS in summer) 4. Variation in estimated peak demand of the existing electrical connections and block loads is due to distribution load transfer, recent historical data, PV penetration, different load growth rate, etc. | bar: 2024-25
Electrical Location | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34
A - Arkana | 2024-25: 1.084%; 2025-26: 1.122%; 2026-27: 1.146%; 2027-28: 1.259%; 2028-29: 1.214%
ALB - Albany | 2024-25: 0.8206%; 2025-26: 0.7971%; 2026-27: 0.8279%; 2027-28: 0.7999%; 2028-29: 0.8648%
AMT - Amherst | 2024-25: 1.708%; 2025-26: 1.568%; 2026-27: 1.619%; 2027-28: 1.585%; 2028-29: 1.358%
APM - Australian Paper Mills | 2024-25: 0.5871%; 2025-26: 0.6139%; 2026-27: 0.6398%; 2027-28: 0.6154%; 2028-29: 0.7938%
BCH - Beechboro | 2024-25: 1.484%; 2025-26: 1.594%; 2026-27: 1.641%; 2027-28: 1.63%; 2028-29: 1.778%
BCT - Balcatta | 2024-25: 0.2959%; 2025-26: 0.2693%; 2026-27: 0.2918%; 2027-28: 0.386%; 2028-29: 0.4142%
BEL - Belmont | 2024-25: 0.9478%; 2025-26: 0.838%; 2026-27: 0.8603%; 2027-28: 1.008%; 2028-29: 0.8852%
BIB - Bibra Lake | 2024-25: 1.239%; 2025-26: 1.241%; 2026-27: 1.277%; 2027-28: 1.321%; 2028-29: 1.336%
BKF - Black Flag | 2024-25: 0.7998%; 2025-26: 0.8423%; 2026-27: 0.8819%; 2027-28: 0.6219%; 2028-29: 0.5116%
BLD - Boulder | 2024-25: 0.6264%; 2025-26: 0.4632%; 2026-27: 0.4993%; 2027-28: 0.4289%; 2028-29: 0.5116%
BNP - Beenup | 2024-25: 0.1479%; 2025-26: 0.14%; 2026-27: 0.1708%; 2027-28: 0.1137%; 2028-29: 0.1401%
BSN - Busselton | 2024-25: 0.957%; 2025-26: 1.336%; 2026-27: 0.8365%; 2027-28: 1.212%; 2028-29: 1.411%
BTN - Bridgetown | 2024-25: 0.5871%; 2025-26: 0.642%; 2026-27: 0.6852%; 2027-28: 0.1287%; 2028-29: 0.2375%
BTY - Bentley | 2024-25: 0.846%; 2025-26: 0.8725%; 2026-27: 0.9035%; 2027-28: 0.8792%; 2028-29: 0.8953%
BUH - Bunbury Harbour | 2024-25: 1.447%; 2025-26: 1.4%; 2026-27: 1.431%; 2027-28: 1.432%; 2028-29: 1.48%
BYF - Byford | 2024-25: 1.78%; 2025-26: 1.915%; 2026-27: 1.993%; 2027-28: 1.81%; 2028-29: 1.764%
CAP - Capel | 2024-25: 0.4739%; 2025-26: 0.4869%; 2026-27: 0.5144%; 2027-28: 0.4267%; 2028-29: 0.4466%
CAR - Carrabin | 2024-25: 0.006935%; 2025-26: 0.006463%; 2026-27: 0.03458%; 2027-28: 0%; 2028-29: 0.0203%
CC - Cockburn Cement | 2024-25: 0.7559%; 2025-26: 1.049%; 2026-27: 1.079%; 2027-28: 1.042%; 2028-29: 1.194%
CK - Cook Street | 2024-25: 1.026%; 2025-26: 0.9435%; 2026-27: 0.4971%; 2027-28: 1.004%; 2028-29: 1.498%
CKN - Clarkson | 2024-25: 1.579%; 2025-26: 1.579%; 2026-27: 1.643%; 2027-28: 1.535%; 2028-29: 1.49%
CL - Clarence St | 2024-25: 0.6704%; 2025-26: 0.5967%; 2026-27: 0.6268%; 2027-28: 0.6669%; 2028-29: 0.5948%
CO - Collie | 2024-25: 0.289%; 2025-26: 0.3124%; 2026-27: 0.3415%; 2027-28: 0.3131%; 2028-29: 0.2984%
COL - Collier | 2024-25: 0.8992%; 2025-26: 0.9392%; 2026-27: 0.9684%; 2027-28: 0.8706%; 2028-29: 1.127%
CPN - Chapman | 2024-25: 0.2728%; 2025-26: 0.2779%; 2026-27: 0.3069%; 2027-28: 0.2959%; 2028-29: 0.2639%
CTE - Cottesloe 132kV | 2024-25: 1.075%; 2025-26: 0.9672%; 2026-27: 0.9921%; 2027-28: 1.042%; 2028-29: 0.9603%
CUN - Cunderdin | 2024-25: 0.1364%; 2025-26: 0.1228%; 2026-27: 0.1491%; 2027-28: 0.1673%; 2028-29: 0.1847%
CVE - Canning Vale | 2024-25: 1.16%; 2025-26: 1.068%; 2026-27: 1.089%; 2027-28: 1.186%; 2028-29: 1.338%
D - Darlington | 2024-25: 0.5016%; 2025-26: 0.4739%; 2026-27: 0.5036%; 2027-28: 0.4996%; 2028-29: 0.4304%
E - Edmund Street | 2024-25: 0.5178%; 2025-26: 0.4761%; 2026-27: 0.4971%; 2027-28: 0.5554%; 2028-29: 0.4913%
ENB - Eneabba | 2024-25: 0.1595%; 2025-26: 0.1486%; 2026-27: 0.1772%; 2027-28: 0.163%; 2028-29: 0.3593%
FFD - Forrestfield | 2024-25: 0.6912%; 2025-26: 0.5859%; 2026-27: 0.5966%; 2027-28: 0.7034%; 2028-29: 0.7248%
G - Gosnells | 2024-25: 1.114%; 2025-26: 1.374%; 2026-27: 1.394%; 2027-28: 1.503%; 2028-29: 1.372%
GTN - Geraldton | 2024-25: 0.6519%; 2025-26: 0.6139%; 2026-27: 0.6506%; 2027-28: 0.6369%; 2028-29: 0.674%
H - Hadfields | 2024-25: 1.07%; 2025-26: 1.103%; 2026-27: 1.12%; 2027-28: 1.209%; 2028-29: 1.104%
HAY - Hay Street | 2024-25: 1.068%; 2025-26: 1.215%; 2026-27: 0.6312%; 2027-28: 1.094%; 2028-29: 0.8445%
HBK - Henley Brook | 2024-25: 1.436%; 2025-26: 1.736%; 2026-27: 1.848%; 2027-28: 1.218%; 2028-29: 1.435%
HZM - Hazelmere | 2024-25: 0.5733%; 2025-26: 0.5407%; 2026-27: 0.5793%; 2027-28: 0.5404%; 2028-29: 0.538%
JDP - Joondalup | 2024-25: 1.114%; 2025-26: 1.135%; 2026-27: 1.167%; 2027-28: 1.083%; 2028-29: 0.9217%
JTE - Joel Terrace 132kV | 2024-25: 1.258%; 2025-26: 1.183%; 2026-27: 1.21%; 2027-28: 1.252%; 2028-29: 1.242%
K - Kalamunda | 2024-25: 0.6981%; 2025-26: 0.7604%; 2026-27: 0.7846%; 2027-28: 0.8363%; 2028-29: 0.6618%
KAT - Katanning | 2024-25: 0.2543%; 2025-26: 0.2348%; 2026-27: 0.2615%; 2027-28: 0.2402%; 2028-29: 0.2619%
KDL - Kewdale | 2024-25: 0.5987%; 2025-26: 0.6118%; 2026-27: 0.6376%; 2027-28: 0.6369%; 2028-29: 0.4852%
KDN - Kondinin | 2024-25: 0.1641%; 2025-26: 0.1529%; 2026-27: 0.1794%; 2027-28: 0.1694%; 2028-29: 0.1543%
KEL - Kellerberrin | 2024-25: 0.06472%; 2025-26: 0.06032%; 2026-27: 0.08862%; 2027-28: 0.06219%; 2028-29: 0.07106%
KOJ - Kojonup | 2024-25: 0.05086%; 2025-26: 0.04524%; 2026-27: 0.07349%; 2027-28: 0.05147%; 2028-29: 0.05887%
LDE - Landsdale | 2024-25: 1.898%; 2025-26: 1.775%; 2026-27: 1.816%; 2027-28: 1.823%; 2028-29: 1.852%
MA - Manning Street | 2024-25: 0.7212%; 2025-26: 0.7303%; 2026-27: 0.7608%; 2027-28: 0.7806%; 2028-29: 0.7979%
MBR - Mount Barker | 2024-25: 0.1433%; 2025-26: 0.1422%; 2026-27: 0.1708%; 2027-28: 0.1372%; 2028-29: 0.1076%
MCE - Medical Centre 132kV | 2024-25: 1.052%; 2025-26: 0.9823%; 2026-27: 1.016%; 2027-28: 1.04%; 2028-29: 0.9562%
MDN - Maddington | 2024-25: 0.4762%; 2025-26: 0.5235%; 2026-27: 0.549%; 2027-28: 0.549%; 2028-29: 0.5847%
MDY - Munday | 2024-25: 0.497%; 2025-26: 0.4632%; 2026-27: 0.4907%; 2027-28: 0.371%; 2028-29: 0.5096%
MED - Medina | 2024-25: 1.357%; 2025-26: 1.398%; 2026-27: 1.459%; 2027-28: 1.447%; 2028-29: 1.338%
MER - Merredin | 2024-25: 0.1896%; 2025-26: 0.1788%; 2026-27: 0.2075%; 2027-28: 0.1844%; 2028-29: 0.2253%
MH - Mandurah | 2024-25: 1.678%; 2025-26: 1.762%; 2026-27: 1.794%; 2027-28: 1.456%; 2028-29: 1.541%
MIL - Milligan Street | 2024-25: 1.359%; 2025-26: 1.416%; 2026-27: 0.262%; 2027-28: 1.119%; 2028-29: 0.7962%
MJ - Midland Junction | 2024-25: 1.119%; 2025-26: 1.209%; 2026-27: 1.239%; 2027-28: 1.39%; 2028-29: 1.51%
MJP - Manjimup | 2024-25: 0.252%; 2025-26: 0.2887%; 2026-27: 0.3177%; 2027-28: 0.2959%; 2028-29: 0.2355%
MLG - Malaga | 2024-25: 0.8414%; 2025-26: 0.8294%; 2026-27: 0.3048%; 2027-28: 1.366%; 2028-29: 1.267%
MO - Morley | 2024-25: 1.153%; 2025-26: 1.217%; 2026-27: 1.249%; 2027-28: 1.327%; 2028-29: 1.289%
MOR - Moora | 2024-25: 0.2751%; 2025-26: 0.2844%; 2026-27: 0.1038%; 2027-28: 0.2916%; 2028-29: 0.3005%
MR - Margaret River | 2024-25: 0.2843%; 2025-26: 0.265%; 2026-27: 0.294%; 2027-28: 0.3259%; 2028-29: 0.337%
MRR - Marriott Road | 2024-25: 1.345%; 2025-26: 1.445%; 2026-27: 0.006485%; 2027-28: 0.3774%; 2028-29: 0.4791%
MSR - Mason Road | 2024-25: 0.7651%; 2025-26: 0.6269%; 2026-27: 0.2378%; 2027-28: 0.4932%; 2028-29: 0.5177%
MSS - Meadow Springs | 2024-25: 1.644%; 2025-26: 1.863%; 2026-27: 1.926%; 2027-28: 1.716%; 2028-29: 1.866%
MUC - Muchea | 2024-25: 0.6218%; 2025-26: 0.5838%; 2026-27: 0.616%; 2027-28: 0.6433%; 2028-29: 0.609%
MUL - Mullaloo | 2024-25: 1.119%; 2025-26: 0.9909%; 2026-27: 1.009%; 2027-28: 1.098%; 2028-29: 1.301%
MUR - Murdoch | 2024-25: 0.7605%; 2025-26: 0.7023%; 2026-27: 0.7284%; 2027-28: 0.7891%; 2028-29: 0.8019%
MYR - Myaree | 2024-25: 0.9894%; 2025-26: 0.9134%; 2026-27: 0.9403%; 2027-28: 0.9585%; 2028-29: 0.9846%
NB - North Beach | 2024-25: 1.331%; 2025-26: 1.303%; 2026-27: 1.347%; 2027-28: 1.218%; 2028-29: 1.273%
NGN - Narrogin | 2024-25: 0.3074%; 2025-26: 0.3081%; 2026-27: 0.3394%; 2027-28: 0.2938%; 2028-29: 0.2152%
NOR - Northam | 2024-25: 0.5224%; 2025-26: 0.5924%; 2026-27: 0.629%; 2027-28: 0.6755%; 2028-29: 0.3573%
NP - North Perth | 2024-25: 1.209%; 2025-26: 1.187%; 2026-27: 1.219%; 2027-28: 1.248%; 2028-29: 1.267%
OC - OConnor | 2024-25: 1.225%; 2025-26: 1.137%; 2026-27: 1.176%; 2027-28: 1.074%; 2028-29: 1.104%
OP - Osborne Park | 2024-25: 0.9663%; 2025-26: 0.8208%; 2026-27: 0.8387%; 2027-28: 0.9928%; 2028-29: 0.9136%
PBY - Padbury | 2024-25: 1.5%; 2025-26: 1.452%; 2026-27: 1.463%; 2027-28: 1.587%; 2028-29: 1.362%
PCY - Piccadilly St | 2024-25: 0.5756%; 2025-26: 0.5321%; 2026-27: 0.5533%; 2027-28: 0.5297%; 2028-29: 0.5786%
PIC - Picton | 2024-25: 0.92%; 2025-26: 0.6613%; 2026-27: 0.6809%; 2027-28: 0.8942%; 2028-29: 0.9603%
PNJ - Pinjarra | 2024-25: 0.4739%; 2025-26: 0.489%; 2026-27: 0.5339%; 2027-28: 0.7977%; 2028-29: 0.6882%
RAN - Rangeway | 2024-25: 0.5756%; 2025-26: 0.7023%; 2026-27: 0.7479%; 2027-28: 0.7977%; 2028-29: 0.672%
RGN22 - Regans 22kV | 2024-25: 0.1318%; 2025-26: 0.1653%; 2026-27: 0.1967%; 2027-28: 0.1673%; 2028-29: 0.136%
RGN33 - Regans 33kV | 2024-25: 0.1641%; 2025-26: 0.1739%; 2026-27: 0.2053%; 2027-28: 0.1887%; 2028-29: 0.1421%
RO - Rockingham | 2024-25: 1.348%; 2025-26: 1.094%; 2026-27: 1.096%; 2027-28: 1.192%; 2028-29: 1.271%
RTN - Riverton | 2024-25: 1.757%; 2025-26: 1.415%; 2026-27: 1.437%; 2027-28: 1.634%; 2028-29: 1.722%
RVE - Rivervale | 2024-25: 1.234%; 2025-26: 1.211%; 2026-27: 1.241%; 2027-28: 1.19%; 2028-29: 1.391%
SNR - Southern River | 2024-25: 1.919%; 2025-26: 2.034%; 2026-27: 2.123%; 2027-28: 1.984%; 2028-29: 2.191%
SPK - Shenton Park 132kV | 2024-25: 1.177%; 2025-26: 1.14%; 2026-27: 1.167%; 2027-28: 1.242%; 2028-29: 1.218%
SVY - Sawyers Valley 132kV | 2024-25: 0.5825%; 2025-26: 0.5838%; 2026-27: 0.4323%; 2027-28: 0.4139%; 2028-29: 0.4385%
SX - Southern Cross | 2024-25: 0.01156%; 2025-26: 0.03016%; 2026-27: 0.06052%; 2027-28: 0.0193%; 2028-29: 0.02233%
TS - Three Springs | 2024-25: 0.2127%; 2025-26: 0.1939%; 2026-27: 0.2248%; 2027-28: 0.1265%; 2028-29: 0.1563%
WAG - Wagin | 2024-25: 0.1017%; 2025-26: 0.1056%; 2026-27: 0.134%; 2027-28: 0.09864%; 2028-29: 0.1015%
WAI - Waikiki | 2024-25: 1.852%; 2025-26: 1.822%; 2026-27: 1.891%; 2027-28: 1.883%; 2028-29: 1.75%
WD - Wembley Downs | 2024-25: 0.8114%; 2025-26: 0.7497%; 2026-27: 0.7825%; 2027-28: 0.8492%; 2028-29: 0.8242%
WE - Welshpool | 2024-25: 1.26%; 2025-26: 1.329%; 2026-27: 1.347%; 2027-28: 1.465%; 2028-29: 1.324%
WGA - Wangara | 2024-25: 0.3837%; 2025-26: 0.4007%; 2026-27: 0.4323%; 2027-28: 0.5061%; 2028-29: 0.6375%
WGP - Wagerup | 2024-25: 0.3976%; 2025-26: 0.3662%; 2026-27: 0.3977%; 2027-28: 0.3838%; 2028-29: 0.3898%
WKT11 - West Kalgoorlie 11 kV | 2024-25: 0.1503%; 2025-26: 0.1551%; 2026-27: 0.1837%; 2027-28: 0.178%; 2028-29: 0.1662%
WKT33 - West Kalgoorlie 33 kV | 2024-25: 0.5109%; 2025-26: 0.5192%; 2026-27: 0.5512%; 2027-28: 0.3838%; 2028-29: 0.3081%
WLN - Willetton | 2024-25: 0.4531%; 2025-26: 0.6333%; 2026-27: 0.6679%; 2027-28: 0.9971%; 2028-29: 0.8872%
WNO - Wanneroo | 2024-25: 1.378%; 2025-26: 1.476%; 2026-27: 1.522%; 2027-28: 1.743%; 2028-29: 1.898%
WUN - Wundowie | 2024-25: 0.1942%; 2025-26: 0%; 2026-27: 0.2205%; 2027-28: 0.1951%; 2028-29: 0.2253%
Y - Yokine | 2024-25: 1.468%; 2025-26: 1.28%; 2026-27: 1.329%; 2027-28: 0.9028%; 2028-29: 1.066%
YER - Yerbillon | 2024-25: 0.04854%; 2025-26: 0.04308%; 2026-27: 0.07133%; 2027-28: 0.02059%; 2028-29: 0.00609%
YLN - Yilgarn | 2024-25: 0.2497%; 2025-26: 0.2434%; 2026-27: 0.2767%; 2027-28: 0.1994%; 2028-29: 0.205%
YP - Yanchep | 2024-25: 1.142%; 2025-26: 1.219%; 2026-27: 1.282%; 2027-28: 1.317%; 2028-29: 1.852%
Total | 2024-25: 84.77%; 2025-26: 84.61%; 2026-27: 82.64%; 2027-28: 85.6%; 2028-29: 86.77%
Table 3 1. The forecast demand of the following Block Loads are provided in MW, up to 2 decimal places, as measured at their respective Connection Points. 2. Block loads with CMD < 10MW are listed here to avoid their CMDs being exceeded when scaling up | bar: 2024-25
Load | 2024-25: 2024-25 (MW); 2025-26: 2025-26 (MW); 2026-27: 2026-27 (MW); 2027-28: 2027-28 (MW); 2028-29: 2028-29 (MW) | diff
ABD - Block Load 1 | 2024-25: 3.4; 2025-26: 3.4; 2026-27: 3.92; 2027-28: 2.89; 2028-29: 2.89
AFM - Block Load 2 | 2024-25: 4.2; 2025-26: 3.8; 2026-27: 2.3363; 2027-28: 2.34; 2028-29: 3.39
APJ - Block Load 3 | 2024-25: 15.2; 2025-26: 20.5; 2026-27: 26.38; 2027-28: 26.38; 2028-29: 26.38
BDE - Block Load 4 | 2024-25: 0.6; 2025-26: 0.6; 2026-27: 0.56974; 2027-28: 0.57; 2028-29: 0.96
BDP - Block Load 5 | 2024-25: 35.3; 2025-26: 41; 2026-27: 14.06; 2027-28: 14.16; 2028-29: 17.04
BEC - Block Load 6 | 2024-25: 9; 2025-26: 9.5; 2026-27: 0; 2027-28: 7.2; 2028-29: 7.2
BGM - Block Load 7 | 2024-25: 130.8; 2025-26: 130.1; 2026-27: 130.7371; 2027-28: 130.74; 2028-29: 125.93
BHK - Block Load 8 | 2024-25: 13.3; 2025-26: 3.7; 2026-27: 3.5597; 2027-28: 3.56; 2028-29: 3.72
BLV - Block Load 9 | 2024-25: 5.4; 2025-26: 5.4; 2026-27: 4.32; 2027-28: 4.32; 2028-29: 4.32
BNY - Block Load 10 | 2024-25: 9.5; 2025-26: 9.5; 2026-27: 6.719; 2027-28: 5.68; 2028-29: 7.33
BNY - Block Load 10a | 2027-28: 2.1; 2028-29: 2.24
BSI - Block Load 11 | 2024-25: 73; 2025-26: 72.4; 2026-27: 72.6186; 2027-28: 72.5; 2028-29: 72.5
CAR - Block Load 12 | 2024-25: 8.5; 2025-26: 8.1; 2026-27: 8.1; 2027-28: 7.9; 2028-29: 8.06
CBP - Block Load 13 | 2024-25: 9; 2025-26: 5.8; 2026-27: 7.72; 2027-28: 7.72; 2028-29: 2.57
CCL - Block Load 14 | 2024-25: 9.2; 2025-26: 10.6; 2026-27: 10.7498; 2027-28: 10.75; 2028-29: 8.35
CTB - Block Load 15 | 2024-25: 8.4; 2025-26: 8.2; 2026-27: 7.9; 2027-28: 11; 2028-29: 10.56
EDG - Block Load 16 | 2024-25: 7.1; 2025-26: 10; 2026-27: 11.48; 2027-28: 7; 2028-29: 7
FFD - Block Load 17 | 2024-25: 5; 2025-26: 5; 2026-27: 4; 2027-28: 5.02; 2028-29: 5.02
GGV - Block Load 18 | 2024-25: 17.2; 2025-26: 18.5; 2026-27: 21.1581; 2027-28: 21.16; 2028-29: 22.16
GNI - Block Load 19 | 2024-25: 13.2; 2025-26: 8.8; 2026-27: 8.8; 2027-28: 17.1; 2028-29: 9.1
KDP - Block Load 20 | 2024-25: 24.4; 2025-26: 21.5; 2026-27: 14.7292; 2027-28: 14.73; 2028-29: 11.53
KMC - Block Load 21 | 2024-25: 11.1; 2025-26: 9.4; 2026-27: 10.122; 2027-28: 10.12; 2028-29: 8.75
KMM - Block Load 22 | 2024-25: 9.1; 2025-26: 9.4; 2026-27: 7.7198; 2027-28: 7.72; 2028-29: 8.01
KRA - Block Load 23 | 2024-25: 78.7; 2025-26: 111; 2026-27: 69.6; 2027-28: 69.6; 2028-29: 72.8
MRN - Block Load 24 | 2024-25: 29; 2025-26: 27; 2026-27: 27; 2027-28: 1; 2028-29: 1.1
NOW - Block Load 25 | 2024-25: 7.5; 2025-26: 6.8; 2026-27: 4.7; 2027-28: 6; 2028-29: 7.6
NP - Block Load 26 | 2024-25: 8.1; 2025-26: 11.7; 2026-27: 4.7; 2027-28: 6; 2028-29: 9.98
PLD - Block Load 27 | 2024-25: 4; 2025-26: 6.2; 2026-27: 6.2; 2027-28: 11.56; 2028-29: 6
SUM - Block Load 28 | 2024-25: 8; 2025-26: 10.1; 2026-27: 8.0584; 2027-28: 8.06; 2028-29: 7.5
TLA - Block Load 29 | 2024-25: 16; 2025-26: 2.5; 2026-27: 4.41; 2027-28: 4.41; 2028-29: 5.15
TPP - Block Load 30 | 2024-25: 27.8; 2025-26: 21.8; 2026-27: 16.3036; 2027-28: 16.3; 2028-29: 0
WCL - Block Load 31 | 2024-25: 5.5; 2025-26: 4.3; 2026-27: 4.2027; 2027-28: 4.2; 2028-29: 3.86
WM - Block Load 32 | 2024-25: 31.3; 2025-26: 30.9; 2026-27: 15.9938; 2027-28: 16; 2028-29: 13.93
WSD - Block Load 33 | 2024-25: 5.9; 2025-26: 18.7; 2026-27: 2.1; 2027-28: 2.1; 2028-29: 11.17
AKW - Block Load 34 | 2024-25: 0; 2025-26: 2.7; 2026-27: 1.54; 2027-28: 1.54; 2028-29: 1.54
WAPL - Block Load 35 | 2024-25: 0; 2025-26: 4.4; 2026-27: 0; 2027-28: 0; 2028-29: 0
WHT - Block Load 36 | 2024-25: 10; 2025-26: 10; 2026-27: 8; 2027-28: 8; 2028-29: 8
SCE - Block Load 37 | 2024-25: 0; 2025-26: 0; 2026-27: 0; 2027-28: 0; 2028-29: 0
BTN - Block Load 38 | 2024-25: 15; 2025-26: 30; 2026-27: 36; 2027-28: 36; 2028-29: 36
MRR(523) - Block Load 39A | 2024-25: combined with other loads; 2026-27: 16.4; 2027-28: 16.42; 2028-29: 16.05
MRR(526) - Block Load 39B* | 2026-27: 7.56; 2027-28: 7.99; 2028-29: 1.24
MRR (512 & 531)- Block Load 40 | 2026-27: 5; 2027-28: 5; 2028-29: 5
PKS - Block Load 41 | 2024-25: 0; 2025-26: 0; 2026-27: 0; 2027-28: 0; 2028-29: 0
YP - Block Load 42* | 2026-27: 27.12; 2027-28: 27.12; 2028-29: 27.12
BNL - Block Load 43* | 2026-27: 7.5; 2027-28: 6; 2028-29: 9.8
BPR - Block Load 44 | 2027-28: 3.68; 2028-29: 3.94
BCH - Block Load 45 | 2027-28: 4.32; 2028-29: 4.32
CK - Block Load 46 | 2027-28: 6; 2028-29: 6
WKT - Block Load 47 | 2027-28: 0.72; 2028-29: 4.1
OFE - Block Load 49 | 2027-28: 0; 2028-29: 6.28
LTH - Block Load 50 | 2027-28: 0; 2028-29: 0
Sub Total | 2024-25: 668.7; 2025-26: 713.3; 2026-27: 650.0879; 2027-28: 660.68; 2028-29: 643.49
* Recently committed loads.

## Sheet6 (hidden)
Row Labels | Sum of Total Active Power
ALCOA_KWI | 49.133
ALCOA_PNJ | 67.724
ALCOA_WGP | 45.946
PRK_EG | 117.8
STHRNCRS_EG | 68
WAPL_WORSLEY | 185.76
(blank) | 0
Grand Total | 534.363

## Sheet1 (hidden)
Row Labels | Sum of Act.Pow.(act.)
ALCOA_KWI | 61
ALCOA_PNJ | 65
ALCOA_WGP | 55
PRK_AG | 108
STHRNCRS_EG | 82.29
WAPL_WORSLEY | 199
(blank) | 0
Grand Total | 570.29

## SWIS_27_28_IMB_GEN (hidden)
Name | In Folder | Grid | Out of service | Pn | Pmax(act.) | Pmin(act.) | Qmin(act.) | Qmax(act.) | Act.Pow.(act.) | React.Pow.(act.) | Facility code
|  |  |  | MW | MW | MW | Mvar | Mvar | MW | Mvar |  | Row Labels | Sum of Act.Pow.(act.)
GEN KBA GT | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | -23.663 | 43.39 | 23 | 7.107 | STHRNCRS_EG | ALCOA_KWI | 61
Gen_AKW_G1 | AKW - ALCOA Kwinana | KW - Kwinana Load Area | 0 | 65.002 | 68 | 25 | -33 | 34.1 | 61 | 0 | ALCOA_KWI | ALCOA_PNJ | 65
Gen_APJ_G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 20 | 25 | 10 | -11.75 | 17.875 | 15 | 6.574 | ALCOA_PNJ | ALCOA_WGP | 55
Gen_APJ_G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 20 | 25 | 10 | -11.75 | 17.875 | 15 | 0 | ALCOA_PNJ | PRK_EG | 108
Gen_APJ_G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 20 | 25 | 10 | -11.75 | 17.875 | 15 | 0 | ALCOA_PNJ | STHRNCRS_EG | 82.29
Gen_APJ_G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 30 | 36 | 17 | -14.3 | 22.375 | 20 | 0 | ALCOA_PNJ | WAPL_WORSLEY | 199
Gen_AWG_G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 25 | 30 | 12 | -14.3 | 24.062 | 15 | 6.34 | ALCOA_WGP | (blank) | 0
Gen_AWG_G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | -12.278 | 17.367 | 10 | 8.696 | ALCOA_WGP | Grand Total | 570.29
Gen_AWG_G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | -12.278 | 17.367 | 10 | 8.696 | ALCOA_WGP
Gen_AWG_G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 37.7 | 40 | 18 | -23.311 | 35.673 | 20 | 9.124 | ALCOA_WGP
Gen_KNS_G1 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 10.72 | 11 | 5 | -5.5 | 9.385 | 9 | 3.523 | STHRNCRS_EG
Gen_KNS_G3 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 11 | 12 | 5 | -5.5 | 8.863 | 10 | 6 | STHRNCRS_EG
Gen_KNS_GT2 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | -22.124 | 35.652 | 40.29 | 22.3 | STHRNCRS_EG
Gen_PRK_GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | -18.973 | 38.323 | 36 | 15.692 | PRK_AG
Gen_PRK_GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 1 | 44.6 | 38 | 7 | -19.167 | 31.167 | 36 | 15.692 | PRK_AG
Gen_PRK_GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | -19.167 | 31.167 | 36 | 15.692 | PRK_AG
Gen_WAPL_G1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 27.5 | 30 | 13 | -15.166 | 21.791 | 25 | 7.57 | WAPL_WORSLEY
Gen_WAPL_G2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | -17.313 | 23.803 | 20 | 7.57 | WAPL_WORSLEY
Gen_WAPL_G3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 27.5 | 30 | 13 | -15.166 | 21.791 | 25 | 7.57 | WAPL_WORSLEY
Gen_WAPL_G4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 32 | 35 | 16 | -9.775 | 27.85 | 25 | 4.517 | WAPL_WORSLEY
Gen_WAPL_G5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | -38.996 | 52.824 | 52 | 0 | WAPL_WORSLEY
Gen_WAPL_G6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | -38.996 | 52.824 | 52 | 0 | WAPL_WORSLEY
Name | In Folder | Grid | Zone | Total Active Power | Total Reactive Power | Facility code |  | Row Labels | Sum of Total Active Power
|  |  |  | MW | Mvar |  |  | ALCOA_KWI | 49.133
IMB LOAD - AKW - 22.0 kV | AKW - ALCOA Kwinana | KW - Kwinana Load Area | Imbedded | 49.133 | 9.876 | ALCOA_KWI |  | ALCOA_PNJ | 67.724
IMB LOAD - APJ - 13.8 kV / 1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 18.923 | 0.721 | ALCOA_PNJ |  | ALCOA_WGP | 45.946
IMB LOAD - APJ - 13.8 kV / 2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 25.445 | 0.721 | ALCOA_PNJ |  | PRK_EG | 117.8
IMB LOAD - APJ - 13.8 kV / 3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 20.356 | 0.721 | ALCOA_PNJ |  | STHRNCRS_EG | 68
IMB LOAD - APJ - 33.0 kV | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 3 | 0.85 | ALCOA_PNJ |  | WAPL_WORSLEY | 185.76
IMB LOAD - AWG - 22.0 kV | AWG - Alcoa Wagerup | MU - Muja Load Area | Imbedded | 45.946 | 3.124 | ALCOA_WGP |  | (blank) | 0
IMB LOAD - FIM - 33.0 kV | FIM - Fimiston | EG - Eastern Goldfields Load Area | Imbedded | 117.8 | -3.1 | PRK_EG |  | Grand Total | 534.363
IMB LOAD - JAN | JAN - Jan | EG - Eastern Goldfields Load Area | Imbedded | 3 | 1.453 | STHRNCRS_EG
IMB LOAD - KNS | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | Imbedded | 23 | 11.139 | STHRNCRS_EG
IMB LOAD - LEF | LEF - Lefroy | EG - Eastern Goldfields Load Area | Imbedded | 22 | 7.231 | STHRNCRS_EG
IMB LOAD - WAPL / 1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 20 | 3.665 | WAPL_WORSLEY
IMB LOAD - WAPL / 2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 20 | 3.665 | WAPL_WORSLEY
IMB LOAD - WAPL / 3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 38 | 3.665 | WAPL_WORSLEY
IMB LOAD - WAPL / 4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 43.88 | 3.665 | WAPL_WORSLEY
IMB LOAD - WAPL / 5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 20 | 3.665 | WAPL_WORSLEY
IMB LOAD - WAPL / 6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 43.88 | 3.665 | WAPL_WORSLEY
IMB LOAD - WMK | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | Imbedded | 20 | 2.008 | STHRNCRS_EG
|  |  | Total generation at IMB_Load | 534.363
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | -2.6603 | -2.6603
ALCOA_PNJ | -20.5298 | -20.5298
ALCOA_WGP | 5.2568 | 0
PRK_EG | -0.86744 | -0.86744
STHRNCRS_EG | 4.3783 | 0
WAPL_WORSLEY | -4.3964 | -4.3964
| Total MW (as Load) to be considered in RCM | -28.4539
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | 11.867 | 0
ALCOA_PNJ | -2.724 | -2.724
ALCOA_WGP | 9.054 | 0
PRK_EG | -9.8 | -9.8
STHRNCRS_EG | 14.29 | 0
WAPL_WORSLEY | 13.24 | 0
| Total MW (as Load) to be considered in RCM | -12.524
Confidential - Not to be published

## IMG gen Raw data (hidden)
Name | In Folder | Grid | Active Power | Reactive Power | Pmax(act.) | Pmin(act.) | Pr(rated) | Out of Service | Pow.Fact. | Power Factor | Qmin(act.) | Qmax(act.) | Total Active Power | Total Reactive Power | Total Nominal Active power | Act.Pow.(act.) | React.Pow.(act.)
|  |  | MW | Mvar | MW | MW | MW |  |  |  | Mvar | Mvar | MW | Mvar | MW | MW | Mvar
GEN KBA GT | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | 23 | -2.736 | 46 | 10 | 46 | 0 | 0.9554 | 0.993 | -23.663 | 43.39 | 23 | 7.107 | 46 | 23 | 7.107
Gen_AKW_G1 | AKW - ALCOA Kwinana | KW - Kwinana Load Area | 61 | 11.263 | 68 | 25 | 65.002 | 0 | 1 | 0.9834 | -33 | 34.1 | 61 | 0 | 65.002 | 61 | 0
Gen_APJ_G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 15 | -2.094 | 25 | 10 | 20 | 0 | 0.9159 | 0.9904 | -11.75 | 17.875 | 15 | 6.574 | 20 | 15 | 6.574
Gen_APJ_G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 15 | -2.094 | 25 | 10 | 20 | 0 | 1 | 0.9904 | -11.75 | 17.875 | 15 | 0 | 20 | 15 | 0
Gen_APJ_G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 15 | -2.094 | 25 | 10 | 20 | 0 | 1 | 0.9904 | -11.75 | 17.875 | 15 | 0 | 20 | 15 | 0
Gen_APJ_G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 20 | -3.811 | 36 | 17 | 30 | 0 | 1 | 0.9823 | -14.3 | 22.375 | 20 | 0 | 30 | 20 | 0
Gen_AWG_G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | 15 | 0.001 | 30 | 12 | 25 | 0 | 0.9211 | 1 | -14.3 | 24.062 | 15 | 6.34 | 25 | 15 | 6.34
Gen_AWG_G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | 10 | -0.251 | 21 | 9 | 18 | 0 | 0.7546 | 0.9997 | -12.278 | 17.367 | 10 | 8.696 | 18 | 10 | 8.696
Gen_AWG_G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | 10 | -0.251 | 21 | 9 | 18 | 0 | 0.7546 | 0.9997 | -12.278 | 17.367 | 10 | 8.696 | 18 | 10 | 8.696
Gen_AWG_G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | 20 | 5.174 | 40 | 18 | 37.7 | 0 | 0.9098 | 0.9681 | -23.311 | 35.673 | 20 | 9.124 | 37.7 | 20 | 9.124
Gen_KNS_G1 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area |  |  | 11 | 5 | 10.72 | 1 | 0.9312 |  | -5.5 | 9.385 |  |  | 10.72 | 9 | 3.523
Gen_KNS_G3 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area |  |  | 12 | 5 | 11 | 1 | 0.8575 |  | -5.5 | 8.863 |  |  | 11 | 10 | 6
Gen_KNS_GT2 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 40.29 | 13.59 | 46 | 10 | 46 | 0 | 0.8749 | 0.9476 | -22.124 | 35.652 | 40.29 | 22.3 | 46 | 40.29 | 22.3
Gen_PRK_GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 36 | 9.709 | 38 | 7 | 44.6 | 0 | 0.9167 | 0.9655 | -18.973 | 38.323 | 36 | 15.692 | 44.6 | 36 | 15.692
Gen_PRK_GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area |  |  | 38 | 7 | 44.6 | 1 | 0.9167 |  | -19.167 | 31.167 |  |  | 44.6 | 36 | 15.692
Gen_PRK_GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 36 | -0.109 | 38 | 7 | 44.6 | 0 | 0.9167 | 1 | -19.167 | 31.167 | 36 | 15.692 | 44.6 | 36 | 15.692
Gen_WAPL_G1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 25 | 2.368 | 30 | 13 | 27.5 | 0 | 0.9571 | 0.9955 | -15.166 | 21.791 | 25 | 7.57 | 27.5 | 25 | 7.57
Gen_WAPL_G2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area |  |  | 30 | 13 | 27.5 | 1 | 0.9352 |  | -17.313 | 23.803 |  |  | 27.5 | 20 | 7.57
Gen_WAPL_G3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 25 | 3.357 | 30 | 13 | 27.5 | 0 | 0.9571 | 0.9911 | -15.166 | 21.791 | 25 | 7.57 | 27.5 | 25 | 7.57
Gen_WAPL_G4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 25 | 3.995 | 35 | 16 | 32 | 0 | 0.9841 | 0.9875 | -9.775 | 27.85 | 25 | 4.517 | 32 | 25 | 4.517
Gen_WAPL_G5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 52 | 6.299 | 61 | 27 | 57.84 | 0 | 1 | 0.9927 | -38.996 | 52.824 | 52 | 0 | 57.84 | 52 | 0
Gen_WAPL_G6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 52 | 6.299 | 61 | 27 | 57.84 | 0 | 1 | 0.9927 | -38.996 | 52.824 | 52 | 0 | 57.84 | 52 | 0

## Sheet5 (hidden)
sub | [5 empty] | MW
A - Arkana | A - Arkana | SUB LOAD - A - 22.0 kV | A - Arkana | NT - Northern Terminal Load Area | Normal | 58.4
ALB - Albany | ALB - Albany | SUB LOAD - A - 22.0 kV_DCAP | A - Arkana | NT - Northern Terminal Load Area | Normal | 0
AMT - Amherst | AMT - Amherst | SUB LOAD - ALB - 22.0 kV | ALB - Albany | MU - Muja Load Area | Normal | 39.9
APM - Australian Paper Mills | APM - Australian Paper Mills | SUB LOAD - ALB - 22.0 kV_DCAP | ALB - Albany | MU - Muja Load Area | Normal | 0
BCH - Beechboro | BCH - Beechboro | SUB LOAD - AMT - 22.0 kV | AMT - Amherst | SF - South Fremantle Load Area | Normal | 68.7
BCT - Balcatta | BCT - Balcatta | SUB LOAD - AMT - 22.0 kV_DCAP | AMT - Amherst | SF - South Fremantle Load Area | Normal | 0
BEL - Belmont | BEL - Belmont | SUB LOAD - APM - 22.0 kV | APM - Australian Paper Mills | SF - South Fremantle Load Area | Normal | 36.4
BIB - Bibra Lake | BIB - Bibra Lake | SUB LOAD - APM - 22.0 kV_DCAP | APM - Australian Paper Mills | SF - South Fremantle Load Area | Normal | 0
BKF - Black Flag | BKF - Black Flag | SUB LOAD - BCH - 22.0 kV | BCH - Beechboro | NT - Northern Terminal Load Area | Normal | 82
BLD - Boulder | BLD - Boulder | SUB LOAD - BCH - 22.0 kV_DCAP | BCH - Beechboro | NT - Northern Terminal Load Area | Normal | 0
BNP - Beenup | BNP - Beenup | SUB LOAD - BCT - 22.0 kV | BCT - Balcatta | NT - Northern Terminal Load Area | Normal | 20.5
BSN - Busselton | BSN - Busselton | SUB LOAD - BCT - 22.0 kV_DCAP | BCT - Balcatta | NT - Northern Terminal Load Area | Normal | 0
BTN - Bridgetown | BSN - Busselton | SUB LOAD - BEL - 22.0 kV | BEL - Belmont | CT - Cannington Terminal Load Area | Normal | 42.3
BTY - Bentley | BSN - Busselton | SUB LOAD - BEL - 22.0 kV_DCAP | BEL - Belmont | CT - Cannington Terminal Load Area | Normal | 0
BUH - Bunbury Harbour | BTN - Bridgetown | SUB LOAD - BIB - 22.0 kV | BIB - Bibra Lake | SF - South Fremantle Load Area | Normal | 59.9
BYF - Byford | BTY - Bentley | SUB LOAD - BIB - 22.0 kV_DCAP | BIB - Bibra Lake | SF - South Fremantle Load Area | Normal | 0
CAP - Capel | BUH - Bunbury Harbour | SUB LOAD - BKF - 33.0 kV | BKF - Black Flag | EG - Eastern Goldfields Load Area | Normal | 24.7
CAR - Carrabin | BYF - Byford | SUB LOAD - BKF - 33.0 kV_DCAP | BKF - Black Flag | EG - Eastern Goldfields Load Area | Normal | 0
CC - Cockburn Cement | CAP - Capel | SUB LOAD - BLD - 33 kV | BLD - Boulder | EG - Eastern Goldfields Load Area | Normal | 25.2
CK - Cook Street | CAR - Carrabin | SUB LOAD - BLD - 33 kV_DCAP | BLD - Boulder | EG - Eastern Goldfields Load Area | Normal | 0
CKN - Clarkson | CC - Cockburn Cement | SUB LOAD - BNP - 22.0 kV | BNP - Beenup | MU - Muja Load Area | Normal | 6.7
CL - Clarence St | CK - Cook Street | SUB LOAD - BNP - 22.0 kV_DCAP | BNP - Beenup | MU - Muja Load Area | Normal | 0
CO - Collie | CK - Cook Street | SUB LOAD - BSN - 22.0 kV / 2 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 37.5
COL - Collier | CK - Cook Street | SUB LOAD - BSN - 22.0 kV / 2_DCAP | BSN - Busselton | BPS - Bunbury Load Area | Normal | 0
CPN - Chapman | CKN - Clarkson | SUB LOAD - BSN - T1 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 12.5
CTE - Cottesloe 132kV | CL - Clarence St | SUB LOAD - BSN - T1_DCAP | BSN - Busselton | BPS - Bunbury Load Area | Normal | 0
CUN - Cunderin | CO - Collie | SUB LOAD - BSN - T2 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 12.5
CVE - Canning Vale | COL - Collier | SUB LOAD - BSN - T2_DCAP | BSN - Busselton | BPS - Bunbury Load Area | Normal | 0
D - Darlington | CPN - Chapman | SUB LOAD - BTN - 22.0 kV | BTN - Bridgetown | MU - Muja Load Area | Normal | 11.9
E - Edmund Street | CTE - Cottesloe 132kV | SUB LOAD - BTN - 22.0 kV_DCAP | BTN - Bridgetown | MU - Muja Load Area | Normal | 0
ENB - Eneabba | CUN - Cunderin | SUB LOAD - BTY - 22.0 kV | BTY - Bentley | CT - Cannington Terminal Load Area | Normal | 43
FFD - Forrestfield | CVE - Canning Vale | SUB LOAD - BTY - 22.0 kV_DCAP | BTY - Bentley | CT - Cannington Terminal Load Area | Normal | 0
G - Gosnells | D - Darlington | SUB LOAD - BUH - 22.0 kV | BUH - Bunbury Harbour | BPS - Bunbury Load Area | Normal | 67.6
GTN - Geraldton | E - Edmund Street | SUB LOAD - BUH - 22.0 kV_DCAP | BUH - Bunbury Harbour | BPS - Bunbury Load Area | Normal | 0
H - Hadfields | ENB - Eneabba | SUB LOAD - BYF - 22.0 kV | BYF - Byford | ST - Southern Terminal Load Area | Normal | 89.2
HAY - Hay Street | FFD - Forrestfield | SUB LOAD - BYF - 22.0 kV_DCAP | BYF - Byford | ST - Southern Terminal Load Area | Normal | 0
HBK - Henley Brook | G - Gosnells | SUB LOAD - CAP - 22.0 kV | CAP - Capel | BPS - Bunbury Load Area | Normal | 21.9
HZM - Hazelmere | GTN - Geraldton | SUB LOAD - CAP - 22.0 kV_DCAP | CAP - Capel | BPS - Bunbury Load Area | Normal | 0
JDP - Joondalup | H - Hadfields | SUB LOAD - CAR - 22.0 kV | CAR - Carrabin | EC - East Country Load Area | Normal | 1
JTE - Joel Terrace 132kV | HAY - Hay Street | SUB LOAD - CAR - 22.0 kV_DCAP | CAR - Carrabin | EC - East Country Load Area | Normal | 0
K - Kalamunda | HAY - Hay Street | SUB LOAD - CC - 22.0 kV | CC - Cockburn Cement | ST - Southern Terminal Load Area | Normal | 54.5
KAT - Katanning | HBK - Henley Brook | SUB LOAD - CC - 22.0 kV_DCAP | CC - Cockburn Cement | ST - Southern Terminal Load Area | Normal | 0
KDL - Kewdale | HZM - Hazelmere | SUB LOAD - CK - 11.0 kV / 1 | CK - Cook Street | EP - East Perth Load Area | Normal | 22.4
KDN - Kondinin | JDP - Joondalup | SUB LOAD - CK - 11.0 kV / 1_DCAP | CK - Cook Street | EP - East Perth Load Area | Normal | 0
KEL - Kellerberrin | JTE - Joel Terrace 132kV | SUB LOAD - CK - 11.0 kV / 2 | CK - Cook Street | EP - East Perth Load Area | Normal | 22.4
KOJ - Kojonup | K - Kalamunda | SUB LOAD - CK - 11.0 kV / 2_DCAP | CK - Cook Street | EP - East Perth Load Area | Normal | 0
LDE - Landsdale | KAT - Katanning | SUB LOAD - CK - 11.0 kV / 3 | CK - Cook Street | EP - East Perth Load Area | Normal | 27
MA - Manning Street | KDL - Kewdale | SUB LOAD - CKN - 22.0 kV | CKN - Clarkson | NT - Northern Terminal Load Area | Normal | 67.2
MBR - Mount Barker | KDN - Kondinin | SUB LOAD - CKN - 22.0 kV_DCAP | CKN - Clarkson | NT - Northern Terminal Load Area | Normal | 0
MCE - Medical Centre 132kV | KEL - Kellerberrin | SUB LOAD - CL - 11.0 kV | CL - Clarence St | CT - Cannington Terminal Load Area | Normal | 28.6
MDY - Munday | KOJ - Kojonup | SUB LOAD - CL - 11.0 kV_DCAP | CL - Clarence St | CT - Cannington Terminal Load Area | Normal | 0
MED - Medina | LDE - Landsdale | SUB LOAD - CO - 22.0 kV | CO - Collie | MU - Muja Load Area | Normal | 14.5
MER - Merredin | MA - Manning Street | SUB LOAD - CO - 22.0 kV_DCAP | CO - Collie | MU - Muja Load Area | Normal | 0
MH - Mandurah | MBR - Mount Barker | SUB LOAD - COL - 11.0 kV | COL - Collier | CT - Cannington Terminal Load Area | Normal | 54
MIL - Milligan Street | MCE - Medical Centre 132kV | SUB LOAD - COL - 11.0 kV_DCAP | COL - Collier | CT - Cannington Terminal Load Area | Normal | 0
MJ - Midland Junction | MDN - Maddington | SUB LOAD - CPN - 11.0 kV | CPN - Chapman | NC - North Country Load Area | Normal | 12.3
MJP - Manjimup | MDY - Munday | SUB LOAD - CPN - 11.0 kV_DCAP | CPN - Chapman | NC - North Country Load Area | Normal | 0
MLG - Malaga | MED - Medina | SUB LOAD - CTE - 11.0 kV | CTE - Cottesloe 132kV | WT - Western Terminal Load Area | Normal | 46.7
MO - Morley | MER - Merredin | SUB LOAD - CTE - 11.0 kV_DCAP | CTE - Cottesloe 132kV | WT - Western Terminal Load Area | Normal | 0
MOR - Moora | MH - Mandurah | SUB LOAD - CUN - 22.0 kV | CUN - Cunderin | EC - East Country Load Area | Normal | 9.1
MR - Margaret River | MIL - Milligan Street | SUB LOAD - CUN - 22.0 kV_DCAP | CUN - Cunderin | EC - East Country Load Area | Normal | 0
MRR - Marriott Road | MIL - Milligan Street | SUB LOAD - CVE - 22.0 kV | CVE - Canning Vale | ST - Southern Terminal Load Area | Normal | 63.1
MSR - Mason Road | MIL - Milligan Street | SUB LOAD - CVE - 22.0 kV_DCAP | CVE - Canning Vale | ST - Southern Terminal Load Area | Normal | 0
MSS - Meadow Springs | MIL - Milligan Street | SUB LOAD - D - 22.0 kV | D - Darlington | GLT - Guildford Terminal Load Area | Normal | 19.8
MUC - Muchea | MIL - Milligan Street | SUB LOAD - D - 22.0 kV_DCAP | D - Darlington | GLT - Guildford Terminal Load Area | Normal | 0
MUL - Mullaloo | MIL - Milligan Street | SUB LOAD - E - 11.0 kV | E - Edmund Street | SF - South Fremantle Load Area | Normal | 23.6
MUR - Murdoch | MJ - Midland Junction | SUB LOAD - E - 11.0 kV_DCAP | E - Edmund Street | SF - South Fremantle Load Area | Normal | 0
MYR - Myaree | MJP - Manjimup | SUB LOAD - ENB - 33.0 kV | ENB - Eneabba | NC - North Country Load Area | Normal | 17
NB - North Beach | MLG - Malaga | SUB LOAD - ENB - 33.0 kV_DCAP | ENB - Eneabba | NC - North Country Load Area | Normal | 0
NGN - Narrogin | MLG - Malaga | SUB LOAD - FFD - 22.0 kV | FFD - Forrestfield | GLT - Guildford Terminal Load Area | Normal | 34.9
NOR - Northam | MLG - Malaga | SUB LOAD - FFD - 22.0 kV_DCAP | FFD - Forrestfield | GLT - Guildford Terminal Load Area | Normal | 0
NP - North Perth | MO - Morley | SUB LOAD - G - 22.0 kV | G - Gosnells | ST - Southern Terminal Load Area | Normal | 63.9
OC - OConnor | MOR - Moora | SUB LOAD - G - 22.0 kV_DCAP | G - Gosnells | ST - Southern Terminal Load Area | Normal | 0
OP - Osborne Park | MOR - Moora | SUB LOAD - GTN - 33.0 kV | GTN - Geraldton | NC - North Country Load Area | Normal | 33.2
PBY - Padbury | MR - Margaret River | SUB LOAD - GTN - 33.0 kV_DCAP | GTN - Geraldton | NC - North Country Load Area | Normal | 0
PCY - Piccadilly St | MRR - Marriott Road | SUB LOAD - H - 22.0 kV | H - Hadfields | NT - Northern Terminal Load Area | Normal | 52.8
PIC - Picton | MSR - Mason Road | SUB LOAD - H - 22.0 kV_DCAP | H - Hadfields | NT - Northern Terminal Load Area | Normal | 0
PNJ - Pinjarra | MSR - Mason Road | SUB LOAD - HAY - 11.0 kV / 1 | HAY - Hay Street | EP - East Perth Load Area | Normal | 20.3
RAN - Rangeway | MSR - Mason Road | SUB LOAD - HAY - 11.0 kV / 1_DCAP | HAY - Hay Street | EP - East Perth Load Area | Normal | 0
RGN - Regans | MSS - Meadow Springs | SUB LOAD - HAY - 11.0 kV / 2 | HAY - Hay Street | EP - East Perth Load Area | Normal | 20.3
RO - Rockingham | MUC - Muchea | SUB LOAD - HAY - 11.0 kV / 2_DCAP | HAY - Hay Street | EP - East Perth Load Area | Normal | 0
RTN - Riverton | MUL - Mullaloo | SUB LOAD - HBK - 22.0 kV | HBK - Henley Brook | NT - Northern Terminal Load Area | Normal | 60.3
RVE - Rivervale | MUR - Murdoch | SUB LOAD - HBK - 22.0 kV_DCAP | HBK - Henley Brook | NT - Northern Terminal Load Area | Normal | 0
SNR - Southern River | MYR - Myaree | SUB LOAD - HZM - 22.0 kV | HZM - Hazelmere | GLT - Guildford Terminal Load Area | Normal | 26.5
SPK - Shenton Park 132kV | NB - North Beach | SUB LOAD - HZM - 22.0 kV_DCAP | HZM - Hazelmere | GLT - Guildford Terminal Load Area | Normal | 0
SVY - Sawyers Valley 132kV | NGN - Narrogin | SUB LOAD - JDP - 22.0 kV | JDP - Joondalup | NT - Northern Terminal Load Area | Normal | 43.9
SX - Southern Cross | NOR - Northam | SUB LOAD - JDP - 22.0 kV_DCAP | JDP - Joondalup | NT - Northern Terminal Load Area | Normal | 0
TS - Three Springs | NP - North Perth | SUB LOAD - JTE - 11.0 kV | JTE - Joel Terrace 132kV | EP - East Perth Load Area | Normal | 59.8
WAG - Wagin | OC - OConnor | SUB LOAD - JTE - 11.0 kV_DCAP | JTE - Joel Terrace 132kV | EP - East Perth Load Area | Normal | 0
WAI - Waikiki | OP - Osborne Park | SUB LOAD - K - 22.0 kV | K - Kalamunda | GLT - Guildford Terminal Load Area | Normal | 30.8
WD - Wembley Downs | PBY - Padbury | SUB LOAD - K - 22.0 kV_DCAP | K - Kalamunda | GLT - Guildford Terminal Load Area | Normal | 0
WE - Welshpool | PCY - Piccadilly St | SUB LOAD - KAT - 22.0 kV | KAT - Katanning | MU - Muja Load Area | Normal | 12.3
WGA - Wangara | PIC - Picton | SUB LOAD - KAT - 22.0 kV_DCAP | KAT - Katanning | MU - Muja Load Area | Normal | 0
WGP - Wagerup | PNJ - Pinjarra | SUB LOAD - KDL - 22.0 kV | KDL - Kewdale | CT - Cannington Terminal Load Area | Normal | 23.7
WKT - West Kalgoorlie | RAN - Rangeway | SUB LOAD - KDL - 22.0 kV_DCAP | KDL - Kewdale | CT - Cannington Terminal Load Area | Normal | 0
WNO - Wanneroo | RGN - Regans | SUB LOAD - KDN - 33.0 kV | KDN - Kondinin | EC - East Country Load Area | Normal | 7.8
WUN - Wundowie | RGN - Regans | SUB LOAD - KDN - 33.0 kV_DCAP | KDN - Kondinin | EC - East Country Load Area | Normal | 0
Y - Yokine | RO - Rockingham | SUB LOAD - KEL - 22.0 kV | KEL - Kellerberrin | EC - East Country Load Area | Normal | 3.3
YER - Yerbillon | RTN - Riverton | SUB LOAD - KEL - 22.0 kV_DCAP | KEL - Kellerberrin | EC - East Country Load Area | Normal | 0
YLN - Yilgarn | RVE - Rivervale | SUB LOAD - KOJ - 22.0 kV | KOJ - Kojonup | MU - Muja Load Area | Normal | 2.9
YP - Yanchep | SNR - Southern River | SUB LOAD - KOJ - 22.0 kV_DCAP | KOJ - Kojonup | MU - Muja Load Area | Normal | 0
| SPK - Shenton Park 132kV | SUB LOAD - LDE - 22.0 kV | LDE - Landsdale | NT - Northern Terminal Load Area | Normal | 86.5
| SVY - Sawyers Valley 132kV | SUB LOAD - LDE - 22.0 kV_DCAP | LDE - Landsdale | NT - Northern Terminal Load Area | Normal | 0
| SX - Southern Cross | SUB LOAD - MA - 11.0 kV | MA - Manning Street | NT - Northern Terminal Load Area | Normal | 38.4
| TS - Three Springs | SUB LOAD - MA - 11.0 kV_DCAP | MA - Manning Street | NT - Northern Terminal Load Area | Normal | 0
| WAG - Wagin | SUB LOAD - MBR - 22.0 kV | MBR - Mount Barker | MU - Muja Load Area | Normal | 6
| WAI - Waikiki | SUB LOAD - MBR - 22.0 kV_DCAP | MBR - Mount Barker | MU - Muja Load Area | Normal | 0
| WD - Wembley Downs | SUB LOAD - MCE | MCE - Medical Centre 132kV | WT - Western Terminal Load Area | Normal | 46.5
| WE - Welshpool | SUB LOAD - MCE_DCAP | MCE - Medical Centre 132kV | WT - Western Terminal Load Area | Normal | 0
| WGA - Wangara | SUB LOAD - MDN - 22.0 kV | MDN - Maddington | ST - Southern Terminal Load Area | Normal | 28
| WGP - Wagerup | SUB LOAD - MDY - 22.0 kV | MDY - Munday | GLT - Guildford Terminal Load Area | Normal | 25.1
| WKT - West Kalgoorlie | SUB LOAD - MDY - 22.0 kV_DCAP | MDY - Munday | GLT - Guildford Terminal Load Area | Normal | 0
| WKT - West Kalgoorlie | SUB LOAD - MED - 22.0 kV | MED - Medina | KW - Kwinana Load Area | Normal | 65.1
| WLN - Willetton | SUB LOAD - MED - 22.0 kV_DCAP | MED - Medina | KW - Kwinana Load Area | Normal | 0
| WNO - Wanneroo | SUB LOAD - MER - 22.0 kV | MER - Merredin | EC - East Country Load Area | Normal | 10.9
| WUN - Wundowie | SUB LOAD - MER - 22.0 kV_DCAP | MER - Merredin | EC - East Country Load Area | Normal | 0
| Y - Yokine | SUB LOAD - MH - 22.0 kV | MH - Mandurah | KW - Kwinana Load Area | Normal | 71.7
| YER - Yerbillon | SUB LOAD - MH - 22.0 kV_DCAP | MH - Mandurah | KW - Kwinana Load Area | Normal | 0
| YLN - Yilgarn | SUB LOAD - MIL - 11.0 kV / 1 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 6.42
| YP - Yanchep | SUB LOAD - MIL - 11.0 kV / 1_DCAP | MIL - Milligan Street | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - MIL - 11.0 kV / 2 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 6.42
|  | SUB LOAD - MIL - 11.0 kV / 2_DCAP | MIL - Milligan Street | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - MIL - 11.0 kV / 3 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 6.42
|  | SUB LOAD - MIL - 11.0 kV / 3_DCAP | MIL - Milligan Street | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - MIL - 11.0 kV / 4 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 6.42
|  | SUB LOAD - MIL - 11.0 kV / 4_DCAP | MIL - Milligan Street | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - MIL - 11.0 kV / 5 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 6.42
|  | SUB LOAD - MIL - 11.0 kV / 5_DCAP | MIL - Milligan Street | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - MIL - 11.0 kV / 6 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 6.42
|  | SUB LOAD - MIL - 11.0 kV / 6_DCAP | MIL - Milligan Street | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - MJ - 22.0 kV | MJ - Midland Junction | GLT - Guildford Terminal Load Area | Normal | 67.4
|  | SUB LOAD - MJ - 22.0 kV_DCAP | MJ - Midland Junction | GLT - Guildford Terminal Load Area | Normal | 0
|  | SUB LOAD - MJP - 22.0 kV | MJP - Manjimup | MU - Muja Load Area | Normal | 11.7
|  | SUB LOAD - MJP - 22.0 kV_DCAP | MJP - Manjimup | MU - Muja Load Area | Normal | 0
|  | SUB LOAD - MLG - 22.0 kV / 1 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 19.8
|  | SUB LOAD - MLG - 22.0 kV / 1_DCAP | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - MLG - 22.0 kV / 2 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 19.8
|  | SUB LOAD - MLG - 22.0 kV / 2_DCAP | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - MLG - 22.0 kV / 3 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 20.4
|  | SUB LOAD - MLG - 22.0 kV / 3_DCAP | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - MO - 11.0 kV | MO - Morley | NT - Northern Terminal Load Area | Normal | 65.6
|  | SUB LOAD - MO - 11.0 kV_DCAP | MO - Morley | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - MOR - T1 | MOR - Moora | NC - North Country Load Area | Normal | 4
|  | SUB LOAD - MOR - T1_DCAP | MOR - Moora | NC - North Country Load Area | Normal | 0
|  | SUB LOAD - MOR - T3 | MOR - Moora | NC - North Country Load Area | Normal | 10.7
|  | SUB LOAD - MOR - T3_DCAP | MOR - Moora | NC - North Country Load Area | Normal | 0
|  | SUB LOAD - MR - 22.0 kV | MR - Margaret River | BPS - Bunbury Load Area | Normal | 15.4
|  | SUB LOAD - MR - 22.0 kV_DCAP | MR - Margaret River | BPS - Bunbury Load Area | Normal | 0
|  | SUB LOAD - MRR - 22.0 kV | MRR - Marriott Road | BPS - Bunbury Load Area | Normal | 21.7
|  | SUB LOAD - MRR - 22.0 kV_DCAP | MRR - Marriott Road | BPS - Bunbury Load Area | Normal | 0
|  | SUB LOAD - MSR - 1 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 8.4
|  | SUB LOAD - MSR - 1_DCAP | MSR - Mason Road | KW - Kwinana Load Area | Normal | 0
|  | SUB LOAD - MSR - 2 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 8.7
|  | SUB LOAD - MSR - 2_DCAP | MSR - Mason Road | KW - Kwinana Load Area | Normal | 0
|  | SUB LOAD - MSR - 3 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 8.4
|  | SUB LOAD - MSR - 3_DCAP | MSR - Mason Road | KW - Kwinana Load Area | Normal | 0
|  | SUB LOAD - MSS - 22.0 kV | MSS - Meadow Springs | KW - Kwinana Load Area | Normal | 85.5
|  | SUB LOAD - MSS - 22.0 kV_DCAP | MSS - Meadow Springs | KW - Kwinana Load Area | Normal | 0
|  | SUB LOAD - MUC - 22.0 kV | MUC - Muchea | NT - Northern Terminal Load Area | Normal | 27.8
|  | SUB LOAD - MUC - 22.0 kV_DCAP | MUC - Muchea | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - MUL - 22.0 kV | MUL - Mullaloo | NT - Northern Terminal Load Area | Normal | 61.9
|  | SUB LOAD - MUL - 22.0 kV_DCAP | MUL - Mullaloo | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - MUR - 22.0 kV | MUR - Murdoch | ST - Southern Terminal Load Area | Normal | 39
|  | SUB LOAD - MUR - 22.0 kV_DCAP | MUR - Murdoch | ST - Southern Terminal Load Area | Normal | 0
|  | SUB LOAD - MYR - 22.0 kV | MYR - Myaree | SF - South Fremantle Load Area | Normal | 46.5
|  | SUB LOAD - MYR - 22.0 kV_DCAP | MYR - Myaree | SF - South Fremantle Load Area | Normal | 0
|  | SUB LOAD - NB - 22.0 kV | NB - North Beach | NT - Northern Terminal Load Area | Normal | 62.2
|  | SUB LOAD - NB - 22.0 kV_DCAP | NB - North Beach | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - NGN - 22.0 kV | NGN - Narrogin | MU - Muja Load Area | Normal | 11.2
|  | SUB LOAD - NGN - 22.0 kV_DCAP | NGN - Narrogin | MU - Muja Load Area | Normal | 0
|  | SUB LOAD - NOR - 22.0 kV | NOR - Northam | EC - East Country Load Area | Normal | 21.6
|  | SUB LOAD - NOR - 22.0 kV_DCAP | NOR - Northam | EC - East Country Load Area | Normal | 0
|  | SUB LOAD - NP - 11.0 kV | NP - North Perth | EP - East Perth Load Area | Normal | 62.1
|  | SUB LOAD - NP - 11.0 kV_DCAP | NP - North Perth | EP - East Perth Load Area | Normal | 0
|  | SUB LOAD - OC - 22.0 kV | OC - OConnor | SF - South Fremantle Load Area | Normal | 51.9
|  | SUB LOAD - OC - 22.0 kV_DCAP | OC - OConnor | SF - South Fremantle Load Area | Normal | 0
|  | SUB LOAD - OP - 11.0 kV | OP - Osborne Park | NT - Northern Terminal Load Area | Normal | 44.3
|  | SUB LOAD - OP - 11.0 kV_DCAP | OP - Osborne Park | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - PBY - 22.0 kV | PBY - Padbury | NT - Northern Terminal Load Area | Normal | 68.4
|  | SUB LOAD - PBY - 22.0 kV_DCAP | PBY - Padbury | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - PCY - 11.0 kV | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Normal | 27.7
|  | SUB LOAD - PCY - 11.0 kV_DCAP | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Normal | 0
|  | SUB LOAD - PIC - 22.0 kV | PIC - Picton | BPS - Bunbury Load Area | Normal | 44.4
|  | SUB LOAD - PIC - 22.0 kV_DCAP | PIC - Picton | BPS - Bunbury Load Area | Normal | 0
|  | SUB LOAD - PNJ - 22.0 kV | PNJ - Pinjarra | BPS - Bunbury Load Area | Normal | 33.8
|  | SUB LOAD - PNJ - 22.0 kV_DCAP | PNJ - Pinjarra | BPS - Bunbury Load Area | Normal | 0
|  | SUB LOAD - RAN - 11.0 kV | RAN - Rangeway | NC - North Country Load Area | Normal | 32.9
|  | SUB LOAD - RAN - 11.0 kV_DCAP | RAN - Rangeway | NC - North Country Load Area | Normal | 0
|  | SUB LOAD - RGN - 22.0 kV | RGN - Regans | NC - North Country Load Area | Normal | 6.7
|  | SUB LOAD - RGN - 22.0 kV_DCAP | RGN - Regans | NC - North Country Load Area | Normal | 0
|  | SUB LOAD - RGN - 33.0 kV | RGN - Regans | NC - North Country Load Area | Normal | 7
|  | SUB LOAD - RGN - 33.0 kV_DCAP | RGN - Regans | NC - North Country Load Area | Normal | 0
|  | SUB LOAD - RO - 22.0 kV | RO - Rockingham | KW - Kwinana Load Area | Normal | 59.3
|  | SUB LOAD - RO - 22.0 kV_DCAP | RO - Rockingham | KW - Kwinana Load Area | Normal | 0
|  | SUB LOAD - RTN - 22.0 kV | RTN - Riverton | ST - Southern Terminal Load Area | Normal | 77.8
|  | SUB LOAD - RTN - 22.0 kV_DCAP | RTN - Riverton | ST - Southern Terminal Load Area | Normal | 0
|  | SUB LOAD - RVE - 22.0 kV | RVE - Rivervale | CT - Cannington Terminal Load Area | Normal | 67
|  | SUB LOAD - RVE - 22.0 kV_DCAP | RVE - Rivervale | CT - Cannington Terminal Load Area | Normal | 0
|  | SUB LOAD - SNR - 22.0 kV | SNR - Southern River | ST - Southern Terminal Load Area | Normal | 99.4
|  | SUB LOAD - SNR - 22.0 kV_DCAP | SNR - Southern River | ST - Southern Terminal Load Area | Normal | 0
|  | SUB LOAD - SPK / 1.A | SPK - Shenton Park 132kV | WT - Western Terminal Load Area | Normal | 58.1
|  | SUB LOAD - SPK / 1.A_DCAP | SPK - Shenton Park 132kV | WT - Western Terminal Load Area | Normal | 0
|  | SUB LOAD - SVY - 22.0 kV | SVY - Sawyers Valley 132kV | EC - East Country Load Area | Normal | 21.3
|  | SUB LOAD - SVY - 22.0 kV_DCAP | SVY - Sawyers Valley 132kV | EC - East Country Load Area | Normal | 0
|  | SUB LOAD - SX - 33.0 kV | SX - Southern Cross | EC - East Country Load Area | Normal | 1.3
|  | SUB LOAD - SX - 33.0 kV_DCAP | SX - Southern Cross | EC - East Country Load Area | Normal | 0
|  | SUB LOAD - TS - 33.0 kV | TS - Three Springs | NC - North Country Load Area | Normal | 8.1
|  | SUB LOAD - TS - 33.0 kV_DCAP | TS - Three Springs | NC - North Country Load Area | Normal | 0
|  | SUB LOAD - WAG - 22.0 kV | WAG - Wagin | MU - Muja Load Area | Normal | 5.1
|  | SUB LOAD - WAG - 22.0 kV_DCAP | WAG - Wagin | MU - Muja Load Area | Normal | 0
|  | SUB LOAD - WAI - 22.0 kV | WAI - Waikiki | KW - Kwinana Load Area | Normal | 87.4
|  | SUB LOAD - WAI - 22.0 kV_DCAP | WAI - Waikiki | KW - Kwinana Load Area | Normal | 0
|  | SUB LOAD - WD - 6.6 kV | WD - Wembley Downs | WT - Western Terminal Load Area | Normal | 39.4
|  | SUB LOAD - WD - 6.6 kV_DCAP | WD - Wembley Downs | WT - Western Terminal Load Area | Normal | 0
|  | SUB LOAD - WE - 22.0 kV | WE - Welshpool | CT - Cannington Terminal Load Area | Normal | 60.6
|  | SUB LOAD - WE - 22.0 kV_DCAP | WE - Welshpool | CT - Cannington Terminal Load Area | Normal | 0
|  | SUB LOAD - WGA - 22.0 kV | WGA - Wangara | NT - Northern Terminal Load Area | Normal | 29.8
|  | SUB LOAD - WGA - 22.0 kV_DCAP | WGA - Wangara | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - WGP - 22.0 kV | WGP - Wagerup | MU - Muja Load Area | Normal | 18.5
|  | SUB LOAD - WGP - 22.0 kV_DCAP | WGP - Wagerup | MU - Muja Load Area | Normal | 0
|  | SUB LOAD - WKT - 11 kV | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Normal | 8.1
|  | SUB LOAD - WKT - 11 kV_DCAP | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Normal | 0
|  | SUB LOAD - WKT - 33.0 kV | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Normal | 15.1
|  | SUB LOAD - WKT - 33.0 kV_DCAP | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Normal | 0
|  | SUB LOAD - WLN - 22.0 kV | WLN - Willetton | ST - Southern Terminal Load Area | Normal | 24.6
|  | SUB LOAD - WNO - 22.0 kV | WNO - Wanneroo | NT - Northern Terminal Load Area | Normal | 85.2
|  | SUB LOAD - WNO - 22.0 kV_DCAP | WNO - Wanneroo | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - WUN - 22.0 kV | WUN - Wundowie | EC - East Country Load Area | Normal | 10.7
|  | SUB LOAD - WUN - 22.0 kV_DCAP | WUN - Wundowie | EC - East Country Load Area | Normal | 0
|  | SUB LOAD - Y - 11.0 kV | Y - Yokine | NT - Northern Terminal Load Area | Normal | 52.2
|  | SUB LOAD - Y - 11.0 kV_DCAP | Y - Yokine | NT - Northern Terminal Load Area | Normal | 0
|  | SUB LOAD - YER - 6.6 kV | YER - Yerbillon | EC - East Country Load Area | Normal | 0.3
|  | SUB LOAD - YER - 6.6 kV_DCAP | YER - Yerbillon | EC - East Country Load Area | Normal | 0
|  | SUB LOAD - YLN - 33.0 kV | YLN - Yilgarn | EC - East Country Load Area | Normal | 10
|  | SUB LOAD - YLN - 33.0 kV_DCAP | YLN - Yilgarn | EC - East Country Load Area | Normal | 0
|  | SUB LOAD - YP - 22.0 kV | YP - Yanchep | NT - Northern Terminal Load Area | Normal | 72.1
|  | SUB LOAD - YP - 22.0 kV_DCAP | YP - Yanchep | NT - Northern Terminal Load Area | Normal | 0