## outputA
Project Name: CNSW-SNW Option 6b | [5 empty] | Indirect Cost Selection
• A new 500 kV double-circuit line between Eraring and Bayswater substation. • A new 500/330 kV substation in locality of Richmond Vale with two 500/330 kV 1,500 MVA transformers, cut in Newcastle-Liddell (#81) and Tomago-Liddell (#82) 330 kV lines, and a new 5 km DCST cutting-in between Tomago-Newcastle 330 kV line (#95). • Two 500/330 kV 1,500 MVA transformers (bringing the total to four transformers) near Eraring. • 1 x 330 kV single-circuit line between Vales Pt and new Eraring. • 1 x 330 kV single-circuit line between Vales Pt and Munmorah. • Thermal upgrade for 330 kV lines Vales Pt – Eraring (#24) and Newcastle – Vales Point (#92). • 1 x 330 kV single-circuit line between locality of Richmond Vale – Newcastle. • Line reactors on 500 kV transmission lines. | [5 empty] | Total Network Elements Cost Category |  |  | $1000-$1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View A | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | CNSW-SNW Option 6b.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element Number | Network Element | Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Bayswater - near Eraring Overhead line | 681253719.1459 | 182418789.686 | 179822829.9778 | 130780239.9928 | 0 | 22942670.8514 | 0 | 96971035.8496 | 21615922.6208 | 46702230.1675
2 | Bayswater Substation | 53406429.7375 | 14178794.24 | 25361754.368 | 3906431.36 | 3455689.28 | 2343095.04 | 1116603.62 | 2960497.1772 | 26439.9238 | 57124.7285
3 | Near Eraring new substation | 208096989.0252 | 88829829.4525 | 73498531.5372 | 14932965.9877 | 8987068.1931 | 8770517.5158 | 3844956.341 | 8940643.6815 | 92539.7666 | 199936.5498
4 | Near Richmond Vale line diversion | 7218587.968 | 1922136.1761 | 1111259.2898 | 2778148.2389 | 0 | 329953.7472 | 0 | 352504.0413 | 229259.7905 | 495326.6842
5 | Richmond Vales Substation | 116230296.0544 | 23691871.024 | 57473053.824 | 9273933.024 | 7315815.36 | 6429209.6 | 3005848.88 | 8748088.026 | 92539.7666 | 199936.5498
6 | Vales Pt - New Eraring | 55763119.5346 | 14919784.782 | 14707464.7665 | 10696338.018 | 0 | 1876449.8523 | 0 | 5109573.3158 | 2674697.4944 | 5778811.3055
7 | Vales Pt - Munmorah | 107543159.1034 | 28773870.65 | 28364396.3331 | 20628651.8801 | 0 | 3618867.5844 | 0 | 9854177.1055 | 5158345.1711 | 11144850.3792
8 | Richmond Vales-Newcastle | 131441638.9216 | 35168064.134 | 34667595.5328 | 25212796.7496 | 0 | 4423060.3673 | 0 | 12043994.2372 | 6304644.1006 | 13621483.8001
9 | Vales Pt substation | 28192456.2507 | 4844592.544 | 14874881.952 | 1970183.04 | 1864815.68 | 1475795.84 | 744022 | 2376382.8574 | 13219.973 | 28562.3643
10 | Munmorah substation | 24586149.3227 | 3445619.296 | 14114954.208 | 1463564.544 | 1721368.32 | 1081276.16 | 595217.6 | 2122366.8574 | 13219.973 | 28562.3643
11 | Newcastle substation | 18676810.0747 | 1813483.84 | 11581861.728 | 1083600.672 | 1577920.96 | 686756.48 | 446413.2 | 1444990.8574 | 13219.973 | 28562.3643
12 | Thermal upgrade for Vales Pt – Eraring and Newcastle – Vales Pt | 59315690.2259 | 20177532.368 | 0 | 28931477.1737 | 0 | 0 | 0 | 10206680.6843 | 0 | 0
| Total Network Element Cost | 1491725045.3647 | 420184368.1926 | 455578583.5173 | 251658330.6808 | 24922677.7931 | 53977653.0384 | 9753061.641 | 161130934.6908 | 36234048.5534 | 78285387.2574
Indirect Costs
| Project Development | 65337556.987
| Works Delivery | 73691217.241
| Land and Environment | 8353660.254
| Stakeholder and Community Engagement | 7309452.7223
| Procurement Costs | 5221037.6588
| Insurance | 4176830.127
| Total Indirect Cost | 164089754.9901
| Total Expected Project Cost | 1655814800.3549

## outputB
Project Name: CNSW-SNW Option 6b | [5 empty] | Indirect Cost Selection
• A new 500 kV double-circuit line between Eraring and Bayswater substation. • A new 500/330 kV substation in locality of Richmond Vale with two 500/330 kV 1,500 MVA transformers, cut in Newcastle-Liddell (#81) and Tomago-Liddell (#82) 330 kV lines, and a new 5 km DCST cutting-in between Tomago-Newcastle 330 kV line (#95). • Two 500/330 kV 1,500 MVA transformers (bringing the total to four transformers) near Eraring. • 1 x 330 kV single-circuit line between Vales Pt and new Eraring. • 1 x 330 kV single-circuit line between Vales Pt and Munmorah. • Thermal upgrade for 330 kV lines Vales Pt – Eraring (#24) and Newcastle – Vales Point (#92). • 1 x 330 kV single-circuit line between locality of Richmond Vale – Newcastle. • Line reactors on 500 kV transmission lines. | [5 empty] | Total Network Elements Cost Category |  |  | $1000-$1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View B | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | CNSW-SNW Option 6b.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
| Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 1096706776.87 | 307552835.27 | 297472590.38 | 157543821.61 | 17265063.5 | 35938784.83 | 6533899.63 | 127274391.86 | 15812278.76 | 131313111.03
Adjusted Baseline Cost | 1110711935.318 | 303005729.1795 | 329549934.3951 | 180441468.9449 | 18325498.3773 | 38992160.7971 | 7041921.7625 | 143866905.9739 | 28314180.5577 | 61174135.3301
Known Risk Allowance | 41024992.8213 | 12120229.1672 | 13181997.3758 | 7217658.7578 | 733019.9351 | 1559686.4319 | 457724.9146 | 5754676.239 | 0 | 0
Unknown Risk Allowance | 339988117.2254 | 105058409.8459 | 112846651.7464 | 63999202.9782 | 5864159.4807 | 13425805.8094 | 2253414.964 | 11509352.4779 | 7919867.9956 | 17111251.9272
Total Network Element Cost | 1491725045.3647 | 420184368.1926 | 455578583.5173 | 251658330.6808 | 24922677.7931 | 53977653.0384 | 9753061.641 | 161130934.6908 | 36234048.5534 | 78285387.2574
Indirect Costs
Project Development | 65337556.987
Works Delivery | 73691217.241
Land and Environment | 8353660.254
Stakeholder and Community Engagement | 7309452.7223
Procurement Costs | 5221037.6588
Insurance | 4176830.127
Total Indirect Cost | 164089754.9901
Total Expected Project Cost | 1655814800.3549

## outputC
Project Name: CNSW-SNW Option 6b
• A new 500 kV double-circuit line between Eraring and Bayswater substation. • A new 500/330 kV substation in locality of Richmond Vale with two 500/330 kV 1,500 MVA transformers, cut in Newcastle-Liddell (#81) and Tomago-Liddell (#82) 330 kV lines, and a new 5 km DCST cutting-in between Tomago-Newcastle 330 kV line (#95). • Two 500/330 kV 1,500 MVA transformers (bringing the total to four transformers) near Eraring. • 1 x 330 kV single-circuit line between Vales Pt and new Eraring. • 1 x 330 kV single-circuit line between Vales Pt and Munmorah. • Thermal upgrade for 330 kV lines Vales Pt – Eraring (#24) and Newcastle – Vales Point (#92). • 1 x 330 kV single-circuit line between locality of Richmond Vale – Newcastle. • Line reactors on 500 kV transmission lines.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | CNSW-SNW Option 6b.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element 1
Bayswater - near Eraring Overhead line
500 kV double circuit line
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 99 | km | 130299135.49 | 110253114.64 | 80184083.38 | 0 | 15034515.63 | 0 | 75948492.99 | 9430924.59 | 78319138.45 | 499469405.17 | 73.32%
Baseline Cost | [6 empty] | 130299135.49 | 110253114.64 | 80184083.38 | 0 | 15034515.63 | 0 | 75948492.99 | 9430924.59 | 78319138.45 | 499469405.17 | 73.32%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 100 to 200km |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Hilly/Undulating |  |  |  | 0% | 7.5% | 7.5% | 0% | 0% | 0% | 5% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0% | 16.5% | 16.5% | 0% | 9% | 9% | 14% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 130299135.49 | 128444878.5556 | 93414457.1377 | 0 | 16387622.0367 | 0 | 86581282.0086 | 16887439.5475 | 36486117.3184 | 508500932.0945 | 74.64%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 5211965.4196 | 5137795.1422 | 3736578.2855 | 0 | 655504.8815 | 0 | 3463251.2803 | 0 | 0 | 18205095.0091 | 2.672%
Subtotal Including Known Risks | [6 empty] | 135511100.9096 | 133582673.6978 | 97151035.4232 | 0 | 17043126.9182 | 0 | 90044533.2889 | 16887439.5475 | 36486117.3184 | 526706027.1036 | 77.31%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 46907688.7764 | 46240156.28 | 33629204.5696 | 0 | 5899543.9332 | 0 | 6926502.5607 | 4728483.0733 | 10216112.8491 | 154547692.0423 | 22.69%
Subtotal Including Unknown Risks | [6 empty] | 182418789.686 | 179822829.9778 | 130780239.9928 | 0 | 22942670.8514 | 0 | 96971035.8496 | 21615922.6208 | 46702230.1675 | 681253719.1459 | 100%
Network Element 2
Bayswater Substation
500 kV extension
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 1 | lot | 4050000 | 4500000 | 1350000 | 600000 | 810000 | 300000 | 840000 | 0 | 0 | 12450000 | 23.31%
| Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 1 | lot | 1350000 | 1800000 | 450000 | 100000 | 270000 | 100000 | 350000 | 0 | 0 | 4420000 | 8.276%
| Station | Reactive Plant | Reactor 100MVAr | 500 | 1 | ea. | 4300000 | 1200000 | 100000 | 200000 | 200000 | 50000 | 0 | 0 | 0 | 6050000 | 11.33%
| Station | Property site work and building | AIS site infrastructure 10000 m2 footprint area and applicable control building | N/A | 1 | lot | 700000 | 9380000 | 700000 | 1400000 | 280000 | 280000 | 1149204.47 | 11907.73 | 98887.8 | 14000000 | 26.21%
Baseline Cost | [6 empty] | 10400000 | 16880000 | 2600000 | 2300000 | 1560000 | 730000 | 2339204.47 | 11907.73 | 98887.8 | 36920000 | 69.13%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 11 - 15 |  |  |  | 0.246% | 1.476% | 1.476% | 1.476% | 1.44% | 1.44% | 4% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0.246% | 10.48% | 10.48% | 10.48% | 10.44% | 10.44% | 13% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 10425584 | 18648348.8 | 2872376 | 2540948 | 1722864 | 806212 | 2643301.0511 | 21322.5192 | 46068.3294 | 39727024.6997 | 74.39%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 417023.36 | 745933.952 | 114895.04 | 101637.92 | 68914.56 | 52403.78 | 105732.042 | 0 | 0 | 1606540.654 | 3.008%
Subtotal Including Known Risks | [6 empty] | 10842607.36 | 19394282.752 | 2987271.04 | 2642585.92 | 1791778.56 | 858615.78 | 2749033.0931 | 21322.5192 | 46068.3294 | 41333565.3538 | 77.39%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 3336186.88 | 5967471.616 | 919160.32 | 813103.36 | 551316.48 | 257987.84 | 211464.0841 | 5117.4046 | 11056.3991 | 12072864.3838 | 22.61%
Subtotal Including Unknown Risks | [6 empty] | 14178794.24 | 25361754.368 | 3906431.36 | 3455689.28 | 2343095.04 | 1116603.62 | 2960497.1772 | 26439.9238 | 57124.7285 | 53406429.7375 | 100%
Network Element 3
Near Eraring new substation
2x 500/330 kV Tx
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 8100000 | 9000000 | 2700000 | 1200000 | 1620000 | 600000 | 1680000 | 0 | 0 | 24900000 | 11.97%
| Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 2 | ea. | 35100000 | 5580000 | 2880000 | 400000 | 720000 | 300000 | 0 | 0 | 0 | 44980000 | 21.61%
| Station | Property site work and building | AIS site infrastructure 35000 m2 footprint area and applicable control building | N/A | 1 | lot | 1550000 | 20770000 | 1550000 | 3100000 | 620000 | 620000 | 2402215.63 | 41677.07 | 346107.3 | 31000000 | 14.9%
| Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 2 | lot | 6480000 | 7740000 | 1800000 | 600000 | 1620000 | 600000 | 2240000 | 0 | 0 | 21080000 | 10.13%
| Station | Secondary system building | Demountable building 10 × 3 × 4m size | N/A | 1 | ea. | 396161.8 | 137606.3 | 31274.16 | 65063.5 | 12336.13 | 13899.63 | 19189.53 | 0 | 0 | 675531.05 | 0.3246%
| Station | Reactive Plant | Reactor 100MVAr | 500 | 1 | ea. | 4300000 | 1200000 | 100000 | 200000 | 200000 | 50000 | 0 | 0 | 0 | 6050000 | 2.907%
| Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 1 | lot | 1350000 | 1800000 | 450000 | 100000 | 270000 | 100000 | 350000 | 0 | 0 | 4420000 | 2.124%
| Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 2700000 | 3600000 | 900000 | 200000 | 540000 | 200000 | 700000 | 0 | 0 | 8840000 | 4.248%
| Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 8600000 | 2400000 | 200000 | 400000 | 400000 | 100000 | 0 | 0 | 0 | 12100000 | 5.815%
Baseline Cost | [6 empty] | 68576161.8 | 52227606.3 | 10611274.16 | 6265063.5 | 6002336.13 | 2583899.63 | 7391405.16 | 41677.07 | 346107.3 | 154045531.05 | 74.03%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 11 - 15 |  |  |  | 0.246% | 1.476% | 1.476% | 1.476% | 1.44% | 1.44% | 4% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | -5% | -3% | -3% | -5% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -4.754% | 3.476% | 3.476% | 5.476% | 7.44% | 7.44% | 8% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 65316051.068 | 54043037.895 | 10980122.0498 | 6608138.3773 | 6448909.9381 | 2776141.7625 | 7982717.5728 | 74628.844 | 161239.1531 | 154390986.6605 | 74.19%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 2612642.0427 | 2161721.5158 | 439204.882 | 264325.5351 | 257956.3975 | 180449.2146 | 319308.7029 | 0 | 0 | 6235608.2906 | 2.996%
Subtotal Including Known Risks | [6 empty] | 67928693.1107 | 56204759.4108 | 11419326.9318 | 6872463.9124 | 6706866.3356 | 2956590.977 | 8302026.2757 | 74628.844 | 161239.1531 | 160626594.9511 | 77.19%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 20901136.3418 | 17293772.1264 | 3513639.0559 | 2114604.2807 | 2063651.1802 | 888365.364 | 638617.4058 | 17910.9226 | 38697.3967 | 47470394.0741 | 22.81%
Subtotal Including Unknown Risks | [6 empty] | 88829829.4525 | 73498531.5372 | 14932965.9877 | 8987068.1931 | 8770517.5158 | 3844956.341 | 8940643.6815 | 92539.7666 | 199936.5498 | 208096989.0252 | 100%
Network Element 4
Near Richmond Vale line diversion
2x 330kV SCST Type 5 cut-ins at lines 81 and 82
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC line diversion | Type 5 (3 × conductor/phase SCST) | 330 | 2 | lot | 1445215.17 | 778192.78 | 1945481.96 | 0 | 222340.8 | 0 | 302630.53 | 100024.96 | 830657.53 | 5624543.73 | 77.92%
Baseline Cost | [6 empty] | 1445215.17 | 778192.78 | 1945481.96 | 0 | 222340.8 | 0 | 302630.53 | 100024.96 | 830657.53 | 5624543.73 | 77.92%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 100 to 200km |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | 0% | -3% | -3% | -5% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Flat/Farmland |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -5% | 2% | 2% | 0% | 6% | 6% | 4% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 1372954.4115 | 793756.6356 | 1984391.5992 | 0 | 235681.248 | 0 | 314735.7512 | 179109.2113 | 386973.972 | 5267602.8288 | 72.97%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 54918.1765 | 31750.2654 | 79375.664 | 0 | 9427.2499 | 0 | 12589.43 | 0 | 0 | 188060.7858 | 2.605%
Subtotal Including Known Risks | [6 empty] | 1427872.588 | 825506.901 | 2063767.2632 | 0 | 245108.4979 | 0 | 327325.1812 | 179109.2113 | 386973.972 | 5455663.6146 | 75.58%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 494263.5881 | 285752.3888 | 714380.9757 | 0 | 84845.2493 | 0 | 25178.8601 | 50150.5792 | 108352.7122 | 1762924.3534 | 24.42%
Subtotal Including Unknown Risks | [6 empty] | 1922136.1761 | 1111259.2898 | 2778148.2389 | 0 | 329953.7472 | 0 | 352504.0413 | 229259.7905 | 495326.6842 | 7218587.968 | 100%
Network Element 5
Richmond Vales Substation
500/330 kV
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 8100000 | 9000000 | 2700000 | 1200000 | 1620000 | 600000 | 1680000 | 0 | 0 | 24900000 | 21.42%
| Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 2 | lot | 6480000 | 7740000 | 1800000 | 600000 | 1620000 | 600000 | 2240000 | 0 | 0 | 21080000 | 18.14%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 2160000 | 3330000 | 540000 | 200000 | 540000 | 200000 | 910000 | 0 | 0 | 7880000 | 6.78%
| Station | Property site work and building | AIS site infrastructure 35000 m2 footprint area and applicable control building | N/A | 1 | lot | 1550000 | 20770000 | 1550000 | 3100000 | 620000 | 620000 | 2402215.63 | 41677.07 | 346107.3 | 31000000 | 26.67%
Baseline Cost | [6 empty] | 18290000 | 40840000 | 6590000 | 5100000 | 4400000 | 2020000 | 7232215.63 | 41677.07 | 346107.3 | 84860000 | 73.01%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 11 - 15 |  |  |  | 0.246% | 1.476% | 1.476% | 1.476% | 1.44% | 1.44% | 4% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | -5% | -3% | -3% | -5% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -4.754% | 3.476% | 3.476% | 5.476% | 7.44% | 7.44% | 8% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 17420493.4 | 42259598.4 | 6819068.4 | 5379276 | 4727360 | 2170288 | 7810792.8804 | 74628.844 | 161239.1531 | 86822745.0775 | 74.7%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 696819.736 | 1690383.936 | 272762.736 | 215171.04 | 189094.4 | 141068.72 | 312431.7152 | 0 | 0 | 3517732.2832 | 3.027%
Subtotal Including Known Risks | [6 empty] | 18117313.136 | 43949982.336 | 7091831.136 | 5594447.04 | 4916454.4 | 2311356.72 | 8123224.5956 | 74628.844 | 161239.1531 | 90340477.3607 | 77.73%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 5574557.888 | 13523071.488 | 2182101.888 | 1721368.32 | 1512755.2 | 694492.16 | 624863.4304 | 17910.9226 | 38697.3967 | 25889818.6937 | 22.27%
Subtotal Including Unknown Risks | [6 empty] | 23691871.024 | 57473053.824 | 9273933.024 | 7315815.36 | 6429209.6 | 3005848.88 | 8748088.026 | 92539.7666 | 199936.5498 | 116230296.0544 | 100%
Network Element 6
Vales Pt - New Eraring
330 kV SCST
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 14 | km | 10656989.13 | 9017452.34 | 6558147.16 | 0 | 1229652.59 | 0 | 4001858.8 | 1166957.84 | 9691004.5 | 42322062.36 | 75.9%
Baseline Cost | [6 empty] | 10656989.13 | 9017452.34 | 6558147.16 | 0 | 1229652.59 | 0 | 4001858.8 | 1166957.84 | 9691004.5 | 42322062.36 | 75.9%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 100 to 200km |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Hilly/Undulating |  |  |  | 0% | 7.5% | 7.5% | 0% | 0% | 0% | 5% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0% | 16.5% | 16.5% | 0% | 9% | 9% | 14% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 10656989.13 | 10505331.9761 | 7640241.4414 | 0 | 1340321.3231 | 0 | 4562119.032 | 2089607.4175 | 4514696.3324 | 41309306.6526 | 74.08%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 426279.5652 | 420213.279 | 305609.6577 | 0 | 53612.8529 | 0 | 182484.7613 | 0 | 0 | 1388200.1161 | 2.489%
Subtotal Including Known Risks | [6 empty] | 11083268.6952 | 10925545.2551 | 7945851.0991 | 0 | 1393934.176 | 0 | 4744603.7933 | 2089607.4175 | 4514696.3324 | 42697506.7687 | 76.57%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 3836516.0868 | 3781919.5114 | 2750486.9189 | 0 | 482515.6763 | 0 | 364969.5226 | 585090.0769 | 1264114.9731 | 13065612.766 | 23.43%
Subtotal Including Unknown Risks | [6 empty] | 14919784.782 | 14707464.7665 | 10696338.018 | 0 | 1876449.8523 | 0 | 5109573.3158 | 2674697.4944 | 5778811.3055 | 55763119.5346 | 100%
Network Element 7
Vales Pt - Munmorah
330 kV SCST
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 27 | km | 20552764.75 | 17390800.94 | 12647855.23 | 0 | 2371472.86 | 0 | 7717870.54 | 2250561.55 | 18689794.4 | 81621120.27 | 75.9%
Baseline Cost | [6 empty] | 20552764.75 | 17390800.94 | 12647855.23 | 0 | 2371472.86 | 0 | 7717870.54 | 2250561.55 | 18689794.4 | 81621120.27 | 75.9%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 100 to 200km |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Hilly/Undulating |  |  |  | 0% | 7.5% | 7.5% | 0% | 0% | 0% | 5% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0% | 16.5% | 16.5% | 0% | 9% | 9% | 14% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 20552764.75 | 20260283.0951 | 14734751.3429 | 0 | 2584905.4174 | 0 | 8798372.4156 | 4029957.1649 | 8706914.3587 | 79667948.5447 | 74.08%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 822110.59 | 810411.3238 | 589390.0537 | 0 | 103396.2167 | 0 | 351934.8966 | 0 | 0 | 2677243.0808 | 2.489%
Subtotal Including Known Risks | [6 empty] | 21374875.34 | 21070694.4189 | 15324141.3967 | 0 | 2688301.6341 | 0 | 9150307.3122 | 4029957.1649 | 8706914.3587 | 82345191.6256 | 76.57%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 7398995.31 | 7293701.9142 | 5304510.4835 | 0 | 930565.9503 | 0 | 703869.7932 | 1128388.0062 | 2437936.0204 | 25197967.4778 | 23.43%
Subtotal Including Unknown Risks | [6 empty] | 28773870.65 | 28364396.3331 | 20628651.8801 | 0 | 3618867.5844 | 0 | 9854177.1055 | 5158345.1711 | 11144850.3792 | 107543159.1034 | 100%
Network Element 8
Richmond Vales-Newcastle
330 kV SCST
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 33 | km | 25120045.81 | 21255423.38 | 15458489.73 | 0 | 2898466.82 | 0 | 9432952.88 | 2750686.34 | 22843082.05 | 99759147.01 | 75.9%
Baseline Cost | [6 empty] | 25120045.81 | 21255423.38 | 15458489.73 | 0 | 2898466.82 | 0 | 9432952.88 | 2750686.34 | 22843082.05 | 99759147.01 | 75.9%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 100 to 200km |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Hilly/Undulating |  |  |  | 0% | 7.5% | 7.5% | 0% | 0% | 0% | 5% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0% | 16.5% | 16.5% | 0% | 9% | 9% | 14% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 25120045.81 | 24762568.2377 | 18009140.5355 | 0 | 3159328.8338 | 0 | 10753566.2832 | 4925503.2036 | 10641784.2188 | 97371937.1226 | 74.08%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 1004801.8324 | 990502.7295 | 720365.6214 | 0 | 126373.1534 | 0 | 430142.6513 | 0 | 0 | 3272185.988 | 2.489%
Subtotal Including Known Risks | [6 empty] | 26124847.6424 | 25753070.9672 | 18729506.1569 | 0 | 3285701.9872 | 0 | 11183708.9345 | 4925503.2036 | 10641784.2188 | 100644123.1106 | 76.57%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 9043216.4916 | 8914524.5656 | 6483290.5928 | 0 | 1137358.3802 | 0 | 860285.3027 | 1379140.897 | 2979699.5813 | 30797515.811 | 23.43%
Subtotal Including Unknown Risks | [6 empty] | 35168064.134 | 34667595.5328 | 25212796.7496 | 0 | 4423060.3673 | 0 | 12043994.2372 | 6304644.1006 | 13621483.8001 | 131441638.9216 | 100%
Network Element 9
Vales Pt substation
330 kV bays
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 1 | lot | 3240000 | 3870000 | 900000 | 300000 | 810000 | 300000 | 1120000 | 0 | 0 | 10540000 | 37.39%
| Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 500000 | 6700000 | 500000 | 1000000 | 200000 | 200000 | 844602.23 | 5953.87 | 49443.9 | 10000000 | 35.47%
Baseline Cost | [6 empty] | 3740000 | 10570000 | 1400000 | 1300000 | 1010000 | 500000 | 1964602.23 | 5953.87 | 49443.9 | 20540000 | 72.86%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 11 - 15 |  |  |  | 0.246% | 1.476% | 1.476% | 1.476% | 1.44% | 1.44% | 4% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | -5% | -3% | -3% | -5% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -4.754% | 3.476% | 3.476% | 5.476% | 7.44% | 7.44% | 8% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 3562200.4 | 10937413.2 | 1448664 | 1371188 | 1085144 | 537200 | 2121770.4084 | 10661.2685 | 23034.1647 | 21097275.4417 | 74.83%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 142488.016 | 437496.528 | 57946.56 | 54847.52 | 43405.76 | 34918 | 84870.8163 | 0 | 0 | 855973.2003 | 3.036%
Subtotal Including Known Risks | [6 empty] | 3704688.416 | 11374909.728 | 1506610.56 | 1426035.52 | 1128549.76 | 572118 | 2206641.2247 | 10661.2685 | 23034.1647 | 21953248.642 | 77.87%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 1139904.128 | 3499972.224 | 463572.48 | 438780.16 | 347246.08 | 171904 | 169741.6327 | 2558.7045 | 5528.1995 | 6239207.6087 | 22.13%
Subtotal Including Unknown Risks | [6 empty] | 4844592.544 | 14874881.952 | 1970183.04 | 1864815.68 | 1475795.84 | 744022 | 2376382.8574 | 13219.973 | 28562.3643 | 28192456.2507 | 100%
Network Element 10
Munmorah substation
330 kV bays
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 500000 | 6700000 | 500000 | 1000000 | 200000 | 200000 | 844602.23 | 5953.87 | 49443.9 | 10000000 | 40.67%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 2160000 | 3330000 | 540000 | 200000 | 540000 | 200000 | 910000 | 0 | 0 | 7880000 | 32.05%
Baseline Cost | [6 empty] | 2660000 | 10030000 | 1040000 | 1200000 | 740000 | 400000 | 1754602.23 | 5953.87 | 49443.9 | 17880000 | 72.72%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 11 - 15 |  |  |  | 0.246% | 1.476% | 1.476% | 1.476% | 1.44% | 1.44% | 4% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | -5% | -3% | -3% | -5% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -4.754% | 3.476% | 3.476% | 5.476% | 7.44% | 7.44% | 8% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 2533543.6 | 10378642.8 | 1076150.4 | 1265712 | 795056 | 429760 | 1894970.4084 | 10661.2685 | 23034.1647 | 18407530.6417 | 74.87%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 101341.744 | 415145.712 | 43046.016 | 50628.48 | 31802.24 | 27934.4 | 75798.8163 | 0 | 0 | 745697.4083 | 3.033%
Subtotal Including Known Risks | [6 empty] | 2634885.344 | 10793788.512 | 1119196.416 | 1316340.48 | 826858.24 | 457694.4 | 1970769.2247 | 10661.2685 | 23034.1647 | 19153228.05 | 77.9%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 810733.952 | 3321165.696 | 344368.128 | 405027.84 | 254417.92 | 137523.2 | 151597.6327 | 2558.7045 | 5528.1995 | 5432921.2727 | 22.1%
Subtotal Including Unknown Risks | [6 empty] | 3445619.296 | 14114954.208 | 1463564.544 | 1721368.32 | 1081276.16 | 595217.6 | 2122366.8574 | 13219.973 | 28562.3643 | 24586149.3227 | 100%
Network Element 11
Newcastle substation
330 kV bays
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 500000 | 6700000 | 500000 | 1000000 | 200000 | 200000 | 844602.23 | 5953.87 | 49443.9 | 10000000 | 53.54%
| Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 1 | lot | 900000 | 1530000 | 270000 | 100000 | 270000 | 100000 | 350000 | 0 | 0 | 3520000 | 18.85%
Baseline Cost | [6 empty] | 1400000 | 8230000 | 770000 | 1100000 | 470000 | 300000 | 1194602.23 | 5953.87 | 49443.9 | 13520000 | 72.39%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 11 - 15 |  |  |  | 0.246% | 1.476% | 1.476% | 1.476% | 1.44% | 1.44% | 4% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | -5% | -3% | -3% | -5% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -4.754% | 3.476% | 3.476% | 5.476% | 7.44% | 7.44% | 8% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 1333444 | 8516074.8 | 796765.2 | 1160236 | 504968 | 322320 | 1290170.4084 | 10661.2685 | 23034.1647 | 13957673.8417 | 74.73%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 53337.76 | 340642.992 | 31870.608 | 46409.44 | 20198.72 | 20950.8 | 51606.8163 | 0 | 0 | 565017.1363 | 3.025%
Subtotal Including Known Risks | [6 empty] | 1386781.76 | 8856717.792 | 828635.808 | 1206645.44 | 525166.72 | 343270.8 | 1341777.2247 | 10661.2685 | 23034.1647 | 14522690.978 | 77.76%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 426702.08 | 2725143.936 | 254964.864 | 371275.52 | 161589.76 | 103142.4 | 103213.6327 | 2558.7045 | 5528.1995 | 4154119.0967 | 22.24%
Subtotal Including Unknown Risks | [6 empty] | 1813483.84 | 11581861.728 | 1083600.672 | 1577920.96 | 686756.48 | 446413.2 | 1444990.8574 | 13219.973 | 28562.3643 | 18676810.0747 | 100%
Network Element 12
Thermal upgrade for Vales Pt – Eraring and Newcastle – Vales Pt
Costed as a Stage 2 development
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | Stage 2 development: 2 x Olive DCST 2212 MVA | 330 | 30 | km | 6651933.75 | 0 | 8186995.38 | 0 | 0 | 0 | 3689517.31 | 0 | 0 | 18528446.44 | 31.24%
| Overhead line | HVAC | Stage 2 development: 2 x Olive DCST 2212 MVA | 330 | 35 | km | 7760589.37 | 0 | 9551494.61 | 0 | 0 | 0 | 4304436.86 | 0 | 0 | 21616520.84 | 36.44%
Baseline Cost | [6 empty] | 14412523.12 | 0 | 17738489.99 | 0 | 0 | 0 | 7993954.17 | 0 | 0 | 40144967.28 | 67.68%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 100 to 200km |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Hilly/Undulating |  |  |  | 0% | 7.5% | 7.5% | 0% | 0% | 0% | 5% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0% | 16.5% | 16.5% | 0% | 9% | 9% | 14% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 14412523.12 | 0 | 20665340.8384 | 0 | 0 | 0 | 9113107.7538 | 0 | 0 | 44190971.7122 | 74.5%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 576500.9248 | 0 | 826613.6335 | 0 | 0 | 0 | 364524.3102 | 0 | 0 | 1767638.8685 | 2.98%
Subtotal Including Known Risks | [6 empty] | 14989024.0448 | 0 | 21491954.4719 | 0 | 0 | 0 | 9477632.064 | 0 | 0 | 45958610.5806 | 77.48%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 5188508.3232 | 0 | 7439522.7018 | 0 | 0 | 0 | 729048.6203 | 0 | 0 | 13357079.6453 | 22.52%
Subtotal Including Unknown Risks | [6 empty] | 20177532.368 | 0 | 28931477.1737 | 0 | 0 | 0 | 10206680.6843 | 0 | 0 | 59315690.2259 | 100%