## outputA
Project Name: REZ N5 Option 2 | [5 empty] | Indirect Cost Selection
Option 2: • Expand the existing Dinawan 500/330kV substation with an additional 500/330/33kV 1,500MVA transformer Pre-requisite: REZ N5 Option 1 or WNV-SNSW Option 1 | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Partly brownfield
Project Cost Estimate - View A | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ N5 Option 2.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element Number | Network Element | Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Dinawan 500/330kV Substation | 100869076.3636 | 37389589.38 | 41442459.52 | 6698080.36 | 4130183.6 | 3307382.4 | 1597443.2 | 6170054.1412 | 50291.7253 | 83592.0371
| Total Network Element Cost | 100869076.3636 | 37389589.38 | 41442459.52 | 6698080.36 | 4130183.6 | 3307382.4 | 1597443.2 | 6170054.1412 | 50291.7253 | 83592.0371
Indirect Costs
| Project Development | 4942584.7418
| Works Delivery | 4135632.1309
| Land and Environment | 1260863.4545
| Stakeholder and Community Engagement | 1513036.1455
| Procurement Costs | 756518.0727
| Insurance | 504345.3818
| Total Indirect Cost | 13112979.9273
| Total Expected Project Cost | 113982056.2908

## outputB
Project Name: REZ N5 Option 2 | [5 empty] | Indirect Cost Selection
Option 2: • Expand the existing Dinawan 500/330kV substation with an additional 500/330/33kV 1,500MVA transformer Pre-requisite: REZ N5 Option 1 or WNV-SNSW Option 1 | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Partly brownfield
Project Cost Estimate - View B | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ N5 Option 2.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
| Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 56660000 | 23260000 | 21560000 | 3730000 | 2300000 | 1780000 | 890000 | 2973806.7 | 17861.6 | 148331.7
Adjusted Baseline Cost | 69158869.2281 | 26146566 | 27264776 | 4716958 | 2908580 | 2249920 | 1124960 | 4639138.452 | 40557.843 | 67412.9331
Known Risk Allowance | 10701399.873 | 2876122.26 | 5452955.2 | 471695.8 | 290858 | 337488 | 112496 | 1159784.613 | 0 | 0
Unknown Risk Allowance | 21008807.2624 | 8366901.12 | 8724728.32 | 1509426.56 | 930745.6 | 719974.4 | 359987.2 | 371131.0762 | 9733.8823 | 16179.1039
Total Network Element Cost | 100869076.3636 | 37389589.38 | 41442459.52 | 6698080.36 | 4130183.6 | 3307382.4 | 1597443.2 | 6170054.1412 | 50291.7253 | 83592.0371
Indirect Costs
Project Development | 4942584.7418
Works Delivery | 4135632.1309
Land and Environment | 1260863.4545
Stakeholder and Community Engagement | 1513036.1455
Procurement Costs | 756518.0727
Insurance | 504345.3818
Total Indirect Cost | 13112979.9273
Total Expected Project Cost | 113982056.2908

## outputC
Project Name: REZ N5 Option 2
Option 2: • Expand the existing Dinawan 500/330kV substation with an additional 500/330/33kV 1,500MVA transformer Pre-requisite: REZ N5 Option 1 or WNV-SNSW Option 1
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ N5 Option 2.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element 1
Dinawan 500/330kV Substation
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 2160000 | 3330000 | 540000 | 200000 | 540000 | 200000 | 910000 | 0 | 0 | 7880000 | 7.812%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 1 | lot | 2700000 | 4050000 | 900000 | 200000 | 540000 | 200000 | 700000 | 0 | 0 | 9290000 | 9.21%
| Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 1 | ea. | 17550000 | 2790000 | 1440000 | 200000 | 360000 | 150000 | 0 | 0 | 0 | 22490000 | 22.3%
| Station | Property site work and building | AIS site infrastructure 15000 m2 footprint area and applicable control building | N/A | 1 | lot | 850000 | 11390000 | 850000 | 1700000 | 340000 | 340000 | 1363806.7 | 17861.6 | 148331.7 | 17000000 | 16.85%
Baseline Cost | [6 empty] | 23260000 | 21560000 | 3730000 | 2300000 | 1780000 | 890000 | 2973806.7 | 17861.6 | 148331.7 | 56660000 | 56.17%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 5% | 5% | 5% | 5% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 1 - 5 |  |  |  | 0.41% | 2.46% | 2.46% | 2.46% | 2.4% | 2.4% | 12% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Southern - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 127.1% | -54.55%
| Station project attribute | Location (regional/distance factors) | Remote |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas | 100 percent |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 12.41% | 26.46% | 26.46% | 26.46% | 26.4% | 26.4% | 56% | 127.1% | -54.55%
Adjusted Baseline | [6 empty] | 26146566 | 27264776 | 4716958 | 2908580 | 2249920 | 1124960 | 4639138.452 | 40557.843 | 67412.9331 | 69158869.2281 | 68.56%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | High |  |  |  | 1% | 10% | 0% | 0% | 5% | 0% | 5% | 0% | 0%
| Station known risk | Outage restrictions | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 11% | 20% | 10% | 10% | 15% | 10% | 25% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 2876122.26 | 5452955.2 | 471695.8 | 290858 | 337488 | 112496 | 1159784.613 | 0 | 0 | 10701399.873 | 10.61%
Subtotal Including Known Risks | [6 empty] | 29022688.26 | 32717731.2 | 5188653.8 | 3199438 | 2587408 | 1237456 | 5798923.065 | 40557.843 | 67412.9331 | 79860269.1011 | 79.17%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 8366901.12 | 8724728.32 | 1509426.56 | 930745.6 | 719974.4 | 359987.2 | 371131.0762 | 9733.8823 | 16179.1039 | 21008807.2624 | 20.83%
Subtotal Including Unknown Risks | [6 empty] | 37389589.38 | 41442459.52 | 6698080.36 | 4130183.6 | 3307382.4 | 1597443.2 | 6170054.1412 | 50291.7253 | 83592.0371 | 100869076.3636 | 100%