## OutputA
Project Name: Ovens Murray (V1) REZ Connection Costs | [5 empty] | Indirect Cost Selection
Project Description: 250 MVA connection to 220 kV network including new connection substation, 275/132 kV transformer and 2 x 5 km feeders at 132 kV. Note that while there is a mismatch in voltage in the substation items, the most appropriate item available in the Transmission Cost Database has been selected. | [5 empty] | Total Network Elements Cost Category |  |  | Below $50 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | REZ Feeder | 7084149.2672 | 1728777.2737 | 1987585.8056 | 1017737.8938 | 0 | 284571.5709 | 0 | 470789.2232 | 285468.75 | 1309218.75
2 | REZ Connection Substation | 21002211.5827 | 6809954.9931 | 8947722.3194 | 1334779.1531 | 1562790.8572 | 776085.3966 | 308739.6485 | 1231764.2148 | 5437.5 | 24937.5
| Total Network Element Cost | 28086360.8499 | 8538732.2669 | 10935308.1249 | 2352517.0469 | 1562790.8572 | 1060656.9675 | 308739.6485 | 1702553.4379 | 290906.25 | 1334156.25
Indirect Costs
| Project Development | 1797527.09
| Works Delivery | 719010.84
| Land and Environment | 763949.02
| Stakeholder and Community Engagement | 494319.95
| Procurement Costs | 449381.77
| Insurance | 269629.06
| Total Indirect Cost | 4493817.74
| Total Expected Project Cost | 32580178.59

## OutputB
Project Name: Ovens Murray (V1) REZ Connection Costs |  |  |  |  | Indirect Cost Selection
Project Description: 250 MVA connection to 220 kV network including new connection substation, 275/132 kV transformer and 2 x 5 km feeders at 132 kV. Note that while there is a mismatch in voltage in the substation items, the most appropriate item available in the Transmission Cost Database has been selected. |  |  |  |  | Total Network Elements Cost Category |  |  | Below $50 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 21968340.575 | 6996535.955 | 8594540 | 1781795 | 1283568.5 | 833939.595 | 251326.6 | 1290384.925 | 133750 | 802500
Adjusted Baseline Cost | 23712840.8983 | 7318200.1535 | 9290258.8112 | 1981942.5804 | 1347233.4976 | 910201.4832 | 266154.8694 | 1635849.5031 | 200625 | 762375
Known Risk Allowance | 412846.2556 | 20467.0151 | 125755.2461 | 36641.5398 | 0 | 0 | 0 | 1269.9547 | 0 | 228712.5
Unknown Risk Allowance | 3960673.696 | 1200065.0983 | 1519294.0677 | 333932.9268 | 215557.3596 | 150455.4843 | 42584.7791 | 65433.9801 | 90281.25 | 343068.75
Total Network Element Cost | 28086360.8499 | 8538732.2669 | 10935308.1249 | 2352517.0469 | 1562790.8572 | 1060656.9675 | 308739.6485 | 1702553.4379 | 290906.25 | 1334156.25
Indirect Costs:
Project Development | 1797527.0944
Works Delivery | 719010.8378
Land and Environment | 763949.0151
Stakeholder and Community Engagement | 494319.951
Procurement Costs | 449381.7736
Insurance | 269629.0642
Total Indirect Cost | 4493817.736
Total Expected Project Cost | 32580178.5859

## OutputC
Project Name: Ovens Murray (V1) REZ Connection Costs
Project Description: 250 MVA connection to 220 kV network including new connection substation, 275/132 kV transformer and 2 x 5 km feeders at 132 kV. Note that while there is a mismatch in voltage in the substation items, the most appropriate item available in the Transmission Cost Database has been selected.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
|  | REZ Feeder | Feeder from Connection Substation to Generator Transformer
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 1 × Lemon DCST 250MVA | 132 | 5 | km | 1301708.955 | 1377075 | 705127.5 | 0 | 202174.595 | 0 | 369124.595 | 131250 | 787500 | 4873960.645 | 68.8%
TRUE | TRUE | Baseline Cost | [6 empty] | 1301708.955 | 1377075 | 705127.5 | 0 | 202174.595 | 0 | 369124.595 | 131250 | 787500 | 4873960.645 | 68.8%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Optimum | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 5 to 10 km | - | - | - | 0.0948 | 0.15784 | 0.15784 | 0 | 0.15784 | 0.15784 | 0.1896 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.1198 | 0.19284 | 0.19284 | 0 | 0.19284 | 0.19284 | 0.2246 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1457653.6878 | 1642632.8971 | 841105.6974 | 0 | 241162.3482 | 0 | 452029.979 | 196875 | 748125 | 5579584.6096 | 78.76%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 8745.9221 | 49278.9869 | 25233.1709 | 0 | 0 | 0 | 678.045 | 0 | 224437.5 | 308373.6249 | 4.353%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1466399.6099 | 1691911.8841 | 866338.8683 | 0 | 241162.3482 | 0 | 452708.024 | 196875 | 972562.5 | 5887958.2345 | 83.11%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 262377.6638 | 295673.9215 | 151399.0255 | 0 | 43409.2227 | 0 | 18081.1992 | 88593.75 | 336656.25 | 1196191.0327 | 16.89%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 1728777.2737 | 1987585.8056 | 1017737.8938 | 0 | 284571.5709 | 0 | 470789.2232 | 285468.75 | 1309218.75 | 7084149.2672 | 100%
Network Element 2
|  | REZ Connection Substation | Substation infrastructure, 275/132 kV transformer and 2 x AIS switchbays
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 142467 | 4986345 | 356167.5 | 783568.5 | 142467 | 142467 | 569868 | 2500 | 15000 | 7140850 | 34%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 132 | 1 | lot | 817780 | 604590 | 216750 | 300000 | 193912 | 38782.4 | 239675.23 | 0 | 0 | 2411489.63 | 11.48%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 1CB | 132 | 1 | lot | 283580 | 426530 | 93750 | 100000 | 90386 | 18077.2 | 111717.1 | 0 | 0 | 1124040.3 | 5.352%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3ph) 300MVA | 275/132 | 1 | ea. | 4451000 | 1200000 | 410000 | 100000 | 205000 | 52000 | 0 | 0 | 0 | 6418000 | 30.56%
TRUE | TRUE | Baseline Cost | [6 empty] | 5694827 | 7217465 | 1076667.5 | 1283568.5 | 631765 | 251326.6 | 921260.33 | 2500 | 15000 | 17094379.93 | 81.39%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Optimum | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0291 | 0.0596 | 0.0596 | 0.0496 | 0.059 | 0.059 | 0.285 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 5860546.4657 | 7647625.914 | 1140836.883 | 1347233.4976 | 669039.135 | 266154.8694 | 1183819.5241 | 3750 | 14250 | 18133256.2888 | 86.34%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 11721.0929 | 76476.2591 | 11408.3688 | 0 | 0 | 0 | 591.9098 | 0 | 4275 | 104472.6307 | 0.4974%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 5872267.5586 | 7724102.1731 | 1152245.2518 | 1347233.4976 | 669039.135 | 266154.8694 | 1184411.4338 | 3750 | 18525 | 18237728.9194 | 86.84%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 937687.4345 | 1223620.1462 | 182533.9013 | 215557.3596 | 107046.2616 | 42584.7791 | 47352.781 | 1687.5 | 6412.5 | 2764482.6633 | 13.16%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 6809954.9931 | 8947722.3194 | 1334779.1531 | 1562790.8572 | 776085.3966 | 308739.6485 | 1231764.2148 | 5437.5 | 24937.5 | 21002211.5827 | 100%