## OutputA
Project Name: VIC - SNSW Option 6 | [5 empty] | Indirect Cost Selection
Project Description: Project Description: Additional two 500 kV lines from north of Melbourne to near Shepparton and Wagga Wagga | [5 empty] | Total Network Elements Cost Category |  |  | Above $1500 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Substation: North of Melbourne | 74490435.289 | 19906949.5084 | 34241401.1684 | 5263527.9032 | 4912690.1162 | 3353838.7396 | 1195427.964 | 5423474.8892 | 43500 | 149625
2 | Substation: Near Shepparton | 172477097.9817 | 85455351.2833 | 52531934.7201 | 11126085.7718 | 7027269.1261 | 6966583.0343 | 2215237.436 | 6942011.6101 | 38062.5 | 174562.5
3 | OHL: North of Melbourne - Near Shepparton | 524424605.7143 | 140652114.7852 | 114734376.7221 | 142716628.9111 | 0 | 21057242.6263 | 0 | 25453322.6696 | 14287140 | 65523780
4 | OHL: Near Shepparton - Near Wagga Wagga | 810563362.8797 | 219807412.7877 | 171867387.2223 | 220473139.3364 | 0 | 33010671.1148 | 0 | 39870952.4185 | 22472100 | 103061700
5 | Substation: Near Wagga Wagga | 131624700.9786 | 64169559.871 | 41105392.4549 | 8548332.5339 | 5456149.3274 | 5213247.4716 | 1828739.2507 | 5102280.0692 | 43500 | 157500
| Total Network Element Cost | 1713580202.8433 | 529991388.2355 | 414480492.2879 | 388127714.4564 | 17396108.5696 | 69601582.9867 | 5239404.6506 | 82792041.6567 | 36884302.5 | 169067167.5
Indirect Costs
| Project Development | 44553085.27
| Works Delivery | 17821234.11
| Land and Environment | 18935061.24
| Stakeholder and Community Engagement | 12252098.45
| Procurement Costs | 11138271.32
| Insurance | 6682962.79
| Total Indirect Cost | 111382713.18
| Total Expected Project Cost | 1824962916.03

## OutputB
Project Name: VIC - SNSW Option 6 |  |  |  |  | Indirect Cost Selection
Project Description: Project Description: Additional two 500 kV lines from north of Melbourne to near Shepparton and Wagga Wagga |  |  |  |  | Total Network Elements Cost Category |  |  | Above $1500 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 1319868670.0862 | 440412290.1 | 314872937.8 | 300517971.7 | 13267151.5 | 55192236.3731 | 3917611 | 73050371.6131 | 16948300 | 101689800
Adjusted Baseline Cost | 1388325655.5681 | 449825385.2211 | 339756948.5469 | 318599901.5712 | 14996645.3186 | 59211360.0595 | 4461727.2884 | 79426427.5623 | 25437450 | 96609810
Known Risk Allowance | 59647579.0349 | 2115365.8719 | 15700468.1307 | 12596444.0444 | 0 | 0 | 63800.9961 | 188556.9918 | 0 | 28982943
Unknown Risk Allowance | 265606968.2404 | 78050637.1425 | 59023075.6103 | 56931368.8408 | 2399463.251 | 10390222.9272 | 713876.3661 | 3177057.1025 | 11446852.5 | 43474414.5
Total Network Element Cost | 1713580202.8433 | 529991388.2355 | 414480492.2879 | 388127714.4564 | 17396108.5696 | 69601582.9867 | 5239404.6506 | 82792041.6567 | 36884302.5 | 169067167.5
Indirect Costs:
Project Development | 44553085.2739
Works Delivery | 17821234.1096
Land and Environment | 18935061.2414
Stakeholder and Community Engagement | 12252098.4503
Procurement Costs | 11138271.3185
Insurance | 6682962.7911
Total Indirect Cost | 111382713.1848
Total Expected Project Cost | 1824962916.0281

## OutputC
Project Name: VIC - SNSW Option 6
Project Description: Project Description: Additional two 500 kV lines from north of Melbourne to near Shepparton and Wagga Wagga
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
|  | Substation: North of Melbourne | 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 30000 m2 footprint area and applicable control building | (blank) | 1 | lot | 455302 | 15935570 | 1138255 | 2504161 | 455302 | 455302 | 1821208 | 15000 | 90000 | 22870100 | 30.7%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 4604000 | 2970300 | 1092000 | 600000 | 926630 | 185326 | 1145314.68 | 0 | 0 | 11523570.68 | 15.47%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 2 | lot | 3094000 | 2620200 | 768000 | 400000 | 688220 | 137644 | 850639.92 | 0 | 0 | 8558703.92 | 11.49%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 1624000 | 1347600 | 429000 | 200000 | 360060 | 72012 | 445034.16 | 0 | 0 | 4477706.16 | 6.011%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 6978000 | 3000000 | 550000 | 200000 | 236000 | 80000 | 0 | 0 | 0 | 11044000 | 14.83%
TRUE | TRUE | Baseline Cost | [6 empty] | 16755302 | 25873670 | 3977255 | 3904161 | 2666212 | 930284 | 4262196.76 | 15000 | 90000 | 58474080.76 | 78.5%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 11 - 15 | - | - | - | 0.00246 | 0.01476 | 0.01476 | 0.01476 | 0.0144 | 0.0144 | 0.15 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02246 | 0.08476 | 0.08476 | 0.08476 | 0.0844 | 0.0844 | 0.22 | 1 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 17131626.0829 | 28066722.2692 | 4314367.1338 | 4235077.6864 | 2891240.2928 | 1008799.9696 | 5199880.0472 | 30000 | 85500 | 62963213.4819 | 84.53%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.06 | 0.06 | 0 | 0 | 0.025 | 0.003 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 34263.2522 | 1684003.3362 | 258862.028 | 0 | 0 | 25219.9992 | 15599.6401 | 0 | 25650 | 2043598.2557 | 2.743%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 17165889.3351 | 29750725.6054 | 4573229.1618 | 4235077.6864 | 2891240.2928 | 1034019.9688 | 5215479.6873 | 30000 | 111150 | 65006811.7376 | 87.27%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 2741060.1733 | 4490675.5631 | 690298.7414 | 677612.4298 | 462598.4468 | 161407.9951 | 207995.2019 | 13500 | 38475 | 9483623.5514 | 12.73%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 19906949.5084 | 34241401.1684 | 5263527.9032 | 4912690.1162 | 3353838.7396 | 1195427.964 | 5423474.8892 | 43500 | 149625 | 74490435.289 | 100%
Network Element 2
|  | Substation: Near Shepparton | 500/220 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 3 | lot | 6906000 | 4455450 | 1638000 | 900000 | 1389945 | 277989 | 1717972.02 | 0 | 0 | 17285356.02 | 10.02%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 4 | lot | 3248000 | 2695200 | 858000 | 400000 | 720120 | 144024 | 890068.32 | 0 | 0 | 8955412.32 | 5.192%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 4 | ea. | 13956000 | 6000000 | 1100000 | 400000 | 472000 | 160000 | 0 | 0 | 0 | 22088000 | 12.81%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1000MVA | 500/330 | 2 | ea. | 26774000 | 6000000 | 2462000 | 200000 | 1232000 | 308000 | 0 | 0 | 0 | 36976000 | 21.44%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 35000 m2 footprint area and applicable control building | (blank) | 1 | lot | 537969 | 18828915 | 1344922.5 | 2958829.5 | 537969 | 537969 | 2151876 | 17500 | 105000 | 27020950 | 15.67%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 220 | 1 | lot | 847300 | 634000 | 217350 | 200000 | 189865 | 37973 | 234673.14 | 0 | 0 | 2361161.14 | 1.369%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 220 | 1 | lot | 1259200 | 733500 | 309150 | 300000 | 260185 | 52037 | 321588.66 | 0 | 0 | 3235660.66 | 1.876%
TRUE | FALSE |  | Station | Reactive Plant | SVC ±200MVAr | 220 | 1 | ea. | 16681000 | 750000 | 563000 | 100000 | 563000 | 188000 | 0 | 0 | 0 | 18845000 | 10.93%
TRUE | TRUE | Baseline Cost | [6 empty] | 70209469 | 40097065 | 8492422.5 | 5458829.5 | 5365084 | 1705992 | 5316178.14 | 17500 | 105000 | 136767540.14 | 79.3%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 11 - 15 | - | - | - | 0.00246 | 0.01476 | 0.01476 | 0.01476 | 0.0144 | 0.0144 | 0.15 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04746 | 0.11976 | 0.11976 | 0.10976 | 0.1194 | 0.1194 | 0.255 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 73541610.3987 | 44899089.5044 | 9509475.0186 | 6057990.6259 | 6005675.0296 | 1909687.4448 | 6671803.5657 | 26250 | 99750 | 148721331.5878 | 86.23%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 147083.2208 | 448990.895 | 95094.7502 | 0 | 0 | 0 | 3335.9018 | 0 | 29925 | 724429.7678 | 0.42%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 73688693.6195 | 45348080.3994 | 9604569.7688 | 6057990.6259 | 6005675.0296 | 1909687.4448 | 6675139.4675 | 26250 | 129675 | 149445761.3556 | 86.65%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 11766657.6638 | 7183854.3207 | 1521516.003 | 969278.5001 | 960908.0047 | 305549.9912 | 266872.1426 | 11812.5 | 44887.5 | 23031336.6262 | 13.35%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 85455351.2833 | 52531934.7201 | 11126085.7718 | 7027269.1261 | 6966583.0343 | 2215237.436 | 6942011.6101 | 38062.5 | 174562.5 | 172477097.9817 | 100%
Network Element 3
|  | OHL: North of Melbourne - Near Shepparton | 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6080MVA | 500 | 154 | km | 114308155.5 | 84279252.75 | 108114237 | 0 | 16599114.41 | 0 | 22878572.21 | 6468000 | 38808000 | 391455331.87 | 74.64%
TRUE | FALSE |  | Overhead line | HVAC line diversion | Type 5 (4 × conductor/phase SCST) | 500 | 4 | lot | 2532917.1 | 2028532.8 | 1416139.2 | 0 | 314890.49 | 0 | 396441.89 | 100800 | 604800 | 7394521.48 | 1.41%
TRUE | TRUE | Baseline Cost | [6 empty] | 116841072.6 | 86307785.55 | 109530376.2 | 0 | 16914004.9 | 0 | 23275014.1 | 6568800 | 39412800 | 398849853.35 | 76.05%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.015 | 0.05505 | 0.05505 | 0 | 0.05505 | 0.05505 | 0.0475 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 118593688.689 | 91059029.1445 | 115560023.4098 | 0 | 17845120.8697 | 0 | 24380577.2698 | 9853200 | 37442160 | 414733799.3828 | 79.08%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.08 | 0.055 | 0 | 0 | 0.025 | 0.004 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 711562.1321 | 7284722.3316 | 6355801.2875 | 0 | 0 | 0 | 97522.3091 | 0 | 11232648 | 25682256.0603 | 4.897%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 119305250.8211 | 98343751.4761 | 121915824.6973 | 0 | 17845120.8697 | 0 | 24478099.5788 | 9853200 | 48674808 | 440416055.4431 | 83.98%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 21346863.964 | 16390625.246 | 20800804.2138 | 0 | 3212121.7566 | 0 | 975223.0908 | 4433940 | 16848972 | 84008550.2711 | 16.02%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 140652114.7852 | 114734376.7221 | 142716628.9111 | 0 | 21057242.6263 | 0 | 25453322.6696 | 14287140 | 65523780 | 524424605.7143 | 100%
Network Element 4
|  | OHL: Near Shepparton - Near Wagga Wagga | 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6080MVA | 500 | 246 | km | 182596144.5 | 134627897.25 | 172701963 | 0 | 26515468.4731 | 0 | 36546290.6731 | 10332000 | 61992000 | 625311763.8962 | 77.15%
TRUE | TRUE | Baseline Cost | [6 empty] | 182596144.5 | 134627897.25 | 172701963 | 0 | 26515468.4731 | 0 | 36546290.6731 | 10332000 | 61992000 | 625311763.8962 | 77.15%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.015 | 0.05505 | 0.05505 | 0 | 0.05505 | 0.05505 | 0.0475 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 185335086.6675 | 142039162.9936 | 182209206.0632 | 0 | 27975145.0126 | 0 | 38282239.4801 | 15498000 | 58892400 | 650231240.2169 | 80.22%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 1112010.52 | 4261174.8898 | 5466276.1819 | 0 | 0 | 0 | 57423.3592 | 0 | 17667720 | 28564604.9509 | 3.524%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 186447097.1875 | 146300337.8834 | 187675482.245 | 0 | 27975145.0126 | 0 | 38339662.8393 | 15498000 | 76560120 | 678795845.1678 | 83.74%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 33360315.6002 | 25567049.3389 | 32797657.0914 | 0 | 5035526.1023 | 0 | 1531289.5792 | 6974100 | 26501580 | 131767517.7118 | 16.26%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 219807412.7877 | 171867387.2223 | 220473139.3364 | 0 | 33010671.1148 | 0 | 39870952.4185 | 22472100 | 103061700 | 810563362.8797 | 100%
Network Element 5
|  | Substation: Near Wagga Wagga | 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 30000 m2 footprint area and applicable control building | (blank) | 1 | lot | 455302 | 15935570 | 1138255 | 2504161 | 455302 | 455302 | 1821208 | 15000 | 90000 | 22870100 | 17.38%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 1 | lot | 2302000 | 1485150 | 546000 | 300000 | 463315 | 92663 | 572657.34 | 0 | 0 | 5761785.34 | 4.377%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 1 | lot | 1547000 | 1310100 | 384000 | 200000 | 344110 | 68822 | 425319.96 | 0 | 0 | 4279351.96 | 3.251%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 1624000 | 1347600 | 429000 | 200000 | 360060 | 72012 | 445034.16 | 0 | 0 | 4477706.16 | 3.402%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 6978000 | 3000000 | 550000 | 200000 | 236000 | 80000 | 0 | 0 | 0 | 11044000 | 8.391%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 1 | ea. | 18338000 | 3000000 | 1687000 | 100000 | 844000 | 211000 | 0 | 0 | 0 | 24180000 | 18.37%
TRUE | FALSE |  | Station | Reactive Plant | SVC ±300MVAr | 330 | 1 | ea. | 21238000 | 955000 | 716000 | 100000 | 716000 | 239000 | 0 | 0 | 0 | 23964000 | 18.21%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 1 | lot | 1528000 | 933100 | 365700 | 300000 | 312680 | 62536 | 386472.48 | 0 | 0 | 3888488.48 | 2.954%
TRUE | TRUE | Baseline Cost | [6 empty] | 54010302 | 27966520 | 5815955 | 3904161 | 3731467 | 1281335 | 3650691.94 | 15000 | 90000 | 100465431.94 | 76.33%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 11 - 15 | - | - | - | 0.00246 | 0.01476 | 0.01476 | 0.01476 | 0.0144 | 0.0144 | 0.15 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02246 | 0.20476 | 0.20476 | 0.20476 | 0.2044 | 0.2044 | 0.34 | 1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 55223373.3829 | 33692944.6352 | 7006829.9458 | 4703577.0064 | 4494178.8548 | 1543239.874 | 4891927.1996 | 30000 | 90000 | 111676070.8987 | 84.84%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.06 | 0.06 | 0 | 0 | 0.025 | 0.003 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 110446.7468 | 2021576.6781 | 420409.7967 | 0 | 0 | 38580.9968 | 14675.7816 | 0 | 27000 | 2632690.0001 | 2%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 55333820.1297 | 35714521.3133 | 7427239.7425 | 4703577.0064 | 4494178.8548 | 1581820.8708 | 4906602.9812 | 30000 | 117000 | 114308760.8988 | 86.84%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 8835739.7413 | 5390871.1416 | 1121092.7913 | 752572.321 | 719068.6168 | 246918.3798 | 195677.088 | 13500 | 40500 | 17315940.0798 | 13.16%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 64169559.871 | 41105392.4549 | 8548332.5339 | 5456149.3274 | 5213247.4716 | 1828739.2507 | 5102280.0692 | 43500 | 157500 | 131624700.9786 | 100%