## OutputA
Project Name: Q2 Option 2 | [5 empty] | Indirect Cost Selection
Project Description: Additional single 275kV circuit option | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | 275kV Substation | 12014729.7236 | 5644426.4341 | 3168030.4016 | 936638.8668 | 663868 | 690218.3837 | 154786.6527 | 756760.9846 | 0 | 0
2 | 275kV Circuit | 351938890.0407 | 108889971.0591 | 99731864.606 | 36921512.1634 | 0 | 13564351.8867 | 0 | 21020637.2255 | 10294098.1 | 61516455
3 | 275kV Substation | 8735143.1603 | 4443500.5728 | 2310375.3028 | 639307.3284 | 419200.8 | 425371.2854 | 102680.2731 | 394707.5977 | 0 | 0
| Total Network Element Cost | 372688762.9245 | 118977898.0661 | 105210270.3105 | 38497458.3586 | 1083068.8 | 14679941.5558 | 257466.9258 | 22172105.8078 | 10294098.1 | 61516455
Indirect Costs
| Project Development | 14907550.52
| Works Delivery | 5963020.21
| Land and Environment | 6335708.97
| Stakeholder and Community Engagement | 4099576.39
| Procurement Costs | 3726887.63
| Insurance | 2236132.58
| Total Indirect Cost | 37268876.29
| Total Expected Project Cost | 409957639.22

## OutputB
Project Name: Q2 Option 2 |  |  |  |  | Indirect Cost Selection
Project Description: Additional single 275kV circuit option |  |  |  |  | Total Network Elements Cost Category |  |  | $100-$500 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 261016512.51 | 80376136.84 | 74991865 | 27438467.6 | 800000 | 10677909.02 | 186954.6 | 18296979.45 | 6892600 | 41355600
Adjusted Baseline Cost | 296614239.3118 | 100494312.4468 | 87105426.638 | 31860608.976 | 933680 | 12456928.6953 | 221954.2464 | 21289690.3093 | 7099378 | 35152260
Known Risk Allowance | 14593139.5347 | 568239.792 | 2519514.8384 | 928879.0181 | 0 | 0 | 0 | 30827.8862 | 0 | 10545678
Unknown Risk Allowance | 61481384.0781 | 17915345.8272 | 15585328.8341 | 5707970.3645 | 149388.8 | 2223012.8605 | 35512.6794 | 851587.6124 | 3194720.1 | 15818517
Total Network Element Cost | 372688762.9245 | 118977898.0661 | 105210270.3105 | 38497458.3586 | 1083068.8 | 14679941.5558 | 257466.9258 | 22172105.8078 | 10294098.1 | 61516455
Indirect Costs:
Project Development | 14907550.517
Works Delivery | 5963020.2068
Land and Environment | 6335708.9697
Stakeholder and Community Engagement | 4099576.3922
Procurement Costs | 3726887.6292
Insurance | 2236132.5775
Total Indirect Cost | 37268876.2925
Total Expected Project Cost | 409957639.217

## OutputC
Project Name: Q2 Option 2
Project Description: Additional single 275kV circuit option
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
|  | 275kV Substation | 275kV Kidston Substation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 2 | lot | 1924400 | 1425020 | 482400 | 400000 | 423182 | 84636.4 | 523052.95 | 0 | 0 | 5262691.35 | 43.8%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 275 | 1 | ea. | 2598000 | 900000 | 205000 | 100000 | 88000 | 30000 | 0 | 0 | 0 | 3921000 | 32.63%
TRUE | TRUE | Baseline Cost | [6 empty] | 4522400 | 2325020 | 687400 | 500000 | 511182 | 114636.4 | 523052.95 | 0 | 0 | 9183691.35 | 76.44%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | QLD | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.15
FALSE | FALSE |  | Station project attribute | Land Use | Desert | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0741 | 0.1646 | 0.1646 | 0.1446 | 0.164 | 0.164 | 0.3905 | 0.03 | -0.15
TRUE | TRUE | Adjusted Baseline | [6 empty] | 4857509.84 | 2707718.292 | 800546.04 | 572300 | 595015.848 | 133436.7696 | 727305.127 | 0 | 0 | 10393831.9166 | 86.51%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 9715.0197 | 27077.1829 | 8005.4604 | 0 | 0 | 0 | 363.6526 | 0 | 0 | 45161.3156 | 0.3759%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 4867224.8597 | 2734795.4749 | 808551.5004 | 572300 | 595015.848 | 133436.7696 | 727668.7795 | 0 | 0 | 10438993.2321 | 86.88%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 777201.5744 | 433234.9267 | 128087.3664 | 91568 | 95202.5357 | 21349.8831 | 29092.2051 | 0 | 0 | 1575736.4914 | 13.12%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 5644426.4341 | 3168030.4016 | 936638.8668 | 663868 | 690218.3837 | 154786.6527 | 756760.9846 | 0 | 0 | 12014729.7236 | 100%
Network Element 2
|  | 275kV Circuit | 275kV Kidston - Mt. Fox circuit
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 × Orange SCST 800MVA | 275 | 190 | km | 71366694.44 | 70323275 | 25249290 | 0 | 9708859.22 | 0 | 17191059.22 | 6792500 | 40755000 | 241386677.88 | 68.59%
TRUE | FALSE |  | Overhead line | HVAC line diversion | Type 3 (2 × conductor/phase DCST) | 275 | 4 | lot | 926842.4 | 731060 | 1055577.6 | 0 | 158276.8 | 0 | 321340.8 | 100100 | 600600 | 3893797.6 | 1.106%
TRUE | TRUE | Baseline Cost | [6 empty] | 72293536.84 | 71054335 | 26304867.6 | 0 | 9867136.02 | 0 | 17512400.02 | 6892600 | 41355600 | 245280475.48 | 69.69%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | QLD | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.15
FALSE | FALSE |  | Overhead line project attribute | Land Use | Desert | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Cyclone region | - | - | - | 0.2 | 0.02 | 0.02 | 0 | 0.025 | 0.01 | 0.01 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.27 | 0.16 | 0.16 | 0 | 0.165 | 0.15 | 0.1525 | 0.03 | -0.15
TRUE | TRUE | Adjusted Baseline | [6 empty] | 91812791.7868 | 82423028.6 | 30513646.416 | 0 | 11495213.4633 | 0 | 20183041.023 | 7099378 | 35152260 | 278679359.2891 | 79.18%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 550876.7507 | 2472690.858 | 915409.3925 | 0 | 0 | 0 | 30274.5615 | 0 | 10545678 | 14514929.5627 | 4.124%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 92363668.5375 | 84895719.458 | 31429055.8085 | 0 | 11495213.4633 | 0 | 20213315.5846 | 7099378 | 45697938 | 293194288.8519 | 83.31%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 16526302.5216 | 14836145.148 | 5492456.3549 | 0 | 2069138.4234 | 0 | 807321.6409 | 3194720.1 | 15818517 | 58744601.1888 | 16.69%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 108889971.0591 | 99731864.606 | 36921512.1634 | 0 | 13564351.8867 | 0 | 21020637.2255 | 10294098.1 | 61516455 | 351938890.0407 | 100%
Network Element 3
|  | 275kV Substation | 275kV Mt. Fox Substation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 1 | lot | 962200 | 712510 | 241200 | 200000 | 211591 | 42318.2 | 261526.48 | 0 | 0 | 2631345.68 | 30.12%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 275 | 1 | ea. | 2598000 | 900000 | 205000 | 100000 | 88000 | 30000 | 0 | 0 | 0 | 3921000 | 44.89%
TRUE | TRUE | Baseline Cost | [6 empty] | 3560200 | 1612510 | 446200 | 300000 | 299591 | 72318.2 | 261526.48 | 0 | 0 | 6552345.68 | 75.01%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Partly brownfield | - | - | - | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | QLD | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.15
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0741 | 0.2246 | 0.2246 | 0.2046 | 0.224 | 0.224 | 0.4505 | 0.2 | -0.15
TRUE | TRUE | Adjusted Baseline | [6 empty] | 3824010.82 | 1974679.746 | 546416.52 | 361380 | 366699.384 | 88517.4768 | 379344.1592 | 0 | 0 | 7541048.106 | 86.33%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 7648.0216 | 19746.7975 | 5464.1652 | 0 | 0 | 0 | 189.6721 | 0 | 0 | 33048.6564 | 0.3783%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 3831658.8416 | 1994426.5435 | 551880.6852 | 361380 | 366699.384 | 88517.4768 | 379533.8313 | 0 | 0 | 7574096.7624 | 86.71%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 611841.7312 | 315948.7594 | 87426.6432 | 57820.8 | 58671.9014 | 14162.7963 | 15173.7664 | 0 | 0 | 1161046.3979 | 13.29%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 4443500.5728 | 2310375.3028 | 639307.3284 | 419200.8 | 425371.2854 | 102680.2731 | 394707.5977 | 0 | 0 | 8735143.1603 | 100%