## OutputA
Project Name: REZ V1, Option3 | [5 empty] | Indirect Cost Selection
Project Description: South Morang-Dederang-Murray 330 kV Single circuit line. This option also includes uprating the Murray-Upper and Lower Tumut lines which has been costed separately. | [5 empty] | Total Network Elements Cost Category |  |  | $500-$1000 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | South Morang to Dederang Overhead line | 505133336.2232 | 130456518.0577 | 133376159.3489 | 67798725.6989 | 0 | 18010646.1013 | 0 | 29681862.0166 | 22912312.5 | 102897112.5
2 | South Morang Terminal Station | 51696877.1565 | 21201070.1142 | 18539957.1728 | 3852176.7865 | 2780986.4328 | 2116225.4666 | 722879.3853 | 2402956.7983 | 16500 | 64125
3 | Dederang Terminal Station | 90820454.0753 | 43881331.6539 | 28332321.7466 | 5403494.9308 | 4447606.0776 | 3560094.5068 | 1284169.0976 | 3789936.062 | 21750 | 99750
4 | Murray Substation | 21778753.7215 | 4931443.1586 | 10987472.3202 | 1448988.4342 | 1695140.8925 | 831334.7749 | 354403.3714 | 1498283.2697 | 5437.5 | 26250
5 | Dederang to Murray Overhead line | 266933955.4402 | 67743212.4089 | 75528483.5381 | 38393180.3318 | 0 | 9396858.8395 | 0 | 17187720.3219 | 10505250 | 48179250
6 | Rowville-Thomastown 220 kV Line diversion at South Morang | 3244250.9949 | 983504.0204 | 956229.12 | 554699.8195 | 0 | 134720.6661 | 0 | 162667.3689 | 57420 | 395010
| Total Network Element Cost | 939607627.6115 | 269197079.4137 | 267720623.2465 | 117451266.0018 | 8923733.4028 | 34049880.3551 | 2361451.8543 | 54723425.8373 | 33518670 | 151661497.5
Indirect Costs
| Project Development | 30067444.08
| Works Delivery | 12026977.63
| Land and Environment | 12778663.74
| Stakeholder and Community Engagement | 8268547.12
| Procurement Costs | 7516861.02
| Insurance | 4510116.61
| Total Indirect Cost | 75168610.21
| Total Expected Project Cost | 1014776237.82

## OutputB
Project Name: REZ V1, Option3 |  |  |  |  | Indirect Cost Selection
Project Description: South Morang-Dederang-Murray 330 kV Single circuit line. This option also includes uprating the Murray-Upper and Lower Tumut lines which has been costed separately. |  |  |  |  | Total Network Elements Cost Category |  |  | $500-$1000 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 635137953.28 | 211320382.28 | 174335890 | 76502192.1 | 6142929.5 | 25173022.59 | 1583948 | 41067388.81 | 14144600 | 84867600
Adjusted Baseline Cost | 700601201.5917 | 215949275.8955 | 206732647.4685 | 90122446.8423 | 7538202.5201 | 27358506.4431 | 1954207.7316 | 49121344.6908 | 21199600 | 80624970
Known Risk Allowance | 94862050.73 | 15557938.1037 | 24703738.8029 | 11277926.3801 | 179418.4795 | 1876689.7191 | 94570.8856 | 3637227.3589 | 2779250 | 34755291
Unknown Risk Allowance | 144144375.2898 | 37689865.4144 | 36284236.9751 | 16050892.7794 | 1206112.4032 | 4814684.193 | 312673.2371 | 1964853.7876 | 9539820 | 36281236.5
Total Network Element Cost | 939607627.6115 | 269197079.4137 | 267720623.2465 | 117451266.0018 | 8923733.4028 | 34049880.3551 | 2361451.8543 | 54723425.8373 | 33518670 | 151661497.5
Indirect Costs:
Project Development | 30067444.0836
Works Delivery | 12026977.6334
Land and Environment | 12778663.7355
Stakeholder and Community Engagement | 8268547.123
Procurement Costs | 7516861.0209
Insurance | 4510116.6125
Total Indirect Cost | 75168610.2089
Total Expected Project Cost | 1014776237.8204

## OutputC
Project Name: REZ V1, Option3
Project Description: South Morang-Dederang-Murray 330 kV Single circuit line. This option also includes uprating the Murray-Upper and Lower Tumut lines which has been costed separately.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
|  | South Morang to Dederang Overhead line | 330 kV Single circuit line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 3 × Mango SCST 1200MVA | 330 | 230 | km | 101044488.38 | 89414225 | 45451680 | 0 | 13548328.11 | 0 | 23546428.11 | 9257500 | 55545000 | 337807649.6 | 66.87%
TRUE | TRUE | Baseline Cost | [6 empty] | 101044488.38 | 89414225 | 45451680 | 0 | 13548328.11 | 0 | 23546428.11 | 9257500 | 55545000 | 337807649.6 | 66.87%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.015 | 0.13005 | 0.13005 | 0 | 0.05505 | 0.05505 | 0.1225 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 102560155.7057 | 101042544.9613 | 51362670.984 | 0 | 14294163.5725 | 0 | 26430865.5535 | 13886250 | 52767750 | 362344400.7769 | 71.73%
FALSE | FALSE | Known Risks: | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | High |  |  |  | 0.012 | 0.06 | 0.06 | 0 | 0 | 0 | 0.003 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Overhead line known risk | Project complexity | Highly complex |  |  |  | 0.08 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0.08 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.092 | 0.14 | 0.14 | 0 | 0.08 | 0.08 | 0.083 | 0.2 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 9435534.3249 | 14145956.2946 | 7190773.9378 | 0 | 1143533.0858 | 0 | 2193761.8409 | 2777250 | 26383875 | 63270684.484 | 12.53%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 111995690.0306 | 115188501.2558 | 58553444.9218 | 0 | 15437696.6583 | 0 | 28624627.3944 | 16663500 | 79151625 | 425615085.2609 | 84.26%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 18460828.027 | 18187658.093 | 9245280.7771 | 0 | 2572949.443 | 0 | 1057234.6221 | 6248812.5 | 23745487.5 | 79518250.9624 | 15.74%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 130456518.0577 | 133376159.3489 | 67798725.6989 | 0 | 18010646.1013 | 0 | 29681862.0166 | 22912312.5 | 102897112.5 | 505133336.2232 | 100%
Network Element 2
|  | South Morang Terminal Station | 330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 1 | lot | 1528000 | 933100 | 365700 | 300000 | 312680 | 62536 | 386472.48 | 0 | 0 | 3888488.48 | 7.522%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 1 | lot | 543000 | 425200 | 153750 | 100000 | 122195 | 24439 | 151033.02 | 0 | 0 | 1519617.02 | 2.939%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 220 | 1 | lot | 847300 | 634000 | 217350 | 200000 | 189865 | 37973 | 234673.14 | 0 | 0 | 2361161.14 | 4.567%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 50MVAr | 330 | 1 | ea. | 2325000 | 1000000 | 183000 | 100000 | 79000 | 27000 | 0 | 0 | 0 | 3714000 | 7.184%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 600MVA | 330/220 | 1 | ea. | 11220000 | 2000000 | 1032000 | 100000 | 516000 | 129000 | 0 | 0 | 0 | 14997000 | 29.01%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 10000 m2 footprint area and applicable control building | N/A | 1 | lot | 191634 | 6707190 | 479085 | 1053987 | 191634 | 191634 | 766536 | 5000 | 30000 | 9616700 | 18.6%
TRUE | TRUE | Baseline Cost | [6 empty] | 16654934 | 11699490 | 2430885 | 1853987 | 1411374 | 472582 | 1538714.64 | 5000 | 30000 | 36096966.64 | 69.82%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.39 | 1 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 17042660.8635 | 14152639.0632 | 2940592.9668 | 2242730.9942 | 1706633.4408 | 571446.1544 | 2138813.3496 | 10000 | 28500 | 40834016.8325 | 78.99%
FALSE | FALSE | Known Risks: | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | High |  |  |  | 0.004 | 0.02 | 0.02 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Station known risk | Project complexity | Highly complex |  |  |  | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.084 | 0.15 | 0.15 | 0.08 | 0.08 | 0.105 | 0.0835 | 0.2 | 0.8
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 1431583.5125 | 2122895.8595 | 441088.945 | 179418.4795 | 136530.6753 | 60001.8462 | 178590.9147 | 2000 | 22800 | 4574910.2327 | 8.849%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 18474244.3761 | 16275534.9227 | 3381681.9118 | 2422149.4737 | 1843164.1161 | 631448.0006 | 2317404.2643 | 12000 | 51300 | 45408927.0652 | 87.84%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 2726825.7382 | 2264422.2501 | 470494.8747 | 358836.9591 | 273061.3505 | 91431.3847 | 85552.534 | 4500 | 12825 | 6287950.0912 | 12.16%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 21201070.1142 | 18539957.1728 | 3852176.7865 | 2780986.4328 | 2116225.4666 | 722879.3853 | 2402956.7983 | 16500 | 64125 | 51696877.1565 | 100%
Network Element 3
|  | Dederang Terminal Station | 330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Reactive Plant | SVC ±300MVAr | 330 | 1 | ea. | 21238000 | 955000 | 716000 | 100000 | 716000 | 239000 | 0 | 0 | 0 | 23964000 | 26.39%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 2 | lot | 3056000 | 1866200 | 731400 | 600000 | 625360 | 125072 | 772944.96 | 0 | 0 | 7776976.96 | 8.563%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 220 | 1 | lot | 847300 | 634000 | 217350 | 200000 | 189865 | 37973 | 234673.14 | 0 | 0 | 2361161.14 | 2.6%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3ph) 400MVA | 330/220 | 1 | ea. | 4837000 | 1500000 | 445000 | 100000 | 223000 | 56000 | 0 | 0 | 0 | 7161000 | 7.885%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 2 | lot | 1086000 | 850400 | 307500 | 200000 | 244390 | 48878 | 302066.04 | 0 | 0 | 3039234.04 | 3.346%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 50MVAr | 330 | 2 | ea. | 4650000 | 2000000 | 366000 | 200000 | 158000 | 54000 | 0 | 0 | 0 | 7428000 | 8.179%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | N/A | 1 | lot | 310068 | 10852380 | 775170 | 1705374 | 310068 | 310068 | 1240272 | 10000 | 60000 | 15573400 | 17.15%
TRUE | TRUE | Baseline Cost | [6 empty] | 36024368 | 18657980 | 3558420 | 3105374 | 2466683 | 870991 | 2549956.14 | 10000 | 60000 | 67303772.14 | 74.11%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04828 | 0.24468 | 0.24468 | 0.23468 | 0.2442 | 0.2442 | 0.425 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 37763624.487 | 23223214.5464 | 4429094.2056 | 3834143.1703 | 3069046.9886 | 1083687.0022 | 3633687.4995 | 15000 | 57000 | 77108497.8997 | 84.9%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.06 | 0.06 | 0 | 0 | 0.025 | 0.003 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 75527.249 | 1393392.8728 | 265745.6523 | 0 | 0 | 27092.1751 | 10901.0625 | 0 | 17100 | 1789759.0116 | 1.971%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 37839151.736 | 24616607.4192 | 4694839.8579 | 3834143.1703 | 3069046.9886 | 1110779.1773 | 3644588.562 | 15000 | 74100 | 78898256.9113 | 86.87%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 6042179.9179 | 3715714.3274 | 708655.0729 | 613462.9073 | 491047.5182 | 173389.9204 | 145347.5 | 6750 | 25650 | 11922197.164 | 13.13%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 43881331.6539 | 28332321.7466 | 5403494.9308 | 4447606.0776 | 3560094.5068 | 1284169.0976 | 3789936.062 | 21750 | 99750 | 90820454.0753 | 100%
Network Element 4
|  | Murray Substation | 330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 1 | lot | 543000 | 425200 | 153750 | 100000 | 122195 | 24439 | 151033.02 | 0 | 0 | 1519617.02 | 6.978%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 142467 | 4986345 | 356167.5 | 783568.5 | 142467 | 142467 | 569868 | 2500 | 15000 | 7140850 | 32.79%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 50MVAr | 330 | 1 | ea. | 2325000 | 1000000 | 183000 | 100000 | 79000 | 27000 | 0 | 0 | 0 | 3714000 | 17.05%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 1038000 | 824150 | 261300 | 200000 | 232345 | 46469 | 287178.42 | 0 | 0 | 2889442.42 | 13.27%
TRUE | TRUE | Baseline Cost | [6 empty] | 4048467 | 7235695 | 954217.5 | 1183568.5 | 576007 | 240375 | 1008079.44 | 2500 | 15000 | 15263909.44 | 70.09%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04828 | 0.24468 | 0.24468 | 0.23468 | 0.2442 | 0.2442 | 0.425 | 0.5 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 4243926.9868 | 9006124.8526 | 1187695.4379 | 1461328.3556 | 716667.9094 | 299074.575 | 1436513.202 | 3750 | 15000 | 18370081.3192 | 84.35%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.06 | 0.06 | 0 | 0 | 0.025 | 0.003 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 8487.854 | 540367.4912 | 71261.7263 | 0 | 0 | 7476.8644 | 4309.5396 | 0 | 4500 | 636403.4754 | 2.922%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 4252414.8407 | 9546492.3438 | 1258957.1642 | 1461328.3556 | 716667.9094 | 306551.4394 | 1440822.7416 | 3750 | 19500 | 19006484.7946 | 87.27%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 679028.3179 | 1440979.9764 | 190031.2701 | 233812.5369 | 114666.8655 | 47851.932 | 57460.5281 | 1687.5 | 6750 | 2772268.9268 | 12.73%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 4931443.1586 | 10987472.3202 | 1448988.4342 | 1695140.8925 | 831334.7749 | 354403.3714 | 1498283.2697 | 5437.5 | 26250 | 21778753.7215 | 100%
Network Element 5
|  | Dederang to Murray Overhead line | 330 kV Single circuit line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 3 × Mango SCST 1200MVA | 330 | 120 | km | 52718863.5 | 46650900 | 23713920 | 0 | 7068692.93 | 0 | 12285092.93 | 4830000 | 28980000 | 176247469.36 | 66.03%
TRUE | TRUE | Baseline Cost | [6 empty] | 52718863.5 | 46650900 | 23713920 | 0 | 7068692.93 | 0 | 12285092.93 | 4830000 | 28980000 | 176247469.36 | 66.03%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Mountainous | - | - | - | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0.2 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.015 | 0.25505 | 0.25505 | 0 | 0.05505 | 0.05505 | 0.2475 | 0.5 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 53509646.4525 | 58549212.045 | 29762155.296 | 0 | 7457824.4758 | 0 | 15325653.4302 | 7245000 | 27531000 | 199380491.6995 | 74.69%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Highly complex |  |  |  | 0.08 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0.08 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.086 | 0.11 | 0.11 | 0 | 0.08 | 0.08 | 0.0815 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 4601829.5949 | 6440413.325 | 3273837.0826 | 0 | 596625.9581 | 0 | 1249040.7546 | 0 | 8259300 | 24421046.715 | 9.149%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 58111476.0474 | 64989625.37 | 33035992.3786 | 0 | 8054450.4339 | 0 | 16574694.1847 | 7245000 | 35790300 | 223801538.4145 | 83.84%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 9631736.3614 | 10538858.1681 | 5357187.9533 | 0 | 1342408.4056 | 0 | 613026.1372 | 3260250 | 12388950 | 43132417.0257 | 16.16%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 67743212.4089 | 75528483.5381 | 38393180.3318 | 0 | 9396858.8395 | 0 | 17187720.3219 | 10505250 | 48179250 | 266933955.4402 | 100%
Network Element 6
|  | Rowville-Thomastown 220 kV Line diversion at South Morang | 220 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 5 (3 × conductor/phase SCST) | 220 | 2 | lot | 829261.4 | 677600 | 393069.6 | 0 | 101937.55 | 0 | 139117.55 | 39600 | 237600 | 2418186.1 | 74.54%
TRUE | TRUE | Baseline Cost | [6 empty] | 829261.4 | 677600 | 393069.6 | 0 | 101937.55 | 0 | 139117.55 | 39600 | 237600 | 2418186.1 | 74.54%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 829261.4 | 758912 | 440237.952 | 0 | 114170.056 | 0 | 155811.656 | 39600 | 225720 | 2563713.064 | 79.02%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.08 | 0.08 | 0 | 0 | 0.025 | 0.004 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 4975.5684 | 60712.96 | 35219.0362 | 0 | 0 | 0 | 623.2466 | 0 | 67716 | 169246.8112 | 5.217%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 834236.9684 | 819624.96 | 475456.9882 | 0 | 114170.056 | 0 | 156434.9026 | 39600 | 293436 | 2732959.8752 | 84.24%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 149267.052 | 136604.16 | 79242.8314 | 0 | 20550.6101 | 0 | 6232.4662 | 17820 | 101574 | 511291.1197 | 15.76%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 983504.0204 | 956229.12 | 554699.8195 | 0 | 134720.6661 | 0 | 162667.3689 | 57420 | 395010 | 3244250.9949 | 100%