## OutputA
Project Name: V3 Option 3 (500 kV cost) | [5 empty] | Indirect Cost Selection
Project Description: Convert the new north of Ballarat-Bulgana line (part of West VIC RIT-T) from 220kV to 500kV. This estimate includes the 500kV line cost. The 220kV cost will need to be deducted to determine the overall project cost given the option is upgrading from 220kV to 500kV. | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | OHL1: north of Ballarat - Bulgana 500 kV | 349588541.7648 | 94753377.6899 | 75367624.7704 | 96682314.8041 | 0 | 14475904.4369 | 0 | 17630230.0635 | 7527240 | 43151850
2 | SS1: Bulgana 500kV | 37393783.4826 | 7980051.9177 | 17050156.3627 | 2835498.6653 | 3066647.523 | 2034998.52 | 666309.4717 | 3672258.5221 | 13050 | 74812.5
| Total Network Element Cost | 386982325.2474 | 102733429.6076 | 92417781.1331 | 99517813.4693 | 3066647.523 | 16510902.9569 | 666309.4717 | 21302488.5857 | 7540290 | 43226662.5
Indirect Costs
| Project Development | 15479293.01
| Works Delivery | 6191717.2
| Land and Environment | 6578699.53
| Stakeholder and Community Engagement | 4256805.58
| Procurement Costs | 3869823.25
| Insurance | 2321893.95
| Total Indirect Cost | 38698232.52
| Total Expected Project Cost | 425680557.77

## OutputB
Project Name: V3 Option 3 (500 kV cost) |  |  |  |  | Indirect Cost Selection
Project Description: Convert the new north of Ballarat-Bulgana line (part of West VIC RIT-T) from 220kV to 500kV. This estimate includes the 500kV line cost. The 220kV cost will need to be deducted to determine the overall project cost given the project is upgrading from 220kV to 500kV. |  |  |  |  | Total Network Elements Cost Category |  |  | $100-$500 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 290490970.11 | 82998958.25 | 69269426.13 | 74455623.99 | 2361255.5 | 12655866.09 | 508773 | 17906567.15 | 4333500 | 26001000
Adjusted Baseline Cost | 313545360.8269 | 86760750.3854 | 76860076.4147 | 82326242.6402 | 2643661.6578 | 14022024.6935 | 574404.717 | 20457050.3185 | 5200200 | 24700950
Known Risk Allowance | 12366199.5432 | 493094.4441 | 2014346.6281 | 2421317.2166 | 0 | 0 | 0 | 27156.2545 | 0 | 7410285
Unknown Risk Allowance | 61070764.8772 | 15479584.7782 | 13543358.0903 | 14770253.6126 | 422985.8652 | 2488878.2634 | 91904.7547 | 818282.0127 | 2340090 | 11115427.5
Total Network Element Cost | 386982325.2474 | 102733429.6076 | 92417781.1331 | 99517813.4693 | 3066647.523 | 16510902.9569 | 666309.4717 | 21302488.5857 | 7540290 | 43226662.5
Indirect Costs:
Project Development | 15479293.0099
Works Delivery | 6191717.204
Land and Environment | 6578699.5292
Stakeholder and Community Engagement | 4256805.5777
Procurement Costs | 3869823.2525
Insurance | 2321893.9515
Total Indirect Cost | 38698232.5247
Total Expected Project Cost | 425680557.7721

## OutputC
Project Name: V3 Option 3 (500 kV cost)
Project Description: Convert the new north of Ballarat-Bulgana line (part of West VIC RIT-T) from 220kV to 500kV. This estimate includes the 500kV line cost. The 220kV cost will need to be deducted to determine the overall project cost given the project is upgrading from 220kV to 500kV.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5 project cost estimates (+/- 30%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
Network Element 1
OHL1: north of Ballarat - Bulgana 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6080MVA | 500 | 103 | km | 76452857.25 | 56368591.13 | 72310171.5 | 0 | 11102005.09 | 0 | 15301902.19 | 4326000 | 25956000 | 261817527.16 | 74.89%
TRUE | TRUE | Baseline Cost | [6 empty] | 76452857.25 | 56368591.13 | 72310171.5 | 0 | 11102005.09 | 0 | 15301902.19 | 4326000 | 25956000 | 261817527.16 | 74.89%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.00125 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Flat/Farmland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.105 | 0.105 | 0 | 0.105 | 0.105 | 0.10625 | 0.2 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 79893235.8263 | 62287293.1987 | 79902739.5075 | 0 | 12267715.6245 | 0 | 16927729.2977 | 5191200 | 24658200 | 281128113.4545 | 80.42%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 479359.415 | 1868618.796 | 2397082.1852 | 0 | 0 | 0 | 25391.5939 | 0 | 7397460 | 12167911.9901 | 3.481%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 80372595.2412 | 64155911.9946 | 82299821.6927 | 0 | 12267715.6245 | 0 | 16953120.8916 | 5191200 | 32055660 | 293296025.4446 | 83.9%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 14380782.4487 | 11211712.7758 | 14382493.1113 | 0 | 2208188.8124 | 0 | 677109.1719 | 2336040 | 11096190 | 56292516.3201 | 16.1%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 94753377.6899 | 75367624.7704 | 96682314.8041 | 0 | 14475904.4369 | 0 | 17630230.0635 | 7527240 | 43151850 | 349588541.7648 | 100%
Network Element 2
SS1: Bulgana 500kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 4604000 | 2970300 | 1092000 | 600000 | 926630 | 185326 | 1145314.68 | 0 | 0 | 11523570.68 | 30.82%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 220 | 2 | lot | 1694600 | 1268000 | 434699.99 | 400000 | 379730 | 75946 | 469346.28 | 0 | 0 | 4722322.27 | 12.63%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 15000 m2 footprint area and applicable control building | N/A | 1 | lot | 247501 | 8662535 | 618752.5 | 1361255.5 | 247501 | 247501 | 990004 | 7500 | 45000 | 12427550 | 33.23%
TRUE | TRUE | Baseline Cost | [6 empty] | 6546101 | 12900835 | 2145452.49 | 2361255.5 | 1553861 | 508773 | 2604664.96 | 7500 | 45000 | 28673442.95 | 76.68%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0491 | 0.1296 | 0.1296 | 0.1196 | 0.129 | 0.129 | 0.355 | 0.2 | -0.05
TRUE | TRUE | Adjusted Baseline | [6 empty] | 6867514.5591 | 14572783.216 | 2423503.1327 | 2643661.6578 | 1754309.069 | 574404.717 | 3529321.0208 | 9000 | 42750 | 32417247.3724 | 86.69%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0.3
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 13735.0291 | 145727.8322 | 24235.0313 | 0 | 0 | 0 | 1764.6605 | 0 | 12825 | 198287.5531 | 0.5303%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 6881249.5882 | 14718511.0482 | 2447738.164 | 2643661.6578 | 1754309.069 | 574404.717 | 3531085.6813 | 9000 | 55575 | 32615534.9255 | 87.22%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5 |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5 |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5 |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.45 | 0.45
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1098802.3295 | 2331645.3146 | 387760.5012 | 422985.8652 | 280689.451 | 91904.7547 | 141172.8408 | 4050 | 19237.5 | 4778248.5571 | 12.78%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 7980051.9177 | 17050156.3627 | 2835498.6653 | 3066647.523 | 2034998.52 | 666309.4717 | 3672258.5221 | 13050 | 74812.5 | 37393783.4826 | 100%