## OutputA
Project Name: CNSW-NNSW Option 3 | [5 empty] | Indirect Cost Selection
Project Description: • New Central South (Hub 1) 500/330 kV substation with 3 x 500/330/33 kV 1,500 MVA transformers • New 330 kV Central (Hub5) switching station and cut into the existing lines between Tamworth and Armidale • New 500 kV built and initially 330 kV operated DCST line from Central (Hub5) to Central South (Hub1) with Quad Orange conductor • New 500 kV DCST line between Central South (Hub 1) and Bayswater with Quad Orange conductor • 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500kV DCST line between Hub 3 and Bayswater • Rebuild portion of Line 86 from Hub 5 to Tamworth as 330 kV double circuit line. • Rebuild Line 88 Tamworth - Muswellbrook and Line 83 Liddell - Muswellbrook as 330 kV double circuit line. • Augment Hub 5, Tamworth, Muswellbrook and Liddell to accommodate additional lines. Pre-requisite: CNSW-NNSW Option 1. | [5 empty] | Total Network Elements Cost Category |  |  | Above $1500 million
[6 empty] | Greenfield or Brownfield |  |  | Partly brownfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  | 15-10-2021
[6 empty] | Project file |  | CNSW-NNSW Option 3 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[6 empty] | Release Date |  | 4499500%
[6 empty] | Version Number |  | 4-0
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | OHL: Hub 1 - Hub 5 | 155113709.5759 | 43305872.1118 | 31664212.1095 | 40619156.2155 | 0 | 5629789.3153 | 0 | 6552368.8734 | 12190918.3522 | 15151392.5982
2 | OHL: Hub 1 - Bayswater | 1008239112.2532 | 281488168.7551 | 205817378.7198 | 264024515.3601 | 0 | 36593630.5792 | 0 | 42590397.6581 | 79240969.2539 | 98484051.927
3 | Hub 1 Substation | 222699245.6162 | 119941587.067 | 58047709.4887 | 16018944.5758 | 7324454.8802 | 10145061.8026 | 2742489.0115 | 8257430.6275 | 101219.483 | 120348.6798
4 | Hub 5 Cut-in | 5901947.8504 | 1980487.5586 | 1519288.8585 | 874173.3226 | 0 | 221605.5048 | 0 | 256582.3025 | 467318.5434 | 582491.76
5 | Hub 5 Substation | 63229107.8022 | 14607267.8109 | 29168157.0229 | 4647492.4382 | 5163654.7557 | 3323350.6918 | 1122306.7826 | 4975310.1372 | 101219.483 | 120348.6798
6 | Bayswater Substation | 48183289.6961 | 23655230.9209 | 14016063.1688 | 3632010.6462 | 1470588.4271 | 2579290.2014 | 594059.9224 | 2236046.4093 | 0 | 0
7 | Hub 5 - Tamworth 330kV rebuild | 249369919.7197 | 72862001.749 | 56235509.0788 | 40194124.2553 | 0 | 8597351.1966 | 0 | 12014194.7699 | 26481383.7421 | 32985354.9282
8 | Tamworth Substation | 11814234.9809 | 4220098.2598 | 3420912.7844 | 1236983.3932 | 735767.7607 | 962001.2399 | 195106.7947 | 1043364.7482 | 0 | 0
9 | Tamworth - Muswellbrook 330kV rebuild | 450506349.2914 | 120851855.4636 | 105028083.123 | 75068437.9268 | 0 | 16056817.6794 | 0 | 22438275.5296 | 49457878.4513 | 61605001.1178
10 | Muswellbrook - Liddell 330kV rebuild | 63851293.6019 | 17128609.4284 | 14885870.0513 | 10639621.1316 | 0 | 2275769.4276 | 0 | 3180228.0342 | 7009778.0515 | 8731417.4772
11 | Muswellbrook Substation | 11814234.9809 | 4220098.2598 | 3420912.7844 | 1236983.3932 | 735767.7607 | 962001.2399 | 195106.7947 | 1043364.7482 | 0 | 0
12 | Liddell Substation | 11227813.5039 | 4033574.5731 | 3315316.6491 | 1051134.1924 | 735767.7607 | 914588.0726 | 185490.7584 | 991941.4975 | 0 | 0
| Total Network Element Cost | 2301950258.8725 | 708294851.958 | 526539413.8392 | 459243576.851 | 16166001.345 | 88261256.9511 | 5034560.0643 | 105579505.3356 | 175050685.3603 | 217780407.168
Indirect Costs
| Project Development | 55361903.73
| Works Delivery | 43391762.38
| Land and Environment | 18703345.85
| Stakeholder and Community Engagement | 13466409.01
| Procurement Costs | 11222007.51
| Insurance | 7481338.34
| Total Indirect Cost | 149626766.83
| Total Expected Project Cost | 2451577025.7

## OutputB
Project Name: CNSW-NNSW Option 3 |  |  |  |  | Indirect Cost Selection
Project Description: • New Central South (Hub 1) 500/330 kV substation with 3 x 500/330/33 kV 1,500 MVA transformers • New 330 kV Central (Hub5) switching station and cut into the existing lines between Tamworth and Armidale • New 500 kV built and initially 330 kV operated DCST line from Central (Hub5) to Central South (Hub1) with Quad Orange conductor • New 500 kV DCST line between Central South (Hub 1) and Bayswater with Quad Orange conductor • 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500kV DCST line between Hub 3 and Bayswater • Rebuild portion of Line 86 from Hub 5 to Tamworth as 330 kV double circuit line. • Rebuild Line 88 Tamworth - Muswellbrook and Line 83 Liddell - Muswellbrook as 330 kV double circuit line. • Augment Hub 5, Tamworth, Muswellbrook and Liddell to accommodate additional lines. Pre-requisite: CNSW-NNSW Option 1. |  |  |  |  | Total Network Elements Cost Category |  |  | Above $1500 million
[5 empty] | Greenfield or Brownfield |  |  | Partly brownfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. |  |  |  |  | TCD Cost Estimation Tool Version
[5 empty] | Tool Version |  | 15-10-2021
[5 empty] | Project file |  | CNSW-NNSW Option 3 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[5 empty] | Release Date |  | 4499500%
[5 empty] | Version Number |  | 4-0
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 1451835961.37 | 498907921.7 | 317455982.61 | 276845276.71 | 10602787.51 | 57089072.11 | 3244868 | 80172127.5 | 123105445.51 | 84412479.72
Adjusted Baseline Cost | 1610616939.6794 | 522676066.4726 | 382420492.6273 | 331294082.3986 | 12246970.7159 | 65318800.638 | 3814060.6548 | 97639085.4932 | 110794900.959 | 84412479.72
Known Risk Allowance | 106479420.3397 | 2619633.2312 | 9797591.1412 | 9520423.2443 | 0 | 0 | 0 | 129293.0029 | 0 | 84412479.72
Unknown Risk Allowance | 584853898.8534 | 182999152.2542 | 134321330.0707 | 118429071.2082 | 3919030.6291 | 22942456.3131 | 1220499.4095 | 7811126.8395 | 64255784.4013 | 48955447.728
Total Network Element Cost | 2301950258.8725 | 708294851.958 | 526539413.8392 | 459243576.851 | 16166001.345 | 88261256.9511 | 5034560.0643 | 105579505.3356 | 175050685.3603 | 217780407.168
Indirect Costs:
Project Development | 55361903.7259
Works Delivery | 43391762.3797
Land and Environment | 18703345.8533
Stakeholder and Community Engagement | 13466409.0144
Procurement Costs | 11222007.512
Insurance | 7481338.3413
Total Indirect Cost | 149626766.8267
Total Expected Project Cost | 2451577025.6992

## OutputC
Project Name: CNSW-NNSW Option 3
Project Description: • New Central South (Hub 1) 500/330 kV substation with 3 x 500/330/33 kV 1,500 MVA transformers • New 330 kV Central (Hub5) switching station and cut into the existing lines between Tamworth and Armidale • New 500 kV built and initially 330 kV operated DCST line from Central (Hub5) to Central South (Hub1) with Quad Orange conductor • New 500 kV DCST line between Central South (Hub 1) and Bayswater with Quad Orange conductor • 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500kV DCST line between Hub 3 and Bayswater • Rebuild portion of Line 86 from Hub 5 to Tamworth as 330 kV double circuit line. • Rebuild Line 88 Tamworth - Muswellbrook and Line 83 Liddell - Muswellbrook as 330 kV double circuit line. • Augment Hub 5, Tamworth, Muswellbrook and Liddell to accommodate additional lines. Pre-requisite: CNSW-NNSW Option 1.
Project Cost Estimate - View C
|  | View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[8 empty] | Tool Version |  | 15-10-2021
[8 empty] | Project file |  | CNSW-NNSW Option 3 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[8 empty] | Release Date |  | 4499500%
[8 empty] | Version Number |  | 4-0
Network Element 1
OHL: Hub 1 - Hub 5
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 30 | km | 30483354.06 | 19552816.37 | 25082541.13 | 0 | 3797578.98 | 0 | 5234206.05 | 8573079.01 | 5872632.79 | 98596208.39 | 63.56%
TRUE | TRUE | Baseline Cost | [6 empty] | 30483354.06 | 19552816.37 | 25082541.13 | 0 | 3797578.98 | 0 | 5234206.05 | 8573079.01 | 5872632.79 | 98596208.39 | 63.56%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04 | 0.16505 | 0.16505 | 0 | 0.09005 | 0.09005 | 0.1575 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 31702688.2224 | 22780008.7119 | 29222414.5435 | 0 | 4139550.9671 | 0 | 6058593.5029 | 7715771.109 | 5872632.79 | 107491659.8468 | 69.3%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 190216.1293 | 683400.2614 | 876672.4363 | 0 | 0 | 0 | 9087.8903 | 0 | 5872632.79 | 7632009.5072 | 4.92%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 31892904.3517 | 23463408.9732 | 30099086.9798 | 0 | 4139550.9671 | 0 | 6067681.3931 | 7715771.109 | 11745265.58 | 115123669.354 | 74.22%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 11412967.7601 | 8200803.1363 | 10520069.2357 | 0 | 1490238.3482 | 0 | 484687.4802 | 4475147.2432 | 3406127.0182 | 39990040.2218 | 25.78%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 43305872.1118 | 31664212.1095 | 40619156.2155 | 0 | 5629789.3153 | 0 | 6552368.8734 | 12190918.3522 | 15151392.5982 | 155113709.5759 | 100%
Network Element 2
OHL: Hub 1 - Bayswater
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 195 | km | 198141801.41 | 127093306.41 | 163036517.32 | 0 | 24684263.39 | 0 | 34022339.31 | 55725013.54 | 38172113.15 | 640875354.53 | 63.56%
TRUE | TRUE | Baseline Cost | [6 empty] | 198141801.41 | 127093306.41 | 163036517.32 | 0 | 24684263.39 | 0 | 34022339.31 | 55725013.54 | 38172113.15 | 640875354.53 | 63.56%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04 | 0.16505 | 0.16505 | 0 | 0.09005 | 0.09005 | 0.1575 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 206067473.4664 | 148070056.633 | 189945694.5037 | 0 | 26907081.3083 | 0 | 39380857.7513 | 50152512.186 | 38172113.15 | 698695788.9986 | 69.3%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 1236404.8408 | 4442101.699 | 5698370.8351 | 0 | 0 | 0 | 59071.2866 | 0 | 38172113.15 | 49608061.8115 | 4.92%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 207303878.3072 | 152512158.332 | 195644065.3388 | 0 | 26907081.3083 | 0 | 39439929.038 | 50152512.186 | 76344226.3 | 748303850.8102 | 74.22%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 74184290.4479 | 53305220.3879 | 68380450.0213 | 0 | 9686549.271 | 0 | 3150468.6201 | 29088457.0679 | 22139825.627 | 259935261.4431 | 25.78%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 281488168.7551 | 205817378.7198 | 264024515.3601 | 0 | 36593630.5792 | 0 | 42590397.6581 | 79240969.2539 | 98484051.927 | 1008239112.2532 | 100%
Network Element 3
Hub 1 Substation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | N/A | 1 | lot | 425245.1 | 12924480.74 | 923177.2 | 1901393.68 | 364148.32 | 369270.88 | 1456593.28 | 73029.93 | 47381.37 | 18484720.5 | 8.3%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 2227247.07 | 1604904.2 | 510911.18 | 222988.47 | 422859.64 | 85761.62 | 522654.52 | 0 | 0 | 5597326.7 | 2.513%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 5 | lot | 10608224.19 | 7801220.66 | 2286595.48 | 1114942.34 | 2020638.68 | 409812.69 | 2497509.4 | 0 | 0 | 26738943.44 | 12.01%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3ph) 1500MVA | 500/330 | 3 | ea. | 54056808.5 | 7145610.87 | 4473152.4 | 334482.7 | 2205550.22 | 560930.45 | 0 | 0 | 0 | 68776535.14 | 30.88%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 150MVAr | 500 | 2 | ea. | 10226785.2 | 3573600.6 | 724985.4 | 222414.4 | 307958.4 | 104791.4 | 0 | 0 | 0 | 15160535.4 | 6.808%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 5 | lot | 7117864.71 | 4907546 | 1555956.77 | 1114942.34 | 1364346.55 | 276707.83 | 1686332.34 | 0 | 0 | 18023696.54 | 8.093%
TRUE | TRUE | Baseline Cost | [6 empty] | 84662174.77 | 37957363.07 | 10474778.43 | 4911163.93 | 6685501.81 | 1807274.87 | 6163089.54 | 73029.93 | 47381.37 | 152781757.72 | 68.6%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07164 | 0.14984 | 0.14984 | 0.12984 | 0.1496 | 0.1496 | 0.24 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 90727372.9705 | 43644894.3524 | 12044319.23 | 5548829.4547 | 7685652.8808 | 2077643.1906 | 7642231.0296 | 65726.937 | 47381.37 | 169484051.4155 | 76.1%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 181454.7459 | 436448.9435 | 120443.1923 | 0 | 0 | 0 | 3821.1155 | 0 | 47381.37 | 789549.3673 | 0.3545%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 90908827.7165 | 44081343.2959 | 12164762.4223 | 5548829.4547 | 7685652.8808 | 2077643.1906 | 7646052.1451 | 65726.937 | 94762.74 | 170273600.7828 | 76.46%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 29032759.3506 | 13966366.1928 | 3854182.1536 | 1775625.4255 | 2459408.9218 | 664845.821 | 611378.4824 | 35492.546 | 25585.9398 | 52425644.8334 | 23.54%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 119941587.067 | 58047709.4887 | 16018944.5758 | 7324454.8802 | 10145061.8026 | 2742489.0115 | 8257430.6275 | 101219.483 | 120348.6798 | 222699245.6162 | 100%
Network Element 4
|  | Hub 5 Cut-in | Cutting in to existing lines between Tamworth and Armdale
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 5 (3 × conductor/phase SCST) | 330 | 2 | lot | 1394081.23 | 850561.12 | 489398.6 | 0 | 134659.91 | 0 | 185711.7 | 328634.7 | 225772 | 3608819.26 | 61.15%
TRUE | TRUE | Baseline Cost | [6 empty] | 1394081.23 | 850561.12 | 489398.6 | 0 | 134659.91 | 0 | 185711.7 | 328634.7 | 225772 | 3608819.26 | 61.15%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04 | 0.28505 | 0.28505 | 0 | 0.21005 | 0.21005 | 0.2775 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1449844.4792 | 1093013.5673 | 628901.6709 | 0 | 162945.2241 | 0 | 237246.6968 | 295771.23 | 225772 | 4093494.8682 | 69.36%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 8699.0669 | 32790.407 | 18867.0501 | 0 | 0 | 0 | 355.87 | 0 | 225772 | 286484.3941 | 4.854%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1458543.5461 | 1125803.9743 | 647768.7211 | 0 | 162945.2241 | 0 | 237602.5668 | 295771.23 | 451544 | 4379979.2623 | 74.21%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 521944.0125 | 393484.8842 | 226404.6015 | 0 | 58660.2807 | 0 | 18979.7357 | 171547.3134 | 130947.76 | 1521968.5881 | 25.79%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 1980487.5586 | 1519288.8585 | 874173.3226 | 0 | 221605.5048 | 0 | 256582.3025 | 467318.5434 | 582491.76 | 5901947.8504 | 100%
Network Element 5
Hub 5 Substation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | N/A | 1 | lot | 425245.1 | 12924480.74 | 923177.2 | 1901393.68 | 364148.32 | 369270.88 | 1456593.28 | 73029.93 | 47381.37 | 18484720.5 | 29.23%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 2 | lot | 4191174.29 | 2222523.17 | 871049.96 | 668965.4 | 734431.78 | 148952.64 | 907757.68 | 0 | 0 | 9744854.92 | 15.41%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 4 | lot | 5694291.77 | 3926036.8 | 1244765.41 | 891953.87 | 1091477.24 | 221366.26 | 1349065.87 | 0 | 0 | 14418957.22 | 22.8%
TRUE | TRUE | Baseline Cost | [6 empty] | 10310711.16 | 19073040.71 | 3038992.57 | 3462312.95 | 2190057.34 | 739589.78 | 3713416.83 | 73029.93 | 47381.37 | 42648532.64 | 67.45%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07164 | 0.14984 | 0.14984 | 0.12984 | 0.1496 | 0.1496 | 0.24 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 11049370.5075 | 21930945.13 | 3494355.2167 | 3911859.6634 | 2517689.9181 | 850232.4111 | 4604636.8692 | 65726.937 | 47381.37 | 48472198.023 | 76.66%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 22098.741 | 219309.4513 | 34943.5522 | 0 | 0 | 0 | 2302.3184 | 0 | 47381.37 | 326035.4329 | 0.5156%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 11071469.2485 | 22150254.5813 | 3529298.7689 | 3911859.6634 | 2517689.9181 | 850232.4111 | 4606939.1876 | 65726.937 | 94762.74 | 48798233.4559 | 77.18%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 3535798.5624 | 7017902.4416 | 1118193.6693 | 1251795.0923 | 805660.7738 | 272074.3715 | 368370.9495 | 35492.546 | 25585.9398 | 14430874.3463 | 22.82%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 14607267.8109 | 29168157.0229 | 4647492.4382 | 5163654.7557 | 3323350.6918 | 1122306.7826 | 4975310.1372 | 101219.483 | 120348.6798 | 63229107.8022 | 100%
Network Element 6
Bayswater Substation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 2 | lot | 4243289.68 | 3120488.27 | 914638.19 | 445976.94 | 808255.47 | 163925.08 | 999003.76 | 0 | 0 | 10695577.39 | 22.2%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 2227247.07 | 1604904.2 | 510911.18 | 222988.47 | 422859.64 | 85761.62 | 522654.52 | 0 | 0 | 5597326.7 | 11.62%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 150MVAr | 500 | 2 | ea. | 10226785.2 | 3573600.6 | 724985.4 | 222414.4 | 307958.4 | 104791.4 | 0 | 0 | 0 | 15160535.4 | 31.46%
TRUE | TRUE | Baseline Cost | [6 empty] | 16697321.95 | 8298993.07 | 2150534.77 | 891379.81 | 1539073.51 | 354478.1 | 1521658.28 | 0 | 0 | 31453439.49 | 65.28%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07164 | 0.26984 | 0.26984 | 0.24984 | 0.2696 | 0.2696 | 0.36 | -0.05 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 17893518.0945 | 10538393.36 | 2730835.0723 | 1114082.1417 | 1954007.7283 | 450045.3958 | 2069455.2608 | 0 | 0 | 36750337.0534 | 76.27%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 35787.0362 | 105383.9336 | 27308.3507 | 0 | 0 | 0 | 1034.7276 | 0 | 0 | 169514.0481 | 0.3518%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 17929305.1307 | 10643777.2936 | 2758143.4231 | 1114082.1417 | 1954007.7283 | 450045.3958 | 2070489.9884 | 0 | 0 | 36919851.1016 | 76.62%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 5725925.7902 | 3372285.8752 | 873867.2231 | 356506.2854 | 625282.4731 | 144014.5266 | 165556.4209 | 0 | 0 | 11263438.5945 | 23.38%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 23655230.9209 | 14016063.1688 | 3632010.6462 | 1470588.4271 | 2579290.2014 | 594059.9224 | 2236046.4093 | 0 | 0 | 48183289.6961 | 100%
Network Element 7
|  | Hub 5 - Tamworth 330kV rebuild | Rebuild of line 86 between Hub 5 and Tamworth
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Olive DCST 2212 MVA | 330 | 68 | km | 51288153.05 | 31482977.92 | 22502343.22 | 0 | 5224231.86 | 0 | 8695753.81 | 18622632.73 | 12785021.29 | 150601113.88 | 60.39%
TRUE | TRUE | Baseline Cost | [6 empty] | 51288153.05 | 31482977.92 | 22502343.22 | 0 | 5224231.86 | 0 | 8695753.81 | 18622632.73 | 12785021.29 | 150601113.88 | 60.39%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04 | 0.28505 | 0.28505 | 0 | 0.21005 | 0.21005 | 0.2775 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 53339679.172 | 40457200.7761 | 28916636.1549 | 0 | 6321581.7622 | 0 | 11108825.4923 | 16760369.457 | 12785021.29 | 169689314.1044 | 68.05%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 320038.075 | 1213716.0233 | 867499.0846 | 0 | 0 | 0 | 16663.2382 | 0 | 12785021.29 | 15202937.7112 | 6.097%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 53659717.247 | 41670916.7994 | 29784135.2395 | 0 | 6321581.7622 | 0 | 11125488.7305 | 16760369.457 | 25570042.58 | 184892251.8156 | 74.14%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 19202284.5019 | 14564592.2794 | 10409989.0157 | 0 | 2275769.4344 | 0 | 888706.0394 | 9721014.2851 | 7415312.3482 | 64477667.9041 | 25.86%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 72862001.749 | 56235509.0788 | 40194124.2553 | 0 | 8597351.1966 | 0 | 12014194.7699 | 26481383.7421 | 32985354.9282 | 249369919.7197 | 100%
Network Element 8
|  | Tamworth Substation | Modifications
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 4 | lot | 2978805.81 | 2025542.49 | 732425.11 | 445976.94 | 574030.26 | 116421.06 | 709501.41 | 0 | 0 | 7582703.08 | 64.18%
TRUE | TRUE | Baseline Cost | [6 empty] | 2978805.81 | 2025542.49 | 732425.11 | 445976.94 | 574030.26 | 116421.06 | 709501.41 | 0 | 0 | 7582703.08 | 64.18%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07164 | 0.26984 | 0.26984 | 0.24984 | 0.2696 | 0.2696 | 0.361 | -0.05 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 3192207.4582 | 2572114.8755 | 930062.7017 | 557399.8187 | 728788.8181 | 147808.1778 | 965631.419 | 0 | 0 | 9094013.269 | 76.98%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 6384.4149 | 25721.1488 | 9300.627 | 0 | 0 | 0 | 482.8157 | 0 | 0 | 41889.0064 | 0.3546%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 3198591.8731 | 2597836.0243 | 939363.3287 | 557399.8187 | 728788.8181 | 147808.1778 | 966114.2347 | 0 | 0 | 9135902.2754 | 77.33%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1021506.3866 | 823076.7602 | 297620.0645 | 178367.942 | 233212.4218 | 47298.6169 | 77250.5135 | 0 | 0 | 2678332.7055 | 22.67%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 4220098.2598 | 3420912.7844 | 1236983.3932 | 735767.7607 | 962001.2399 | 195106.7947 | 1043364.7482 | 0 | 0 | 11814234.9809 | 100%
Network Element 9
|  | Tamworth - Muswellbrook 330kV rebuild | Rebuild line 88 between Tamworth and Muswellbrook
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 × Mango DCST 1834 MVA | 330 | 126.9 | km | 85068599.69 | 58799091.11 | 42026435.12 | 0 | 9757021.27 | 0 | 16240599.03 | 34780505.24 | 23877907.41 | 270550158.87 | 60.05%
TRUE | TRUE | Baseline Cost | [6 empty] | 85068599.69 | 58799091.11 | 42026435.12 | 0 | 9757021.27 | 0 | 16240599.03 | 34780505.24 | 23877907.41 | 270550158.87 | 60.05%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04 | 0.28505 | 0.28505 | 0 | 0.21005 | 0.21005 | 0.2775 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 88471343.6776 | 75559772.0309 | 54006070.451 | 0 | 11806483.5878 | 0 | 20747365.2608 | 31302454.716 | 23877907.41 | 305771397.1341 | 67.87%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 530828.0621 | 2266793.1609 | 1620182.1135 | 0 | 0 | 0 | 31121.0479 | 0 | 23877907.41 | 28326831.7944 | 6.288%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 89002171.7397 | 77826565.1918 | 55626252.5645 | 0 | 11806483.5878 | 0 | 20778486.3087 | 31302454.716 | 47755814.82 | 334098228.9285 | 74.16%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 31849683.7239 | 27201517.9311 | 19442185.3623 | 0 | 4250334.0916 | 0 | 1659789.2209 | 18155423.7353 | 13849186.2978 | 116408120.3629 | 25.84%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 120851855.4636 | 105028083.123 | 75068437.9268 | 0 | 16056817.6794 | 0 | 22438275.5296 | 49457878.4513 | 61605001.1178 | 450506349.2914 | 100%
Network Element 10
|  | Muswellbrook - Liddell 330kV rebuild | Rebuild of line 83 between Liddell and Muswellbrook
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 × Mango DCST 1834 MVA | 330 | 17.7 | km | 12056966.88 | 8333729.45 | 5956502.62 | 0 | 1382884.9 | 0 | 2301817.19 | 4929520.43 | 3384270.34 | 38345691.81 | 60.05%
TRUE | TRUE | Baseline Cost | [6 empty] | 12056966.88 | 8333729.45 | 5956502.62 | 0 | 1382884.9 | 0 | 2301817.19 | 4929520.43 | 3384270.34 | 38345691.81 | 60.05%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Northern | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04 | 0.28505 | 0.28505 | 0 | 0.21005 | 0.21005 | 0.2775 | -0.1 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 12539245.5552 | 10709259.0297 | 7654403.6918 | 0 | 1673359.8732 | 0 | 2940571.4602 | 4436568.387 | 3384270.34 | 43337678.3372 | 67.87%
FALSE | FALSE | Known Risks: | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 75235.4733 | 321277.7709 | 229632.1108 | 0 | 0 | 0 | 4410.8572 | 0 | 3384270.34 | 4014826.5522 | 6.288%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 12614481.0285 | 11030536.8006 | 7884035.8026 | 0 | 1673359.8732 | 0 | 2944982.3174 | 4436568.387 | 6768540.68 | 47352504.8894 | 74.16%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 4514128.3999 | 3855333.2507 | 2755585.3291 | 0 | 602409.5544 | 0 | 235245.7168 | 2573209.6645 | 1962876.7972 | 16498788.7125 | 25.84%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 17128609.4284 | 14885870.0513 | 10639621.1316 | 0 | 2275769.4276 | 0 | 3180228.0342 | 7009778.0515 | 8731417.4772 | 63851293.6019 | 100%
Network Element 11
|  | Muswellbrook Substation | Modifications
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 4 | lot | 2978805.81 | 2025542.49 | 732425.11 | 445976.94 | 574030.26 | 116421.06 | 709501.41 | 0 | 0 | 7582703.08 | 64.18%
TRUE | TRUE | Baseline Cost | [6 empty] | 2978805.81 | 2025542.49 | 732425.11 | 445976.94 | 574030.26 | 116421.06 | 709501.41 | 0 | 0 | 7582703.08 | 64.18%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07164 | 0.26984 | 0.26984 | 0.24984 | 0.2696 | 0.2696 | 0.361 | -0.05 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 3192207.4582 | 2572114.8755 | 930062.7017 | 557399.8187 | 728788.8181 | 147808.1778 | 965631.419 | 0 | 0 | 9094013.269 | 76.98%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 6384.4149 | 25721.1488 | 9300.627 | 0 | 0 | 0 | 482.8157 | 0 | 0 | 41889.0064 | 0.3546%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 3198591.8731 | 2597836.0243 | 939363.3287 | 557399.8187 | 728788.8181 | 147808.1778 | 966114.2347 | 0 | 0 | 9135902.2754 | 77.33%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1021506.3866 | 823076.7602 | 297620.0645 | 178367.942 | 233212.4218 | 47298.6169 | 77250.5135 | 0 | 0 | 2678332.7055 | 22.67%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 4220098.2598 | 3420912.7844 | 1236983.3932 | 735767.7607 | 962001.2399 | 195106.7947 | 1043364.7482 | 0 | 0 | 11814234.9809 | 100%
Network Element 12
|  | Liddell Substation | Modifications
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 2 | lot | 2847145.88 | 1963018.4 | 622382.71 | 445976.94 | 545738.62 | 110683.13 | 674532.94 | 0 | 0 | 7209478.62 | 64.21%
TRUE | TRUE | Baseline Cost | [6 empty] | 2847145.88 | 1963018.4 | 622382.71 | 445976.94 | 545738.62 | 110683.13 | 674532.94 | 0 | 0 | 7209478.62 | 64.21%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Remote | - | - | - | 0.05 | 0.07 | 0.07 | 0.05 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.07164 | 0.26984 | 0.26984 | 0.24984 | 0.2696 | 0.2696 | 0.361 | -0.05 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 3051115.4108 | 2492719.2851 | 790326.4605 | 557399.8187 | 692869.752 | 140523.3018 | 918039.3313 | 0 | 0 | 8642993.3602 | 76.98%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 6102.2308 | 24927.1929 | 7903.2646 | 0 | 0 | 0 | 459.0197 | 0 | 0 | 39391.7079 | 0.3508%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 3057217.6417 | 2517646.4779 | 798229.7251 | 557399.8187 | 692869.752 | 140523.3018 | 918498.351 | 0 | 0 | 8682385.0681 | 77.33%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 976356.9315 | 797670.1712 | 252904.4673 | 178367.942 | 221718.3206 | 44967.4566 | 73443.1465 | 0 | 0 | 2545428.4357 | 22.67%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 4033574.5731 | 3315316.6491 | 1051134.1924 | 735767.7607 | 914588.0726 | 185490.7584 | 991941.4975 | 0 | 0 | 11227813.5039 | 100%