## OutputA
Project Name: CNSW-SNW Option 3 | [5 empty] | Indirect Cost Selection
Project Description: Both SNW Northern 500 kV loop and SNW Southern 500 kV loop: • CNSW-SNW Option 1. • CNSW-SNW Option 2. | [5 empty] | Total Network Elements Cost Category |  |  | Above $1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Highly sensitive
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  | 15-10-2021
[6 empty] | Project file |  | CNSW-SNW Option 3 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[6 empty] | Release Date |  | 4499500%
[6 empty] | Version Number |  | 4-0
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Bannaby to locality of South Creek overhead line | 738499883.962 | 181260373.9538 | 138643440.1828 | 177853140.1577 | 0 | 24701194.2586 | 0 | 28922777.7534 | 123988155.1416 | 63130802.514
2 | Bannaby Substation | 28243074.8167 | 9204352.9009 | 10212278.4369 | 2530986.1185 | 1114350.8062 | 2250005.6443 | 464719.85 | 2466381.0599 | 0 | 0
3 | New South Creek substation | 225208138.8536 | 97284784.1966 | 76912769.7402 | 16093975.3843 | 10925752.3281 | 9432688.2782 | 3179333.2263 | 10458487.5896 | 619476.3982 | 300871.7122
4 | Near South Creek to Sydney West | 28203920.7787 | 7348973.8518 | 5252433.9229 | 3690743.0776 | 0 | 767999.7232 | 0 | 1094187.9838 | 6654030.9841 | 3395551.2354
5 | Eraring-Kemps Creek 500 kV line diversion near South Creek | 11427689.6652 | 3244125.2086 | 2374925.0345 | 3258747.218 | 0 | 438056.891 | 0 | 450010.6082 | 1056546.256 | 605278.449
6 | Bayswater-Sydney West and Regentville-Sydney West line cut-in near South Creek | 10629640.1559 | 3718476.888 | 2762622.5015 | 1158951.1046 | 0 | 393876.0022 | 0 | 444168.7851 | 986561.3544 | 1164983.52
7 | Sydney West substation | 17080470.2307 | 1308108.9473 | 10980473.4421 | 1034664.88 | 1607514.4179 | 507093.8199 | 330252.6327 | 1227447.7147 | 54827.2124 | 30087.1636
8 | Bayswater - Eraring Overhead line | 610984978.6215 | 152258714.1235 | 114455519.528 | 144344496.6135 | 0 | 19632514.9587 | 0 | 23113808.9904 | 104150050.3009 | 53029874.1066
9 | Bayswater Substation | 33987600.8238 | 6373863.8447 | 17620121.9149 | 2471538.2354 | 2440746.7666 | 1684862.8641 | 618775.9178 | 2650319.7163 | 82240.8187 | 45130.7454
10 | Eraring Substation | 205487876.4384 | 83731768.9861 | 77625365.4172 | 14378329.6332 | 9978426.3524 | 7568161.3488 | 2970980.5216 | 8314496.0686 | 619476.3982 | 300871.7122
| Total Network Element Cost | 1909753274.3465 | 545733542.9012 | 456839950.121 | 366815572.4228 | 26066790.6713 | 67376453.7889 | 7564062.1484 | 79142086.27 | 238211364.8645 | 122003451.1584
Indirect Costs
| Project Development | 42205547.36
| Works Delivery | 52136264.39
| Land and Environment | 9930717.03
| Stakeholder and Community Engagement | 13034066.1
| Procurement Costs | 6206698.14
| Insurance | 4965358.51
| Total Indirect Cost | 128478651.53
| Total Expected Project Cost | 2038231925.88

## OutputB
Project Name: CNSW-SNW Option 3 |  |  |  |  | Indirect Cost Selection
Project Description: Both SNW Northern 500 kV loop and SNW Southern 500 kV loop: • CNSW-SNW Option 1. • CNSW-SNW Option 2. |  |  |  |  | Total Network Elements Cost Category |  |  | Above $1500 million
[5 empty] | Greenfield or Brownfield |  |  | Brownfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Highly sensitive
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. |  |  |  |  | TCD Cost Estimation Tool Version
[5 empty] | Tool Version |  | 15-10-2021
[5 empty] | Project file |  | CNSW-SNW Option 3 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[5 empty] | Release Date |  | 4499500%
[5 empty] | Version Number |  | 4-0
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 1117111763.51 | 384310437.26 | 272801108.86 | 219184508.67 | 16549211.82 | 43734159.07 | 4696216.95 | 59488868.74 | 69054960.68 | 47292291.46
Adjusted Baseline Cost | 1290170248.3188 | 392714595.203 | 317543025.5968 | 254926308.6809 | 19166757.8466 | 48576517.6634 | 5461416.7137 | 70489431.2185 | 133999903.936 | 47292291.46
Known Risk Allowance | 148920064.4165 | 17453819.0896 | 30427942.6038 | 21144229.0746 | 766670.3139 | 1943060.7065 | 354992.0864 | 3013500.554 | 26523558.5277 | 47292291.46
Unknown Risk Allowance | 470662961.6113 | 135565128.6086 | 108868981.9204 | 90745034.6673 | 6133362.5109 | 16856875.419 | 1747653.3484 | 5639154.4975 | 77687902.4008 | 27418868.2384
Total Network Element Cost | 1909753274.3465 | 545733542.9012 | 456839950.121 | 366815572.4228 | 26066790.6713 | 67376453.7889 | 7564062.1484 | 79142086.27 | 238211364.8645 | 122003451.1584
Indirect Costs:
Project Development | 42205547.3631
Works Delivery | 52136264.3897
Land and Environment | 9930717.0266
Stakeholder and Community Engagement | 13034066.0974
Procurement Costs | 6206698.1416
Insurance | 4965358.5133
Total Indirect Cost | 128478651.5317
Total Expected Project Cost | 2038231925.8782

## OutputC
Project Name: CNSW-SNW Option 3
Project Description: Both SNW Northern 500 kV loop and SNW Southern 500 kV loop: • CNSW-SNW Option 1. • CNSW-SNW Option 2.
Project Cost Estimate - View C
|  | View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[8 empty] | Tool Version |  | 15-10-2021
[8 empty] | Project file |  | CNSW-SNW Option 3 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[8 empty] | Release Date |  | 4499500%
[8 empty] | Version Number |  | 4-0
Network Element 1
|  | Bannaby to locality of South Creek overhead line | 500 kV line double circuit line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 125 | km | 127013975.26 | 81470068.21 | 104510588.03 | 0 | 15823245.76 | 0 | 21809191.86 | 35721162.53 | 24469303.3 | 410817534.95 | 55.63%
TRUE | TRUE | Baseline Cost | [6 empty] | 127013975.26 | 81470068.21 | 104510588.03 | 0 | 15823245.76 | 0 | 21809191.86 | 35721162.53 | 24469303.3 | 410817534.95 | 55.63%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Partly brownfield | - | - | - | 0 | 0.06 | 0.06 | 0 | 0.06 | 0.06 | 0.06 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.015 | 0.19005 | 0.19005 | 0 | 0.11505 | 0.11505 | 0.1825 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 128919184.8889 | 96953454.6733 | 124372825.2851 | 0 | 17643710.1847 | 0 | 25789369.3745 | 69656266.9335 | 24469303.3 | 487804114.6399 | 66.05%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.07 | 0.07 | 0 | 0.04 | 0.04 | 0.0415 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 5930282.5049 | 6786741.8271 | 8706097.77 | 0 | 705748.4074 | 0 | 1070258.829 | 13931253.3867 | 24469303.3 | 61599686.0251 | 8.341%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 134849467.3938 | 103740196.5004 | 133078923.0551 | 0 | 18349458.5921 | 0 | 26859628.2035 | 83587520.3202 | 48938606.6 | 549403800.6651 | 74.39%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 46410906.56 | 34903243.6824 | 44774217.1026 | 0 | 6351735.6665 | 0 | 2063149.55 | 40400634.8214 | 14192195.914 | 189096083.2969 | 25.61%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 181260373.9538 | 138643440.1828 | 177853140.1577 | 0 | 24701194.2586 | 0 | 28922777.7534 | 123988155.1416 | 63130802.514 | 738499883.962 | 100%
Network Element 2
|  | Bannaby Substation | 500 kV Extension
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 1CB | 500 | 2 | lot | 2213532.49 | 2703541.87 | 528775.2 | 222988.47 | 531786.58 | 107853.47 | 657288.21 | 0 | 0 | 6965766.29 | 24.66%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 2 | lot | 4243289.68 | 3120488.27 | 914638.19 | 445976.94 | 808255.47 | 163925.08 | 999003.76 | 0 | 0 | 10695577.39 | 37.87%
TRUE | TRUE | Baseline Cost | [6 empty] | 6456822.17 | 5824030.14 | 1443413.39 | 668965.41 | 1340042.05 | 271778.55 | 1656291.97 | 0 | 0 | 17661343.68 | 62.53%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.8 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04664 | 0.23484 | 0.23484 | 0.22484 | 0.2346 | 0.2346 | 0.326 | -0.85 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 6757968.356 | 7191745.3781 | 1782384.5905 | 819375.5928 | 1654415.9149 | 335537.7978 | 2196243.1522 | 0 | 0 | 20737670.7824 | 73.43%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 283834.671 | 719174.5378 | 178238.4591 | 32775.0237 | 66176.6366 | 21809.9569 | 94438.4555 | 0 | 0 | 1396447.7405 | 4.944%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 7041803.027 | 7910919.9159 | 1960623.0496 | 852150.6165 | 1720592.5515 | 357347.7547 | 2290681.6078 | 0 | 0 | 22134118.5229 | 78.37%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 2162549.8739 | 2301358.521 | 570363.069 | 262200.1897 | 529413.0928 | 107372.0953 | 175699.4522 | 0 | 0 | 6108956.2938 | 21.63%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 9204352.9009 | 10212278.4369 | 2530986.1185 | 1114350.8062 | 2250005.6443 | 464719.85 | 2466381.0599 | 0 | 0 | 28243074.8167 | 100%
Network Element 3
|  | New South Creek substation | 500/330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 4 | lot | 12628381.17 | 7074869.32 | 2601002.36 | 1337930.81 | 2176495.21 | 441422.49 | 2690148.08 | 0 | 0 | 28950249.44 | 12.85%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 2 | ea. | 48535730.23 | 7145610.87 | 4018215.18 | 222988.47 | 1982411.49 | 502574.63 | 0 | 0 | 0 | 62407530.87 | 27.71%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 3 | lot | 6286761.43 | 3333784.75 | 1306574.95 | 1003448.11 | 1101647.67 | 223428.96 | 1361636.52 | 0 | 0 | 14617282.39 | 6.491%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 1423572.94 | 981509.2 | 311191.35 | 222988.47 | 272869.31 | 55341.57 | 337266.47 | 0 | 0 | 3604739.31 | 1.601%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 25000 m2 footprint area and applicable control building | (blank) | 2 | lot | 1040483.7 | 31623436.81 | 2258816.91 | 4652303.18 | 890992.96 | 903526.77 | 3563971.85 | 182574.83 | 118453.43 | 45234560.44 | 20.09%
TRUE | TRUE | Baseline Cost | [6 empty] | 69914929.47 | 50159210.95 | 10495800.75 | 7439659.04 | 6424416.64 | 2126294.42 | 7953022.92 | 182574.83 | 118453.43 | 154814362.45 | 68.74%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02164 | 0.07984 | 0.07984 | 0.07984 | 0.0796 | 0.0796 | 0.171 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 71427888.5437 | 54163922.3522 | 11333785.4819 | 8033641.4178 | 6935800.2045 | 2295547.4558 | 9312989.8393 | 356020.9185 | 118453.43 | 163978049.6438 | 72.81%
FALSE | FALSE | Known Risks: | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 2999971.3188 | 5416392.2352 | 1133378.5482 | 321345.6567 | 277432.0082 | 149210.5846 | 400458.5631 | 71204.1837 | 118453.43 | 10887846.5286 | 4.835%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 74427859.8626 | 59580314.5875 | 12467164.0301 | 8354987.0745 | 7213232.2127 | 2444758.0405 | 9713448.4024 | 427225.1022 | 236906.86 | 174865896.1724 | 77.65%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 22856924.334 | 17332455.1527 | 3626811.3542 | 2570765.2537 | 2219456.0655 | 734575.1859 | 745039.1871 | 192251.296 | 63964.8522 | 50342242.6813 | 22.35%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 97284784.1966 | 76912769.7402 | 16093975.3843 | 10925752.3281 | 9432688.2782 | 3179333.2263 | 10458487.5896 | 619476.3982 | 300871.7122 | 225208138.8536 | 100%
Network Element 4
|  | Near South Creek to Sydney West | 330 kV DCT
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Olive DCST 2212 MVA | 330 | 7 | km | 5279662.81 | 3240894.79 | 2316417.68 | 0 | 537788.57 | 0 | 895151.13 | 1917035.72 | 1316105.13 | 15503055.83 | 54.97%
TRUE | TRUE | Baseline Cost | [6 empty] | 5279662.81 | 3240894.79 | 2316417.68 | 0 | 537788.57 | 0 | 895151.13 | 1917035.72 | 1316105.13 | 15503055.83 | 54.97%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | -0.01 | 0.09505 | 0.09505 | 0 | 0.02005 | 0.02005 | 0.0875 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 5226866.1819 | 3548941.8398 | 2536593.1805 | 0 | 548571.2308 | 0 | 973476.8539 | 3738219.654 | 1316105.13 | 17888774.0709 | 63.43%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 240435.8444 | 425873.0208 | 240976.3521 | 0 | 21942.8492 | 0 | 42832.9816 | 747643.9308 | 1316105.13 | 3035810.1089 | 10.76%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 5467302.0263 | 3974814.8606 | 2777569.5326 | 0 | 570514.0801 | 0 | 1016309.8354 | 4485863.5848 | 2632210.26 | 20924584.1798 | 74.19%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1881671.8255 | 1277619.0623 | 913173.545 | 0 | 197485.6431 | 0 | 77878.1483 | 2168167.3993 | 763340.9754 | 7279336.5989 | 25.81%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 7348973.8518 | 5252433.9229 | 3690743.0776 | 0 | 767999.7232 | 0 | 1094187.9838 | 6654030.9841 | 3395551.2354 | 28203920.7787 | 100%
Network Element 5
|  | Eraring-Kemps Creek 500 kV line diversion near South Creek | 500 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 6 (4 × conductor/phase DCST) | 500 | 2 | lot | 2148370.38 | 1207925.5 | 1686529.94 | 0 | 244271.24 | 0 | 292158.81 | 342923.16 | 234604.05 | 6156783.08 | 53.88%
TRUE | TRUE | Baseline Cost | [6 empty] | 2148370.38 | 1207925.5 | 1686529.94 | 0 | 244271.24 | 0 | 292158.81 | 342923.16 | 234604.05 | 6156783.08 | 53.88%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 10 to 100 km | - | - | - | 0.0336 | 0.055944 | 0.055944 | 0 | 0.055944 | 0.055944 | 0.0672 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0786 | 0.35594 | 0.35594 | 0 | 0.28094 | 0.28094 | 0.3722 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 2317232.2919 | 1637879.3342 | 2286840.153 | 0 | 312897.7793 | 0 | 400900.3191 | 668700.162 | 234604.05 | 7859054.0893 | 68.77%
FALSE | FALSE | Known Risks: | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.04 | 0.09 | 0.065 | 0 | 0.04 | 0.065 | 0.0425 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 92689.2917 | 147409.1401 | 148644.6099 | 0 | 12515.9112 | 0 | 17038.2636 | 0 | 234604.05 | 652901.2664 | 5.713%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2409921.5835 | 1785288.4742 | 2435484.7629 | 0 | 325413.6904 | 0 | 417938.5826 | 668700.162 | 469208.1 | 8511955.3558 | 74.49%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 834203.6251 | 589636.5603 | 823262.4551 | 0 | 112643.2005 | 0 | 32072.0255 | 387846.094 | 136070.349 | 2915734.3095 | 25.51%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 3244125.2086 | 2374925.0345 | 3258747.218 | 0 | 438056.891 | 0 | 450010.6082 | 1056546.256 | 605278.449 | 11427689.6652 | 100%
Network Element 6
Bayswater-Sydney West and Regentville-Sydney West line cut-in near South Creek
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 5 (2 × conductor/phase SCST) | 330 | 4 | lot | 2656054.92 | 1701122.23 | 726159.84 | 0 | 251196.43 | 0 | 353300.02 | 657269.39 | 451544 | 6796646.83 | 63.94%
TRUE | TRUE | Baseline Cost | [6 empty] | 2656054.92 | 1701122.23 | 726159.84 | 0 | 251196.43 | 0 | 353300.02 | 657269.39 | 451544 | 6796646.83 | 63.94%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | -0.05 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 2656054.92 | 1905256.8976 | 813299.0208 | 0 | 281340.0016 | 0 | 395696.0224 | 624405.9205 | 451544 | 7127596.7829 | 67.05%
FALSE | FALSE | Known Risks: | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.04 | 0.09 | 0.065 | 0 | 0.04 | 0.065 | 0.0425 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 106242.1968 | 171473.1208 | 52864.4364 | 0 | 11253.6001 | 0 | 16817.081 | 0 | 451544 | 810194.435 | 7.622%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2762297.1168 | 2076730.0184 | 866163.4572 | 0 | 292593.6017 | 0 | 412513.1034 | 624405.9205 | 903088 | 7937791.2179 | 74.68%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 956179.7712 | 685892.4831 | 292787.6475 | 0 | 101282.4006 | 0 | 31655.6818 | 362155.4339 | 261895.52 | 2691848.9381 | 25.32%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 3718476.888 | 2762622.5015 | 1158951.1046 | 0 | 393876.0022 | 0 | 444168.7851 | 986561.3544 | 1164983.52 | 10629640.1559 | 100%
Network Element 7
|  | Sydney West substation | 330 kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | (blank) | 1 | lot | 195387.44 | 5938413.5 | 424172.39 | 873633.7 | 167315.29 | 169668.96 | 669261.18 | 18257.48 | 11845.34 | 8467955.28 | 49.58%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 1 | lot | 744701.45 | 506385.62 | 183106.28 | 111494.23 | 143507.57 | 29105.26 | 177375.35 | 0 | 0 | 1895675.76 | 11.1%
TRUE | TRUE | Baseline Cost | [6 empty] | 940088.89 | 6444799.12 | 607278.67 | 985127.93 | 310822.86 | 198774.22 | 846636.53 | 18257.48 | 11845.34 | 10363631.04 | 60.68%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02164 | 0.19984 | 0.19984 | 0.19984 | 0.1996 | 0.1996 | 0.291 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 960432.4136 | 7732727.7761 | 728637.2394 | 1181995.8955 | 372863.1029 | 238449.5543 | 1093007.7602 | 35602.086 | 11845.34 | 12355561.1681 | 72.34%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 40338.1614 | 773272.7776 | 72863.7239 | 47279.8358 | 14914.5241 | 15499.221 | 46999.3337 | 0 | 11845.34 | 1023012.9176 | 5.989%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1000770.5749 | 8506000.5538 | 801500.9634 | 1229275.7314 | 387777.627 | 253948.7753 | 1140007.0939 | 35602.086 | 23690.68 | 13378574.0856 | 78.33%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 307338.3723 | 2474472.8884 | 233163.9166 | 378238.6866 | 119316.1929 | 76303.8574 | 87440.6208 | 19225.1264 | 6396.4836 | 3701896.145 | 21.67%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 1308108.9473 | 10980473.4421 | 1034664.88 | 1607514.4179 | 507093.8199 | 330252.6327 | 1227447.7147 | 54827.2124 | 30087.1636 | 17080470.2307 | 100%
Network Element 8
|  | Bayswater - Eraring Overhead line | 500kV line double circuit line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 105 | km | 106691739.22 | 68434857.3 | 87788893.94 | 0 | 13291526.44 | 0 | 18319721.16 | 30005776.52 | 20554214.77 | 345086729.35 | 56.48%
TRUE | TRUE | Baseline Cost | [6 empty] | 106691739.22 | 68434857.3 | 87788893.94 | 0 | 13291526.44 | 0 | 18319721.16 | 30005776.52 | 20554214.77 | 345086729.35 | 56.48%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | Above 200 km | - | - | - | -0.03 | -0.04995 | -0.04995 | 0 | -0.04995 | -0.04995 | -0.06 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.015 | 0.13005 | 0.13005 | 0 | 0.05505 | 0.05505 | 0.1225 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 108292115.3083 | 77334810.4919 | 99205839.5969 | 0 | 14023224.9705 | 0 | 20563887.0021 | 58511264.214 | 20554214.77 | 398485356.3537 | 65.22%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 4981437.3042 | 9280177.259 | 9424554.7617 | 0 | 560928.9988 | 0 | 904811.0281 | 11702252.8428 | 20554214.77 | 57408376.9646 | 9.396%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 113273552.6125 | 86614987.7509 | 108630394.3586 | 0 | 14584153.9693 | 0 | 21468698.0302 | 70213517.0568 | 41108429.54 | 455893733.3183 | 74.62%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 38985161.511 | 27840531.7771 | 35714102.2549 | 0 | 5048360.9894 | 0 | 1645110.9602 | 33936533.2441 | 11921444.5666 | 155091245.3032 | 25.38%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 152258714.1235 | 114455519.528 | 144344496.6135 | 0 | 19632514.9587 | 0 | 23113808.9904 | 104150050.3009 | 53029874.1066 | 610984978.6215 | 100%
Network Element 9
|  | Bayswater Substation | 500kV Extension
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 2 | lot | 4243289.68 | 3120488.27 | 914638.19 | 445976.94 | 808255.47 | 163925.08 | 999003.76 | 0 | 0 | 10695577.39 | 31.47%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 7500 m2 footprint area and applicable control building | N/A | 1 | lot | 227954.07 | 6928211.61 | 494872.26 | 1019248.51 | 195202.94 | 197948.9 | 780811.75 | 27386.22 | 17768.01 | 9889404.27 | 29.1%
TRUE | TRUE | Baseline Cost | [6 empty] | 4471243.75 | 10048699.88 | 1409510.45 | 1465225.45 | 1003458.41 | 361873.98 | 1779815.51 | 27386.22 | 17768.01 | 20584981.66 | 60.57%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04664 | 0.23484 | 0.23484 | 0.22484 | 0.2346 | 0.2346 | 0.326 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 4679782.5585 | 12408536.5598 | 1740519.8841 | 1794666.7402 | 1238869.753 | 446769.6157 | 2360035.3663 | 53403.129 | 17768.01 | 24740351.6165 | 72.79%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 196550.8675 | 1240853.656 | 174051.9884 | 71786.6696 | 49554.7901 | 29040.025 | 101481.5207 | 0 | 17768.01 | 1881087.5273 | 5.535%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 4876333.426 | 13649390.2158 | 1914571.8725 | 1866453.4098 | 1288424.5431 | 475809.6407 | 2461516.887 | 53403.129 | 35536.02 | 26621439.1439 | 78.33%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1497530.4187 | 3970731.6991 | 556966.3629 | 574293.3569 | 396438.321 | 142966.277 | 188802.8293 | 28837.6897 | 9594.7254 | 7366161.68 | 21.67%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 6373863.8447 | 17620121.9149 | 2471538.2354 | 2440746.7666 | 1684862.8641 | 618775.9178 | 2650319.7163 | 82240.8187 | 45130.7454 | 33987600.8238 | 100%
Network Element 10
|  | Eraring Substation | 500/330kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 6314190.58 | 3537434.66 | 1300501.18 | 668965.4 | 1088247.6 | 220711.25 | 1345074.04 | 0 | 0 | 14475124.71 | 7.044%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 2 | ea. | 48535730.23 | 7145610.87 | 4018215.18 | 222988.47 | 1982411.49 | 502574.63 | 0 | 0 | 0 | 62407530.87 | 30.37%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 2 | lot | 2847145.88 | 1963018.4 | 622382.71 | 445976.94 | 545738.62 | 110683.13 | 674532.94 | 0 | 0 | 7209478.62 | 3.508%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 25000 m2 footprint area and applicable control building | (blank) | 2 | lot | 1040483.7 | 31623436.81 | 2258816.91 | 4652303.18 | 890992.96 | 903526.77 | 3563971.85 | 182574.83 | 118453.43 | 45234560.44 | 22.01%
TRUE | TRUE | Baseline Cost | [6 empty] | 58737550.39 | 44269500.74 | 8199915.98 | 5990233.99 | 4507390.67 | 1737495.78 | 5583578.83 | 182574.83 | 118453.43 | 129326694.64 | 62.94%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 16 - 20 | - | - | - | 0.00164 | 0.00984 | 0.00984 | 0.00984 | 0.0096 | 0.0096 | 0.1 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04664 | 0.23484 | 0.23484 | 0.22484 | 0.2346 | 0.2346 | 0.326 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 61477069.7402 | 54665750.2938 | 10125584.2487 | 7337078.2003 | 5564824.5212 | 2145112.29 | 7403825.5286 | 356020.9185 | 118453.43 | 149193719.1713 | 72.6%
FALSE | FALSE | Known Risks: | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 2582036.9291 | 5466575.0294 | 1012558.4249 | 293483.128 | 222592.9808 | 139432.2988 | 318364.4977 | 71204.1837 | 118453.43 | 10224700.9025 | 4.976%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 64059106.6693 | 60132325.3232 | 11138142.6736 | 7630561.3283 | 5787417.502 | 2284544.5888 | 7722190.0263 | 427225.1022 | 236906.86 | 159418420.0738 | 77.58%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 19672662.3169 | 17493040.094 | 3240186.9596 | 2347865.0241 | 1780743.8468 | 686435.9328 | 592306.0423 | 192251.296 | 63964.8522 | 46069456.3646 | 22.42%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 83731768.9861 | 77625365.4172 | 14378329.6332 | 9978426.3524 | 7568161.3488 | 2970980.5216 | 8314496.0686 | 619476.3982 | 300871.7122 | 205487876.4384 | 100%