## OutputA
Project Name: CNSW-SNW Option 4 | [5 empty] | Indirect Cost Selection
Project Description: (Pre-requisite: CNSW-SNW Option 1, N3 REZ Option 1) • A new 500 kV substation near Eraring. • A new 500 kV double circuit line between substation near Eraring and Eraring. • A new 500 kV double circuit line between Wollar South and new Eraring substation with Quad Orange conductor • Two 500/330 kV 1,500 MVA transformers at Kemps Creek. • 1 x 330 kV SCST line between Vales Pt and new Eraring. • 1 x 330 kV SCST line between Vales Pt and Munmorah. • Thermal upgrade for Line 24 Vales Pt – Eraring and 92 Newcastle – Vales Point. • 1 x 330 kV SCST line between Liddell – Newcastle. • 1 x 330 kV SCST line between Eraring – Newcastle. • Line reactors on 500 kV transmission lines | [5 empty] | Total Network Elements Cost Category |  |  | Above $1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Highly sensitive
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  | 15-10-2021
[6 empty] | Project file |  | CNSW-SNW Option 4 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[6 empty] | Release Date |  | 4499500%
[6 empty] | Version Number |  | 4-0
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Eraring - new substation near Eraring | 31491759.7783 | 7464712.9366 | 6269936.4525 | 7907271.0881 | 0 | 1085474.6584 | 0 | 1279606.3457 | 4959526.2015 | 2525232.0954
2 | Eraring Substation | 49521053.1812 | 7147229.6004 | 27704192.3956 | 3330961.8067 | 4128839.3041 | 1998623.5874 | 921866.0727 | 3949682.8547 | 219308.8798 | 120348.6798
3 | Near Eraring new substation | 113529752.4336 | 28417460.7951 | 55445175.2335 | 7583952.5684 | 7738446.6261 | 4451743.0727 | 1862424.7423 | 7436148.6523 | 383790.5471 | 210610.196
4 | Kemps Creek Substation | 135090619.1628 | 75438382.6194 | 34942565.0516 | 10033154.2512 | 3964312.9172 | 5236816.7715 | 1644871.6534 | 3575772.715 | 164481.6674 | 90261.5162
5 | Vales Pt - New Eraring | 115372629.2736 | 27804774.1295 | 26723492.4299 | 9388937.2485 | 0 | 3309071.3884 | 0 | 5076715.9308 | 28517275.676 | 14552362.4706
6 | Vales Pt - Munmorah | 30766034.4886 | 7414606.4365 | 7126264.6582 | 2503716.6034 | 0 | 882419.0358 | 0 | 1353790.9139 | 7604606.8539 | 3880629.987
7 | Liddell-Newcastle | 384575430.9119 | 92682580.4122 | 89078308.1126 | 31296457.4949 | 0 | 11030237.9726 | 0 | 16922386.431 | 95057585.5866 | 48507874.902
8 | Vales Pt substation | 29459596.0089 | 6113583.3682 | 14018413.0568 | 2224862.4927 | 2537829.7398 | 1482933.8776 | 533608.9756 | 2463450.1221 | 54827.2124 | 30087.1636
9 | Munmorah substation | 19968243.4035 | 2256356.9972 | 11886666.7703 | 1263167.8288 | 1804124.193 | 723888.8569 | 376834.585 | 1572289.7964 | 54827.2124 | 30087.1636
10 | Newcastle substation | 20263583.5393 | 2348104.7109 | 11940367.0191 | 1357680.2702 | 1804124.193 | 747151.8277 | 381639.3528 | 1599601.7897 | 54827.2124 | 30087.1636
11 | Thermal upgrade for Vales Pt – Eraring and Newcastle – Vales Pt | 50542979.9579 | 18007902.2188 | 0 | 20342697.3717 | 0 | 0 | 0 | 12192380.3674 | 0 | 0
12 | Eraring-Newcastle | 76915086.1896 | 18536516.0766 | 17815661.6264 | 6259291.499 | 0 | 2206047.598 | 0 | 3384477.2921 | 19011517.1173 | 9701574.9804
13 | Wollar South - new substation near Eraring | 1196686872.1932 | 283659091.621 | 238257585.0803 | 300476301.4227 | 0 | 41248037.0554 | 0 | 48625041.3863 | 188461995.7958 | 95958819.8316
14 | Wollar South substation | 60440343.9545 | 20740595.9642 | 25653251.245 | 4099803.9912 | 3217275.0206 | 2416121.9146 | 870222.2701 | 3273244.7412 | 109654.4549 | 60174.3526
| Total Network Element Cost | 2314623984.477 | 598031897.8867 | 566861879.1318 | 408068255.9374 | 25194951.9937 | 76818567.6168 | 6591467.652 | 112704589.3384 | 344654224.4176 | 175698150.5024
Indirect Costs
| Project Development | 51153190.06
| Works Delivery | 63189234.78
| Land and Environment | 12036044.72
| Stakeholder and Community Engagement | 15797308.69
| Procurement Costs | 7522527.95
| Insurance | 6018022.36
| Total Indirect Cost | 155716328.56
| Total Expected Project Cost | 2470340313.03

## OutputB
Project Name: CNSW-SNW Option 4 |  |  |  |  | Indirect Cost Selection
Project Description: (Pre-requisite: CNSW-SNW Option 1, N3 REZ Option 1) • A new 500 kV substation near Eraring. • A new 500 kV double circuit line between substation near Eraring and Eraring. • A new 500 kV double circuit line between Wollar South and new Eraring substation with Quad Orange conductor • Two 500/330 kV 1,500 MVA transformers at Kemps Creek. • 1 x 330 kV SCST line between Vales Pt and new Eraring. • 1 x 330 kV SCST line between Vales Pt and Munmorah. • Thermal upgrade for Line 24 Vales Pt – Eraring and 92 Newcastle – Vales Point. • 1 x 330 kV SCST line between Liddell – Newcastle. • 1 x 330 kV SCST line between Eraring – Newcastle. • Line reactors on 500 kV transmission lines |  |  |  |  | Total Network Elements Cost Category |  |  | Above $1500 million
[5 empty] | Greenfield or Brownfield |  |  | Brownfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Highly sensitive
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. |  |  |  |  | TCD Cost Estimation Tool Version
[5 empty] | Tool Version |  | 15-10-2021
[5 empty] | Project file |  | CNSW-SNW Option 4 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[5 empty] | Release Date |  | 4499500%
[5 empty] | Version Number |  | 4-0
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 579799276.99 | 204218334.38 | 166737159.97 | 56039184.65 | 13308135.19 | 19663751.63 | 3400710.56 | 40536026.09 | 45009458.57 | 30886515.95
Adjusted Baseline Cost | 709402848.9769 | 211639021.1588 | 209148612.2749 | 71565575.7301 | 16160056.5979 | 23989307.8148 | 4130863.0916 | 54114452.1473 | 87768444.2115 | 30886515.95
Known Risk Allowance | 91725335.8543 | 9377917.3871 | 22901532.3529 | 6889552.8606 | 646402.2639 | 959572.3126 | 268506.101 | 2362694.8919 | 17432641.7343 | 30886515.95
Unknown Risk Allowance | 256368583.4981 | 72615271.7555 | 70900898.1788 | 25037021.9327 | 5171218.1113 | 8205528.5194 | 1321876.1893 | 4329156.1718 | 50881488.2211 | 17906124.4182
Total Network Element Cost | 1057496768.3292 | 293632210.3014 | 302951042.8065 | 103492150.5235 | 21977676.9731 | 33154408.6468 | 5721245.3819 | 60806303.2109 | 156082574.1669 | 79679156.3182
Indirect Costs:
Project Development | 51153190.0569
Works Delivery | 63189234.7762
Land and Environment | 12036044.7193
Stakeholder and Community Engagement | 15797308.6941
Procurement Costs | 7522527.9496
Insurance | 6018022.3596
Total Indirect Cost | 155716328.5557
Total Expected Project Cost | 1213213096.8849

## OutputC
Project Name: CNSW-SNW Option 4
Project Description: (Pre-requisite: CNSW-SNW Option 1, N3 REZ Option 1) • A new 500 kV substation near Eraring. • A new 500 kV double circuit line between substation near Eraring and Eraring. • A new 500 kV double circuit line between Wollar South and new Eraring substation with Quad Orange conductor • Two 500/330 kV 1,500 MVA transformers at Kemps Creek. • 1 x 330 kV SCST line between Vales Pt and new Eraring. • 1 x 330 kV SCST line between Vales Pt and Munmorah. • Thermal upgrade for Line 24 Vales Pt – Eraring and 92 Newcastle – Vales Point. • 1 x 330 kV SCST line between Liddell – Newcastle. • 1 x 330 kV SCST line between Eraring – Newcastle. • Line reactors on 500 kV transmission lines
Project Cost Estimate - View C
|  | View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[8 empty] | Tool Version |  | 15-10-2021
[8 empty] | Project file |  | CNSW-SNW Option 4 - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[8 empty] | Release Date |  | 4499500%
[8 empty] | Version Number |  | 4-0
Network Element 1
|  | Eraring - new substation near Eraring | 500 kV DCST overhead line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 5 | km | 5080559.01 | 3258802.73 | 4180423.52 | 0 | 632929.83 | 0 | 872367.67 | 1428846.5 | 978772.13 | 16432701.39 | 52.18%
TRUE | TRUE | Baseline Cost | [6 empty] | 5080559.01 | 3258802.73 | 4180423.52 | 0 | 632929.83 | 0 | 872367.67 | 1428846.5 | 978772.13 | 16432701.39 | 52.18%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 5309184.1654 | 4236443.549 | 5434550.576 | 0 | 775339.0417 | 0 | 1138439.8093 | 2786250.675 | 978772.13 | 20658979.9466 | 65.6%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 244222.4716 | 508373.2259 | 516282.3047 | 0 | 31013.5617 | 0 | 50091.3516 | 557250.135 | 978772.13 | 2886005.1805 | 9.164%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 5553406.6371 | 4744816.7749 | 5950832.8807 | 0 | 806352.6034 | 0 | 1188531.161 | 3343500.81 | 1957544.26 | 23544985.127 | 74.77%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1911306.2996 | 1525119.6776 | 1956438.2074 | 0 | 279122.055 | 0 | 91075.1847 | 1616025.3915 | 567687.8354 | 7946774.6512 | 25.23%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 7464712.9366 | 6269936.4525 | 7907271.0881 | 0 | 1085474.6584 | 0 | 1279606.3457 | 4959526.2015 | 2525232.0954 | 31491759.7783 | 100%
Network Element 2
|  | Eraring Substation | 500 kV Extension
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 1 | lot | 3157095.29 | 1768717.33 | 650250.59 | 334482.7 | 544123.8 | 110355.62 | 672537.02 | 0 | 0 | 7237562.35 | 14.62%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 1423572.94 | 981509.2 | 311191.35 | 222988.47 | 272869.31 | 55341.57 | 337266.47 | 0 | 0 | 3604739.31 | 7.279%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | N/A | 1 | lot | 425245.1 | 12924480.74 | 923177.2 | 1901393.68 | 364148.32 | 369270.88 | 1456593.28 | 73029.93 | 47381.37 | 18484720.5 | 37.33%
TRUE | TRUE | Baseline Cost | [6 empty] | 5005913.33 | 15674707.27 | 1884619.14 | 2458864.85 | 1181141.43 | 534968.07 | 2466396.77 | 73029.93 | 47381.37 | 29327022.16 | 59.22%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04828 | 0.24468 | 0.24468 | 0.23468 | 0.2442 | 0.2442 | 0.426 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 5247598.8256 | 19509994.6448 | 2345747.7512 | 3035911.253 | 1469576.1672 | 665607.2727 | 3517081.794 | 142408.3635 | 47381.37 | 35981307.442 | 72.66%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 220399.1507 | 1950999.4645 | 234574.7751 | 121436.4501 | 58783.0467 | 43264.4727 | 151234.5171 | 0 | 47381.37 | 2828073.247 | 5.711%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 5467997.9762 | 21460994.1093 | 2580322.5263 | 3157347.7031 | 1528359.2139 | 708871.7454 | 3668316.3112 | 142408.3635 | 94762.74 | 38809380.6889 | 78.37%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1679231.6242 | 6243198.2863 | 750639.2804 | 971491.601 | 470264.3735 | 212994.3273 | 281366.5435 | 76900.5163 | 25585.9398 | 10711672.4922 | 21.63%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 7147229.6004 | 27704192.3956 | 3330961.8067 | 4128839.3041 | 1998623.5874 | 921866.0727 | 3949682.8547 | 219308.8798 | 120348.6798 | 49521053.1812 | 100%
Network Element 3
|  | Near Eraring new substation | 500kV bays
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 6314190.58 | 3537434.66 | 1300501.18 | 668965.4 | 1088247.6 | 220711.25 | 1345074.04 | 0 | 0 | 14475124.71 | 12.75%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 35000 m2 footprint area and applicable control building | N/A | 1 | lot | 737801.65 | 22424016.6 | 1601715.47 | 3298924.29 | 631798.53 | 640686.19 | 2527194.14 | 127802.38 | 82917.4 | 32072856.65 | 28.25%
TRUE | FALSE |  | Station | Secondary system building | Demountable building 10 × 3 × 4m size | N/A | 1 | ea. | 452580.99 | 157203.44 | 35728.05 | 66896.54 | 14092.97 | 14291.22 | 28185.95 | 0 | 0 | 768979.16 | 0.6773%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 9234440.11 | 3572805.43 | 655014.33 | 222988.47 | 277161.8 | 95274.81 | 0 | 0 | 0 | 14057684.95 | 12.38%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 2227247.07 | 1604904.2 | 510911.18 | 222988.47 | 422859.64 | 85761.62 | 522654.52 | 0 | 0 | 5597326.7 | 4.93%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 1423572.94 | 981509.2 | 311191.35 | 222988.47 | 272869.31 | 55341.57 | 337266.47 | 0 | 0 | 3604739.31 | 3.175%
TRUE | TRUE | Baseline Cost | [6 empty] | 20389833.34 | 32277873.53 | 4415061.56 | 4703751.64 | 2707029.85 | 1112066.66 | 4760375.12 | 127802.38 | 82917.4 | 70576711.48 | 62.17%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 20864508.6602 | 39045898.0518 | 5340811.6679 | 5690034.2839 | 3273340.4946 | 1344711.0053 | 6621681.7919 | 249214.641 | 82917.4 | 82513117.9965 | 72.68%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 876309.3637 | 3904589.8052 | 534081.1668 | 227601.3714 | 130933.6198 | 87406.2153 | 284732.3171 | 0 | 82917.4 | 6128571.2592 | 5.398%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 21740818.0239 | 42950487.8569 | 5874892.8347 | 5917635.6552 | 3404274.1144 | 1432117.2206 | 6906414.109 | 249214.641 | 165834.8 | 88641689.2557 | 78.08%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 6676642.7712 | 12494687.3766 | 1709059.7337 | 1820810.9708 | 1047468.9583 | 430307.5217 | 529734.5434 | 134575.9061 | 44775.396 | 24888063.1778 | 21.92%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 28417460.7951 | 55445175.2335 | 7583952.5684 | 7738446.6261 | 4451743.0727 | 1862424.7423 | 7436148.6523 | 383790.5471 | 210610.196 | 113529752.4336 | 100%
Network Element 4
|  | Kemps Creek Substation | 2x 500/330 kV TX's
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 1 | lot | 3157095.29 | 1768717.33 | 650250.59 | 334482.7 | 544123.8 | 110355.62 | 672537.02 | 0 | 0 | 7237562.35 | 5.358%
TRUE | FALSE |  | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 2 | ea. | 48535730.23 | 7145610.87 | 4018215.18 | 222988.47 | 1982411.49 | 502574.63 | 0 | 0 | 0 | 62407530.87 | 46.2%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 1 | lot | 2095587.14 | 1111261.58 | 435524.98 | 334482.7 | 367215.89 | 74476.32 | 453878.84 | 0 | 0 | 4872427.45 | 3.607%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 15000 m2 footprint area and applicable control building | (blank) | 1 | lot | 339437.12 | 10316517.37 | 736894.1 | 1517721.39 | 290668.74 | 294757.64 | 1162674.94 | 54772.45 | 35536.03 | 14748979.78 | 10.92%
TRUE | TRUE | Baseline Cost | [6 empty] | 54127849.78 | 20342107.15 | 5840884.85 | 2409675.26 | 3184419.92 | 982164.21 | 2289090.8 | 54772.45 | 35536.03 | 89266500.45 | 66.08%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 55387946.1229 | 24607440.1772 | 7065601.5853 | 2914935.9685 | 3850600.5673 | 1187632.9627 | 3184125.3028 | 106806.2775 | 35536.03 | 98340624.9943 | 72.8%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 2326293.7372 | 2460744.0177 | 706560.1585 | 116597.4387 | 154024.0227 | 77196.1426 | 136917.388 | 0 | 35536.03 | 6013868.9354 | 4.452%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 57714239.86 | 27068184.1949 | 7772161.7439 | 3031533.4073 | 4004624.59 | 1264829.1053 | 3321042.6908 | 106806.2775 | 71072.06 | 104354493.9297 | 77.25%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE |  | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 17724142.7593 | 7874380.8567 | 2260992.5073 | 932779.5099 | 1232192.1815 | 380042.5481 | 254730.0242 | 57675.3898 | 19189.4562 | 30736125.2331 | 22.75%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 75438382.6194 | 34942565.0516 | 10033154.2512 | 3964312.9172 | 5236816.7715 | 1644871.6534 | 3575772.715 | 164481.6674 | 90261.5162 | 135090619.1628 | 100%
Network Element 5
|  | Vales Pt - New Eraring | 330kV SCST
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 30 | km | 18924210.07 | 13889549.08 | 4963752.18 | 0 | 1929487.69 | 0 | 3461035.39 | 8215867.38 | 5640450.57 | 57024352.36 | 49.43%
TRUE | TRUE | Baseline Cost | [6 empty] | 18924210.07 | 13889549.08 | 4963752.18 | 0 | 1929487.69 | 0 | 3461035.39 | 8215867.38 | 5640450.57 | 57024352.36 | 49.43%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 19775799.5232 | 18056413.804 | 6452877.834 | 0 | 2363622.4202 | 0 | 4516651.1839 | 16020941.391 | 5640450.57 | 72826756.7264 | 63.12%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 909686.7781 | 2166769.6565 | 613023.3942 | 0 | 94544.8968 | 0 | 198732.6521 | 3204188.2782 | 5640450.57 | 12827396.2259 | 11.12%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 20685486.3012 | 20223183.4605 | 7065901.2282 | 0 | 2458167.3171 | 0 | 4715383.836 | 19225129.6692 | 11280901.14 | 85654152.9522 | 74.24%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 7119287.8283 | 6500308.9694 | 2323036.0202 | 0 | 850904.0713 | 0 | 361332.0947 | 9292146.0068 | 3271461.3306 | 29718476.3214 | 25.76%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 27804774.1295 | 26723492.4299 | 9388937.2485 | 0 | 3309071.3884 | 0 | 5076715.9308 | 28517275.676 | 14552362.4706 | 115372629.2736 | 100%
Network Element 6
|  | Vales Pt - Munmorah | 330kV SCST
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 8 | km | 5046456.02 | 3703879.76 | 1323667.25 | 0 | 514530.05 | 0 | 922942.77 | 2190897.97 | 1504120.15 | 15206493.97 | 49.43%
TRUE | TRUE | Baseline Cost | [6 empty] | 5046456.02 | 3703879.76 | 1323667.25 | 0 | 514530.05 | 0 | 922942.77 | 2190897.97 | 1504120.15 | 15206493.97 | 49.43%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 5273546.5409 | 4815043.688 | 1720767.425 | 0 | 630299.3113 | 0 | 1204440.3148 | 4272251.0415 | 1504120.15 | 19420468.4715 | 63.12%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 242583.1409 | 577805.2426 | 163472.9054 | 0 | 25211.9725 | 0 | 52995.3739 | 854450.2083 | 1504120.15 | 3420638.9934 | 11.12%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 5516129.6818 | 5392848.9306 | 1884240.3304 | 0 | 655511.2837 | 0 | 1257435.6887 | 5126701.2498 | 3008240.3 | 22841107.4649 | 74.24%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1898476.7547 | 1733415.7277 | 619476.273 | 0 | 226907.7521 | 0 | 96355.2252 | 2477905.6041 | 872389.687 | 7924927.0237 | 25.76%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 7414606.4365 | 7126264.6582 | 2503716.6034 | 0 | 882419.0358 | 0 | 1353790.9139 | 7604606.8539 | 3880629.987 | 30766034.4886 | 100%
Network Element 7
|  | Liddell-Newcastle | 330kV SCST
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 100 | km | 63080700.22 | 46298496.94 | 16545840.6 | 0 | 6431625.64 | 0 | 11536784.63 | 27386224.6 | 18801501.9 | 190081174.53 | 49.43%
TRUE | TRUE | Baseline Cost | [6 empty] | 63080700.22 | 46298496.94 | 16545840.6 | 0 | 6431625.64 | 0 | 11536784.63 | 27386224.6 | 18801501.9 | 190081174.53 | 49.43%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 65919331.7299 | 60188046.022 | 21509592.78 | 0 | 7878741.409 | 0 | 15055503.9422 | 53403137.97 | 18801501.9 | 242755855.753 | 63.12%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 3032289.2596 | 7222565.5226 | 2043411.3141 | 0 | 315149.6564 | 0 | 662442.1735 | 10680627.594 | 18801501.9 | 42757987.4201 | 11.12%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 68951620.9895 | 67410611.5446 | 23553004.0941 | 0 | 8193891.0654 | 0 | 15717946.1156 | 64083765.564 | 37603003.8 | 285513843.1732 | 74.24%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 23730959.4228 | 21667696.5679 | 7743453.4008 | 0 | 2836346.9072 | 0 | 1204440.3154 | 30973820.0226 | 10904871.102 | 99061587.7387 | 25.76%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 92682580.4122 | 89078308.1126 | 31296457.4949 | 0 | 11030237.9726 | 0 | 16922386.431 | 95057585.5866 | 48507874.902 | 384575430.9119 | 100%
Network Element 8
|  | Vales Pt substation | 330 kV bays
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 330 | 2 | lot | 4191174.29 | 2222523.17 | 871049.96 | 668965.4 | 734431.78 | 148952.64 | 907757.68 | 0 | 0 | 9744854.92 | 33.08%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 195387.44 | 5938413.5 | 424172.39 | 873633.7 | 167315.29 | 169668.96 | 669261.18 | 18257.48 | 11845.34 | 8467955.28 | 28.74%
TRUE | TRUE | Baseline Cost | [6 empty] | 4386561.73 | 8160936.67 | 1295222.35 | 1542599.1 | 901747.07 | 318621.6 | 1577018.86 | 18257.48 | 11845.34 | 18212810.2 | 61.82%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 4488680.8871 | 9872121.871 | 1566804.5723 | 1866051.2793 | 1090392.557 | 385277.2387 | 2193633.2343 | 35602.086 | 11845.34 | 21510409.0657 | 73.02%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 188524.5973 | 987212.1871 | 156680.4572 | 74642.0512 | 43615.7023 | 25043.0205 | 94326.2291 | 0 | 11845.34 | 1581889.5846 | 5.37%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 4677205.4843 | 10859334.0581 | 1723485.0296 | 1940693.3305 | 1134008.2593 | 410320.2592 | 2287959.4633 | 35602.086 | 23690.68 | 23092298.6503 | 78.39%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1436377.8839 | 3159078.9987 | 501377.4632 | 597136.4094 | 348925.6183 | 123288.7164 | 175490.6587 | 19225.1264 | 6396.4836 | 6367297.3585 | 21.61%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 6113583.3682 | 14018413.0568 | 2224862.4927 | 2537829.7398 | 1482933.8776 | 533608.9756 | 2463450.1221 | 54827.2124 | 30087.1636 | 29459596.0089 | 100%
Network Element 9
|  | Munmorah substation | 330kV bays
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 195387.44 | 5938413.5 | 424172.39 | 873633.7 | 167315.29 | 169668.96 | 669261.18 | 18257.48 | 11845.34 | 8467955.28 | 42.41%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 1423572.94 | 981509.2 | 311191.35 | 222988.47 | 272869.31 | 55341.57 | 337266.47 | 0 | 0 | 3604739.31 | 18.05%
TRUE | TRUE | Baseline Cost | [6 empty] | 1618960.38 | 6919922.7 | 735363.74 | 1096622.17 | 440184.6 | 225010.53 | 1006527.65 | 18257.48 | 11845.34 | 12072694.59 | 60.46%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1656649.7776 | 8370892.0917 | 889554.809 | 1326561.9066 | 532271.2183 | 272082.7329 | 1400079.9612 | 35602.086 | 11845.34 | 14495539.9233 | 72.59%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 69579.2907 | 837089.2092 | 88955.4809 | 53062.4763 | 21290.8487 | 17685.3776 | 60203.4383 | 0 | 11845.34 | 1159711.4617 | 5.808%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1726229.0683 | 9207981.3009 | 978510.2899 | 1379624.3829 | 553562.0671 | 289768.1105 | 1460283.3995 | 35602.086 | 23690.68 | 15655251.385 | 78.4%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 530127.9288 | 2678685.4694 | 284657.5389 | 424499.8101 | 170326.7899 | 87066.4745 | 112006.3969 | 19225.1264 | 6396.4836 | 4312992.0185 | 21.6%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 2256356.9972 | 11886666.7703 | 1263167.8288 | 1804124.193 | 723888.8569 | 376834.585 | 1572289.7964 | 54827.2124 | 30087.1636 | 19968243.4035 | 100%
Network Element 10
|  | Newcastle substation | 330kV bays
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 1 | lot | 195387.44 | 5938413.5 | 424172.39 | 873633.7 | 167315.29 | 169668.96 | 669261.18 | 18257.48 | 11845.34 | 8467955.28 | 41.79%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 2 | lot | 1489402.91 | 1012771.25 | 366212.56 | 222988.47 | 287015.13 | 58210.53 | 354750.7 | 0 | 0 | 3791351.55 | 18.71%
TRUE | TRUE | Baseline Cost | [6 empty] | 1684790.35 | 6951184.75 | 790384.95 | 1096622.17 | 454330.42 | 227879.49 | 1024011.88 | 18257.48 | 11845.34 | 12259306.83 | 60.5%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1724012.2693 | 8408709.1684 | 956112.8663 | 1326561.9066 | 549376.3439 | 275551.8793 | 1424400.5251 | 35602.086 | 11845.34 | 14712172.3849 | 72.6%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 72408.5153 | 840870.9168 | 95611.2866 | 53062.4763 | 21975.0538 | 17910.8722 | 61249.2226 | 0 | 11845.34 | 1174933.6835 | 5.798%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1796420.7847 | 9249580.0852 | 1051724.1529 | 1379624.3829 | 571351.3976 | 293462.7515 | 1485649.7477 | 35602.086 | 23690.68 | 15887106.0684 | 78.4%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 551683.9262 | 2690786.9339 | 305956.1172 | 424499.8101 | 175800.43 | 88176.6014 | 113952.042 | 19225.1264 | 6396.4836 | 4376477.4709 | 21.6%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 2348104.7109 | 11940367.0191 | 1357680.2702 | 1804124.193 | 747151.8277 | 381639.3528 | 1599601.7897 | 54827.2124 | 30087.1636 | 20263583.5393 | 100%
Network Element 11
|  | Thermal upgrade for Vales Pt – Eraring and Newcastle – Vales Pt | Costed as Stage 2 development
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | Stage 2 development: 2 x Olive DCST 2212 MVA | 330 | 30 | km | 5656781.59 | 0 | 4963752.18 | 0 | 0 | 0 | 3836361.98 | 0 | 0 | 14456895.75 | 28.6%
TRUE | FALSE |  | Overhead line | HVAC | Stage 2 development: 2 x Olive DCST 2212 MVA | 330 | 35 | km | 6599578.52 | 0 | 5791044.21 | 0 | 0 | 0 | 4475755.64 | 0 | 0 | 16866378.37 | 33.37%
TRUE | TRUE | Baseline Cost | [6 empty] | 12256360.11 | 0 | 10754796.39 | 0 | 0 | 0 | 8312117.62 | 0 | 0 | 31323274.12 | 61.97%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 12807896.3149 | 0 | 13981235.307 | 0 | 0 | 0 | 10847313.4941 | 0 | 0 | 37636445.116 | 74.46%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 589163.2305 | 0 | 1328217.3542 | 0 | 0 | 0 | 477281.7937 | 0 | 0 | 2394662.3784 | 4.738%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 13397059.5454 | 0 | 15309452.6612 | 0 | 0 | 0 | 11324595.2878 | 0 | 0 | 40031107.4944 | 79.2%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 4610842.6734 | 0 | 5033244.7105 | 0 | 0 | 0 | 867785.0795 | 0 | 0 | 10511872.4634 | 20.8%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 18007902.2188 | 0 | 20342697.3717 | 0 | 0 | 0 | 12192380.3674 | 0 | 0 | 50542979.9579 | 100%
Network Element 12
|  | Eraring-Newcastle | 330kV SCST
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 20 | km | 12616140.04 | 9259699.39 | 3309168.12 | 0 | 1286325.13 | 0 | 2307356.93 | 5477244.92 | 3760300.38 | 38016234.91 | 49.43%
TRUE | TRUE | Baseline Cost | [6 empty] | 12616140.04 | 9259699.39 | 3309168.12 | 0 | 1286325.13 | 0 | 2307356.93 | 5477244.92 | 3760300.38 | 38016234.91 | 49.43%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 13183866.3418 | 12037609.207 | 4301918.556 | 0 | 1575748.2843 | 0 | 3011100.7936 | 10680627.594 | 3760300.38 | 48551171.1567 | 63.12%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 606457.8517 | 1444513.1048 | 408682.2628 | 0 | 63029.9314 | 0 | 132488.4349 | 2136125.5188 | 3760300.38 | 8551597.4845 | 11.12%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 13790324.1935 | 13482122.3118 | 4710600.8188 | 0 | 1638778.2156 | 0 | 3143589.2286 | 12816753.1128 | 7520600.76 | 57102768.6412 | 74.24%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 4746191.883 | 4333539.3145 | 1548690.6802 | 0 | 567269.3823 | 0 | 240888.0635 | 6194764.0045 | 2180974.2204 | 19812317.5485 | 25.76%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 18536516.0766 | 17815661.6264 | 6259291.499 | 0 | 2206047.598 | 0 | 3384477.2921 | 19011517.1173 | 9701574.9804 | 76915086.1896 | 100%
Network Element 13
|  | Wollar South - new substation near Eraring | 500kV DCST overhead line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 190 | km | 193061242.4 | 123834503.68 | 158856093.8 | 0 | 24051333.56 | 0 | 33149971.63 | 54296167.04 | 37193341.02 | 624442653.13 | 52.18%
TRUE | TRUE | Baseline Cost | [6 empty] | 193061242.4 | 123834503.68 | 158856093.8 | 0 | 24051333.56 | 0 | 33149971.63 | 54296167.04 | 37193341.02 | 624442653.13 | 52.18%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 100 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 100 to 200km | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.045 | 0.3 | 0.3 | 0 | 0.225 | 0.225 | 0.305 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 201748998.308 | 160984854.784 | 206512921.94 | 0 | 29462883.611 | 0 | 43260712.9771 | 105877525.728 | 37193341.02 | 785041238.3682 | 65.6%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.025 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.046 | 0.12 | 0.095 | 0 | 0.04 | 0.065 | 0.044 | 0.2 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 9280453.9222 | 19318182.5741 | 19618727.5843 | 0 | 1178515.3444 | 0 | 1903471.371 | 21175505.1456 | 37193341.02 | 109668196.9616 | 9.164%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 211029452.2302 | 180303037.3581 | 226131649.5243 | 0 | 30641398.9554 | 0 | 45164184.3481 | 127053030.8736 | 74386682.04 | 894709435.3297 | 74.77%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 72629639.3909 | 57954547.7222 | 74344651.8984 | 0 | 10606638.1 | 0 | 3460857.0382 | 61408964.9222 | 21572137.7916 | 301977436.8635 | 25.23%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 283659091.621 | 238257585.0803 | 300476301.4227 | 0 | 41248037.0554 | 0 | 48625041.3863 | 188461995.7958 | 95958819.8316 | 1196686872.1932 | 100%
Network Element 14
|  | Wollar South substation | 500kV bays and reactive support
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 1 | lot | 3157095.29 | 1768717.33 | 650250.59 | 334482.7 | 544123.8 | 110355.62 | 672537.02 | 0 | 0 | 7237562.35 | 11.97%
TRUE | FALSE |  | Station | Reactive Plant | Reactor 100MVAr | 500 | 2 | ea. | 9234440.11 | 3572805.43 | 655014.33 | 222988.47 | 277161.8 | 95274.81 | 0 | 0 | 0 | 14057684.95 | 23.26%
TRUE | FALSE |  | Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 2 | lot | 2227247.07 | 1604904.2 | 510911.18 | 222988.47 | 422859.64 | 85761.62 | 522654.52 | 0 | 0 | 5597326.7 | 9.261%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 10000 m2 footprint area and applicable control building | N/A | 1 | lot | 262817.9 | 7987828.29 | 570559.16 | 1175134.73 | 225057.73 | 228223.67 | 900230.91 | 36514.97 | 23690.69 | 11410058.05 | 18.88%
TRUE | TRUE | Baseline Cost | [6 empty] | 14881600.37 | 14934255.25 | 2386735.26 | 1955594.37 | 1469202.97 | 519615.72 | 2095422.45 | 36514.97 | 23690.69 | 38302632.05 | 63.37%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW - Central | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 50 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Urban | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.02328 | 0.20968 | 0.20968 | 0.20968 | 0.2092 | 0.2092 | 0.391 | 0.95 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 15228044.0266 | 18065669.8908 | 2887185.9093 | 2365643.3975 | 1776560.2313 | 628319.3286 | 2914732.628 | 71204.1915 | 23690.69 | 43961050.2937 | 72.73%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | High |  |  |  | 0 | 0.05 | 0.05 | 0 | 0 | 0.025 | 0.0025 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.1 | 0.1 | 0.04 | 0.04 | 0.065 | 0.043 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 639577.8491 | 1806566.9891 | 288718.5909 | 94625.7359 | 71062.4093 | 40840.7564 | 125333.503 | 0 | 23690.69 | 3090416.5236 | 5.113%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 15867621.8757 | 19872236.8799 | 3175904.5002 | 2460269.1334 | 1847622.6406 | 669160.085 | 3040066.131 | 71204.1915 | 47381.38 | 47051466.8173 | 77.85%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 4872974.0885 | 5781014.3651 | 923899.491 | 757005.8872 | 568499.274 | 201062.1852 | 233178.6102 | 38450.2634 | 12792.9726 | 13388877.1372 | 22.15%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 20740595.9642 | 25653251.245 | 4099803.9912 | 3217275.0206 | 2416121.9146 | 870222.2701 | 3273244.7412 | 109654.4549 | 60174.3526 | 60440343.9545 | 100%