## OutputA
Project Name: T2 North West Tasmania Option 1 prior to (without) Marinus Link | [5 empty] | Indirect Cost Selection
Project Description: • Build a new 220 kV switching station at Staverton and cut-in all Sheffield-Mersey Forth 220 kV lines at Staverton. • Build a new double-circuit Staverton–Hampshire Hills 220 kV line, and Hampshire Hills wind collector station (note this is part of the TAS-VIC Option 1 augmentations) | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Sensitive
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  | 15-10-2021
[6 empty] | Project file |  | REZ T2 Option 1 without (prior to) Marinus_30Aug - 15-10-2021.xlsb
Cost and Risk Data Version
[6 empty] | Release Date |  | 4499500%
[6 empty] | Version Number |  | 4-0
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Staverton - Hampshire Hills Transmission Line | 191014154.7221 | 55943750.942 | 40310417.3301 | 29082840.6891 | 0 | 5890687.9283 | 0 | 9131981.7522 | 44431941.4976 | 6222534.5829
2 | Staverton Substation | 52383379.4876 | 11510795.3065 | 23726842.1704 | 3792600.3548 | 4820218.1922 | 2573617.3061 | 923814.2183 | 4762080.3975 | 241144.8289 | 32266.713
3 | Hampshire Hills Substation | 23575970.6174 | 3286683.3145 | 13017499.6569 | 1493210.1547 | 2186495.1151 | 911336.0658 | 433190.0462 | 2064476.4614 | 166946.4428 | 16133.3599
4 | Staverton Line Diversion | 9252957.0564 | 2858349.4385 | 2513395.5609 | 1081674.0592 | 0 | 317147.9371 | 0 | 421652.1796 | 1807401.0045 | 253336.8765
| Total Network Element Cost | 276226461.8835 | 73599579.0015 | 79568154.7183 | 35450325.2577 | 7006713.3074 | 9692789.2373 | 1357004.2645 | 16380190.7907 | 46647433.7738 | 6524271.5323
Indirect Costs
| Project Development | 11049058.48
| Works Delivery | 4419623.39
| Land and Environment | 4695849.85
| Stakeholder and Community Engagement | 3038491.08
| Procurement Costs | 2762264.62
| Insurance | 1657358.77
| Total Indirect Cost | 27622646.19
| Total Expected Project Cost | 303849108.07

## OutputB
Project Name: T2 North West Tasmania Option 1 prior to (without) Marinus Link |  |  |  |  | Indirect Cost Selection
Project Description: • Build a new 220 kV switching station at Staverton and cut-in all Sheffield-Mersey Forth 220 kV lines at Staverton. • Build a new double-circuit Staverton–Hampshire Hills 220 kV line, and Hampshire Hills wind collector station (note this is part of the TAS-VIC Option 1 augmentations) |  |  |  |  | Total Network Elements Cost Category |  |  | $100-$500 million
[5 empty] | Greenfield or Brownfield |  |  | Greenfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Sensitive
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. |  |  |  |  | TCD Cost Estimation Tool Version
[5 empty] | Tool Version |  | 15-10-2021
[5 empty] | Project file |  | REZ T2 Option 1 without (prior to) Marinus_30Aug - 15-10-2021.xlsb
Cost and Risk Data Version
[5 empty] | Release Date |  | 4499500%
[5 empty] | Version Number |  | 4-0
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 181556136.69 | 55754485.06 | 54278393.6 | 23222207.15 | 5194918.86 | 6909276.85 | 997590.4 | 11806015.4 | 13895872.42 | 9497376.95
Adjusted Baseline Cost | 221028933.08 | 59783655.6474 | 64105466.0613 | 28272722.6352 | 5790672.1549 | 7927147.7824 | 1121491.1277 | 15012781.3242 | 36165783.262 | 2849213.085
Known Risk Allowance | 14358361.2099 | 3299048.1531 | 4526071.0254 | 2175165.1795 | 289533.6077 | 396357.3891 | 56074.5564 | 766898.2136 | 0 | 2849213.085
Unknown Risk Allowance | 40839167.5936 | 10516875.201 | 10936617.6316 | 5002437.443 | 926507.5448 | 1369284.0658 | 179438.5804 | 600511.253 | 10481650.5118 | 825845.3623
Total Network Element Cost | 276226461.8835 | 73599579.0015 | 79568154.7183 | 35450325.2577 | 7006713.3074 | 9692789.2373 | 1357004.2645 | 16380190.7907 | 46647433.7738 | 6524271.5323
Indirect Costs:
Project Development | 11049058.4753
Works Delivery | 4419623.3901
Land and Environment | 4695849.852
Stakeholder and Community Engagement | 3038491.0807
Procurement Costs | 2762264.6188
Insurance | 1657358.7713
Total Indirect Cost | 27622646.1883
Total Expected Project Cost | 303849108.0718

## OutputC
Project Name: T2 North West Tasmania Option 1 prior to (without) Marinus Link
Project Description: • Build a new 220 kV switching station at Staverton and cut-in all Sheffield-Mersey Forth 220 kV lines at Staverton. • Build a new double-circuit Staverton–Hampshire Hills 220 kV line, and Hampshire Hills wind collector station (note this is part of the TAS-VIC Option 1 augmentations)
Project Cost Estimate - View C
|  | View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[8 empty] | Tool Version |  | 15-10-2021
[8 empty] | Project file |  | REZ T2 Option 1 without (prior to) Marinus_30Aug - 15-10-2021.xlsb
Cost and Risk Data Version
[8 empty] | Release Date |  | 4499500%
[8 empty] | Version Number |  | 4-0
Network Element 1
|  | Staverton - Hampshire Hills Transmission Line | 220 kV DCST
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 x Sulphur DCST 1724 MVA | 220 | 59 | km | 41963595.79 | 25884987.27 | 18675295.64 | 0 | 4125243.92 | 0 | 6701470.98 | 13247448.27 | 9057546.7 | 119655588.57 | 62.64%
TRUE | TRUE | Baseline Cost | [6 empty] | 41963595.79 | 25884987.27 | 18675295.64 | 0 | 4125243.92 | 0 | 6701470.98 | 13247448.27 | 9057546.7 | 119655588.57 | 62.64%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | TAS - North West | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | -0.7
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 10 to 100 km | - | - | - | 0.0336 | 0.055944 | 0.055944 | 0 | 0.055944 | 0.055944 | 0.0672 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.00125 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0786 | 0.23594 | 0.23594 | 0 | 0.16094 | 0.16094 | 0.24845 | 1.6 | -0.7
TRUE | TRUE | Adjusted Baseline | [6 empty] | 45261934.4191 | 31992394.7064 | 23081619.5945 | 0 | 4789177.1775 | 0 | 8366451.445 | 34443365.502 | 2717264.01 | 150652206.8545 | 78.87%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | Tight |  |  |  | 0.05 | 0.05 | 0.05 | 0 | 0.05 | 0.05 | 0.05 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.056 | 0.08 | 0.08 | 0 | 0.05 | 0.05 | 0.0515 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 2534668.3275 | 2559391.5765 | 1846529.5676 | 0 | 239458.8589 | 0 | 430872.2494 | 0 | 2717264.01 | 10328184.5898 | 5.407%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 47796602.7466 | 34551786.2829 | 24928149.162 | 0 | 5028636.0363 | 0 | 8797323.6944 | 34443365.502 | 5434528.02 | 160980391.4443 | 84.28%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5a |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5a |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5a |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5a |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.14 | 0.14
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.29 | 0.29
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 8147148.1954 | 5758631.0472 | 4154691.527 | 0 | 862051.8919 | 0 | 334658.0578 | 9988575.9956 | 788006.5629 | 30033763.2778 | 15.72%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 55943750.942 | 40310417.3301 | 29082840.6891 | 0 | 5890687.9283 | 0 | 9131981.7522 | 44431941.4976 | 6222534.5829 | 191014154.7221 | 100%
Network Element 2
|  | Staverton Substation | 220 kV substation at Staverton
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work and building | AIS site infrastructure 20000 m2 footprint area and applicable control building | N/A | 1 | lot | 425245.1 | 12924480.74 | 923177.2 | 1901393.68 | 364148.32 | 369270.88 | 1456593.28 | 73029.93 | 47381.37 | 18484720.5 | 35.29%
TRUE | FALSE |  | Station | AIS Switchbay | 3CB Diameter 3CBs | 220 | 5 | lot | 8634696.77 | 4367754.64 | 1840887.97 | 1672413.51 | 1527825.04 | 309863.46 | 1888391.74 | 0 | 0 | 20241833.13 | 38.64%
TRUE | TRUE | Baseline Cost | [6 empty] | 9059941.87 | 17292235.38 | 2764065.17 | 3573807.19 | 1891973.36 | 679134.34 | 3344985.02 | 73029.93 | 47381.37 | 38726553.63 | 73.93%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | TAS - North West | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | -0.7
FALSE | FALSE |  | Station project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04828 | 0.12468 | 0.12468 | 0.11468 | 0.1242 | 0.1242 | 0.3055 | 1.6 | -0.7
TRUE | TRUE | Adjusted Baseline | [6 empty] | 9497355.8635 | 19448231.2872 | 3108688.8154 | 3983651.3985 | 2126956.4513 | 763482.825 | 4366877.9436 | 189877.818 | 14214.411 | 43499336.8136 | 83.04%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | Tight |  |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.052 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.0505 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 493862.5049 | 1166893.8772 | 186521.3289 | 199182.5699 | 106347.8226 | 38174.1413 | 220527.3362 | 0 | 14214.411 | 2425723.992 | 4.631%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 9991218.3684 | 20615125.1644 | 3295210.1443 | 4182833.9685 | 2233304.2739 | 801656.9663 | 4587405.2798 | 189877.818 | 28428.822 | 45925060.8055 | 87.67%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5a |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5a |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5a |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5a |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.12 | 0.12
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.27 | 0.27
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 1519576.9382 | 3111717.0059 | 497390.2105 | 637384.2238 | 340313.0322 | 122157.252 | 174675.1177 | 51267.0109 | 3837.891 | 6458318.6821 | 12.33%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 11510795.3065 | 23726842.1704 | 3792600.3548 | 4820218.1922 | 2573617.3061 | 923814.2183 | 4762080.3975 | 241144.8289 | 32266.713 | 52383379.4876 | 100%
Network Element 3
|  | Hampshire Hills Substation | New Hampshire Hills Wind Collector Station
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 2CB Diameter 2CBs | 220 | 2 | lot | 2324071.97 | 1499387.35 | 517699.5 | 445976.94 | 444903.4 | 90232.39 | 549900.6 | 0 | 0 | 5872172.15 | 24.91%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 10000 m2 footprint area and applicable control building | N/A | 1 | lot | 262817.9 | 7987828.29 | 570559.16 | 1175134.73 | 225057.73 | 228223.67 | 900230.91 | 36514.97 | 23690.69 | 11410058.05 | 48.4%
TRUE | TRUE | Baseline Cost | [6 empty] | 2586889.87 | 9487215.64 | 1088258.66 | 1621111.67 | 669961.13 | 318456.06 | 1450131.51 | 36514.97 | 23690.69 | 17282230.2 | 73.3%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Developed area | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | TAS - North West | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | -0.7
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 6 - 10 | - | - | - | 0.00328 | 0.01968 | 0.01968 | 0.01968 | 0.0192 | 0.0192 | 0.2 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.04828 | 0.12468 | 0.12468 | 0.11468 | 0.1242 | 0.1242 | 0.3055 | 2.6 | -0.7
TRUE | TRUE | Adjusted Baseline | [6 empty] | 2711784.9129 | 10670081.686 | 1223942.7497 | 1807020.7563 | 753170.3023 | 358008.3027 | 1893146.6863 | 131453.892 | 7107.207 | 19555716.4953 | 82.95%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | Tight |  |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.052 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.0505 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 141012.8155 | 640204.9012 | 73436.565 | 90351.0378 | 37658.5151 | 17900.4151 | 95603.9077 | 0 | 7107.207 | 1103275.3643 | 4.68%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2852797.7284 | 11310286.5872 | 1297379.3147 | 1897371.7941 | 790828.8175 | 375908.7178 | 1988750.594 | 131453.892 | 14214.414 | 20658991.8596 | 87.63%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5a |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5a |  |  |  | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5a |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5a |  |  |  | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.12 | 0.12
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.04 | 0.27 | 0.27
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 433885.5861 | 1707213.0698 | 195830.84 | 289123.321 | 120507.2484 | 57281.3284 | 75725.8675 | 35492.5508 | 1918.9459 | 2916978.7578 | 12.37%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 3286683.3145 | 13017499.6569 | 1493210.1547 | 2186495.1151 | 911336.0658 | 433190.0462 | 2064476.4614 | 166946.4428 | 16133.3599 | 23575970.6174 | 100%
Network Element 4
|  | Staverton Line Diversion | Line Diversion
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC line diversion | Type 5 (2 × conductor/phase SCST) | 220 | 4 | lot | 2144057.53 | 1613955.31 | 694587.68 | 0 | 222098.44 | 0 | 309427.89 | 538879.25 | 368758.19 | 5891764.29 | 63.67%
TRUE | TRUE | Baseline Cost | [6 empty] | 2144057.53 | 1613955.31 | 694587.68 | 0 | 222098.44 | 0 | 309427.89 | 538879.25 | 368758.19 | 5891764.29 | 63.67%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Delivery timetable | Long | - | - | - | 0.02 | 0.07 | 0.07 | 0 | 0.07 | 0.07 | 0.07 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Greenfield or brownfield | Greenfield | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | TAS - North West | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | -0.7
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Land Use | Grazing | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Location wind loading zones | Non-cyclone region | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 10 to 100 km | - | - | - | 0.0336 | 0.055944 | 0.055944 | 0 | 0.055944 | 0.055944 | 0.0672 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 25 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.00125 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Terrain | Hilly/Undulating | - | - | - | 0 | 0.075 | 0.075 | 0 | 0 | 0 | 0.075 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0786 | 0.23594 | 0.23594 | 0 | 0.16094 | 0.16094 | 0.24845 | 1.6 | -0.7
TRUE | TRUE | Adjusted Baseline | [6 empty] | 2312580.4519 | 1994758.3817 | 858471.4756 | 0 | 257843.8513 | 0 | 386305.2493 | 1401086.05 | 110627.457 | 7321672.9167 | 79.13%
FALSE | FALSE | Known Risks: | Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | BAU |  |  |  | 0.006 | 0.03 | 0.03 | 0 | 0 | 0 | 0.0015 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Environmental offset risks | High |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
FALSE | FALSE |  | Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Market activity | Tight |  |  |  | 0.05 | 0.05 | 0.05 | 0 | 0.05 | 0.05 | 0.05 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Project complexity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Weather delays | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.056 | 0.08 | 0.08 | 0 | 0.05 | 0.05 | 0.0515 | 0 | 1
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 129504.5053 | 159580.6705 | 68677.718 | 0 | 12892.1926 | 0 | 19894.7203 | 0 | 110627.457 | 501177.2638 | 5.416%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 2442084.9572 | 2154339.0522 | 927149.1936 | 0 | 270736.0439 | 0 | 406199.9696 | 1401086.05 | 221254.914 | 7822850.1805 | 84.54%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Productivity and labour cost risks | Class 5a |  |  |  | 0 | 0.04 | 0.04 | 0 | 0.04 | 0.04 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5a |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.15 | 0.15
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5a |  |  |  | 0.14 | 0.14 | 0.14 | 0 | 0.14 | 0.14 | 0 | 0.14 | 0.14
FALSE | FALSE |  | Overhead line unknown risk | Plant procurement cost risks | Class 5a |  |  |  | 0.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.18 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.04 | 0.29 | 0.29
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 416264.4813 | 359056.5087 | 154524.8656 | 0 | 46411.8932 | 0 | 15452.21 | 406314.9545 | 32081.9625 | 1430106.8759 | 15.46%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 2858349.4385 | 2513395.5609 | 1081674.0592 | 0 | 317147.9371 | 0 | 421652.1796 | 1807401.0045 | 253336.8765 | 9252957.0564 | 100%