## OutputA
Project Name: Latrobe Valley | [5 empty] | Indirect Cost Selection
Project Description: Augmentations include: (1) 4x 600 MVA power flow controllers, (2) 14.3 km of double-circuit 220 kV rated at 400 MVA per circuit | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  | 15-10-2021
[6 empty] | Project file |  | SEVIC Option 1 New latrobe_valley - 15-10-2021.xlsb
Cost and Risk Data Version
[6 empty] | Release Date |  | 4499500%
[6 empty] | Version Number |  | 4-0
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | HWTS 500/220 kV txfr power flow controllers | 154161098.2132 | 133870955.7472 | 11097610.0435 | 5360145.6563 | 519473.9397 | 2642894.6253 | 670018.2012 | 0 | 0 | 0
2 | new HWPS-YPS double-circuit 220kV line | 46289626.113 | 10483464.3809 | 9929544.0143 | 7741442.5096 | 1393677.93 | 2434150.6225 | 582991.4636 | 2374850.3183 | 9436673.8246 | 1912831.0493
3 | HWPS and YPS station works | 30410408.3202 | 2247176.0065 | 19934452.4438 | 1801242.2321 | 2304411.2539 | 911372.8959 | 614425.3856 | 2466625.4483 | 109617.9399 | 21084.7141
| Total Network Element Cost | 230861132.6465 | 146601596.1346 | 40961606.5016 | 14902830.398 | 4217563.1236 | 5988418.1437 | 1867435.0504 | 4841475.7666 | 9546291.7645 | 1933915.7634
Indirect Costs
| Project Development | 7849278.51
| Works Delivery | 9696167.57
| Land and Environment | 1846889.06
| Stakeholder and Community Engagement | 1616027.93
| Procurement Costs | 1154305.66
| Insurance | 923444.53
| Total Indirect Cost | 23086113.26
| Total Expected Project Cost | 253947245.91

## OutputB
Project Name: Latrobe Valley |  |  |  |  | Indirect Cost Selection
Project Description: Augmentations include: (1) 4x 600 MVA power flow controllers, (2) 14.3 km of double-circuit 220 kV rated at 400 MVA per circuit |  |  |  |  | Total Network Elements Cost Category |  |  | $100-$500 million
[5 empty] | Greenfield or Brownfield |  |  | Brownfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. |  |  |  |  | TCD Cost Estimation Tool Version
[5 empty] | Tool Version |  | 15-10-2021
[5 empty] | Project file |  | SEVIC Option 1 New latrobe_valley - 15-10-2021.xlsb
Cost and Risk Data Version
[5 empty] | Release Date |  | 4499500%
[5 empty] | Version Number |  | 4-0
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 185498252.42 | 128414971.9 | 28328357.44 | 10534277.48 | 3809910.73 | 4315388.82 | 1319248.87 | 3423180.85 | 3179977.27 | 2172939.06
Adjusted Baseline Cost | 196579392.4346 | 128888404.0507 | 33040813.6881 | 12302064.6662 | 4197583.3567 | 5001188.5955 | 1532869.3088 | 4488042.4256 | 6041956.813 | 1086469.53
Known Risk Allowance | 5024118.9158 | 4781105.5624 | -132419.7145 | 27457.4869 | 19979.7669 | 101649.7933 | 14662.1678 | -5610.053 | 0 | 217293.906
Unknown Risk Allowance | 29257621.2961 | 12932086.5215 | 8053212.528 | 2573308.245 | 0 | 885579.7549 | 319903.5738 | 359043.394 | 3504334.9515 | 630152.3274
Total Network Element Cost | 230861132.6465 | 146601596.1346 | 40961606.5016 | 14902830.398 | 4217563.1236 | 5988418.1437 | 1867435.0504 | 4841475.7666 | 9546291.7645 | 1933915.7634
Indirect Costs:
Project Development | 7849278.51
Works Delivery | 9696167.5712
Land and Environment | 1846889.0612
Stakeholder and Community Engagement | 1616027.9285
Procurement Costs | 1154305.6632
Insurance | 923444.5306
Total Indirect Cost | 23086113.2646
Total Expected Project Cost | 253947245.9111

## OutputC
Project Name: Latrobe Valley
Project Description: Augmentations include: (1) 4x 600 MVA power flow controllers, (2) 14.3 km of double-circuit 220 kV rated at 400 MVA per circuit
Project Cost Estimate - View C
|  | View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[8 empty] | Tool Version |  | 15-10-2021
[8 empty] | Project file |  | SEVIC Option 1 New latrobe_valley - 15-10-2021.xlsb
Cost and Risk Data Version
[8 empty] | Release Date |  | 4499500%
[8 empty] | Version Number |  | 4-0
Network Element 1
|  | HWTS 500/220 kV txfr power flow controllers | 4x HWTS >600MVA 500/220kV 40deg power flow controllers
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Power Flow Controller | Phase Shifting Transformer Angle ±40deg 750MVA 2 winding Tx (3ph assumed) | 500 | 4 | ea. | 119527639.06 | 9527481.15 | 4601773.4 | 445976.94 | 2268968.6 | 575221.67 | 0 | 0 | 0 | 136947060.82 | 88.83%
TRUE | TRUE | Baseline Cost | [6 empty] | 119527639.06 | 9527481.15 | 4601773.4 | 445976.94 | 2268968.6 | 575221.67 | 0 | 0 | 0 | 136947060.82 | 88.83%
FALSE | FALSE | Adjustments: | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC - Gippsland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | -0.5
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.9 | -0.5
TRUE | TRUE | Adjusted Baseline | [6 empty] | 119527639.06 | 10670778.888 | 5153986.208 | 499494.1728 | 2541244.832 | 644248.2704 | 0 | 0 | 0 | 139037391.4312 | 90.19%
FALSE | FALSE | Known Risks: | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 4781105.5624 | 426831.1555 | 206159.4483 | 19979.7669 | 101649.7933 | 25769.9308 | 0 | 0 | 0 | 5561495.6572 | 3.608%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 124308744.6224 | 11097610.0435 | 5360145.6563 | 519473.9397 | 2642894.6253 | 670018.2012 | 0 | 0 | 0 | 144598887.0884 | 93.8%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.08 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 9562211.1248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9562211.1248 | 6.203%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 133870955.7472 | 11097610.0435 | 5360145.6563 | 519473.9397 | 2642894.6253 | 670018.2012 | 0 | 0 | 0 | 154161098.2132 | 100%
Network Element 2
|  | new HWPS-YPS double-circuit 220kV line | >400 MVA per circuit, 1m/s wind speed, 14.3 km, HWPS-YPS double-circuit 220kV
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Overhead line | HVAC | 2 × Lemon DCST 892 MVA | 220 | 14.3 | km | 7281720.85 | 6142200.37 | 4431407.74 | 0 | 949547.72 | 0 | 1560853.89 | 3143462.3 | 2149248.37 | 25658441.24 | 55.43%
TRUE | FALSE |  | Station | Special Protection Scheme | Minor scheme | N/A | 1 | lot | 0 | 0 | 357280.54 | 1393677.93 | 528486.47 | 357280.54 | 234882.88 | 0 | 0 | 2871608.36 | 6.204%
TRUE | TRUE | Baseline Cost | [6 empty] | 7281720.85 | 6142200.37 | 4788688.28 | 1393677.93 | 1478034.19 | 357280.54 | 1795736.77 | 3143462.3 | 2149248.37 | 28530049.6 | 61.63%
FALSE | FALSE | Adjustments: | Overhead line project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Proportion of environmentally sensitive areas | 75 percent | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0.00375 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Jurisdiction | VIC - Gippsland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | -0.5
FALSE | FALSE |  | Overhead line project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Overhead line project attribute | Project network element size | 10 to 100 km | - | - | - | 0.0336 | 0.055944 | 0.055944 | 0 | 0.055944 | 0.055944 | 0.0672 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0586 | 0.21094 | 0.21094 | 0 | 0.21094 | 0.21094 | 0.22595 | 0.9 | -0.5
TRUE | TRUE | Adjusted Baseline | [6 empty] | 7708429.6918 | 7437860.6848 | 5798833.3405 | 1393677.93 | 1789816.6342 | 432646.7262 | 2201483.4932 | 5972578.37 | 1074624.185 | 33809951.0558 | 73.04%
FALSE | FALSE | Known Risks: | Overhead line known risk | Environmental offset risks | Low |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2
FALSE | FALSE |  | Overhead line known risk | Weather delays | Low |  |  |  | 0 | -0.025 | -0.025 | 0 | 0 | -0.0125 | -0.00125 | 0 | 0
FALSE | FALSE |  | Overhead line known risk | Cultural heritage | Low |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0 | -0.025 | -0.025 | 0 | 0 | -0.0125 | -0.00125 | 0 | 0.2
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 0 | -185946.5171 | -144970.8335 | 0 | 0 | -5408.0841 | -2751.8544 | 0 | 214924.837 | -124152.4521 | -0.2682%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 7708429.6918 | 7251914.1677 | 5653862.507 | 1393677.93 | 1789816.6342 | 427238.6422 | 2198731.6388 | 5972578.37 | 1289549.022 | 33685798.6037 | 72.77%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 2775034.6891 | 2677629.8465 | 2087580.0026 | 0 | 644333.9883 | 155752.8214 | 176118.6795 | 3464095.4546 | 623282.0273 | 12603827.5093 | 27.23%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 10483464.3809 | 9929544.0143 | 7741442.5096 | 1393677.93 | 2434150.6225 | 582991.4636 | 2374850.3183 | 9436673.8246 | 1912831.0493 | 46289626.113 | 100%
Network Element 3
|  | HWPS and YPS station works | station works to accomodate new line
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | AIS Switchbay | 1CB Diameter 1CB | 220 | 2 | lot | 1214837.1 | 781848.92 | 295471.01 | 222988.47 | 233755.44 | 47408.75 | 288921.72 | 0 | 0 | 3085231.41 | 10.15%
TRUE | FALSE |  | Station | Property site work and building | AIS site infrastructure 5000 m2 footprint area and applicable control building | N/A | 2 | lot | 390774.89 | 11876827 | 848344.79 | 1747267.39 | 334630.59 | 339337.91 | 1338522.36 | 36514.97 | 23690.69 | 16935910.59 | 55.69%
TRUE | TRUE | Baseline Cost | [6 empty] | 1605611.99 | 12658675.92 | 1143815.8 | 1970255.86 | 568386.03 | 386746.66 | 1627444.08 | 36514.97 | 23690.69 | 20021142 | 65.84%
FALSE | FALSE | Adjustments: | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | VIC - Gippsland | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | -0.5
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Brownfield | - | - | - | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0291 | 0.1796 | 0.1796 | 0.1696 | 0.179 | 0.179 | 0.405 | 0.9 | -0.5
TRUE | TRUE | Adjusted Baseline | [6 empty] | 1652335.2989 | 14932174.1152 | 1349245.1177 | 2304411.2539 | 670127.1294 | 455974.3121 | 2286558.9324 | 69378.443 | 11845.345 | 23732049.9476 | 78.04%
FALSE | FALSE | Known Risks: | Station known risk | Cultural heritage | Low |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | Low |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2
FALSE | FALSE |  | Station known risk | Weather delays | Low |  |  |  | 0 | -0.025 | -0.025 | 0 | 0 | -0.0125 | -0.00125 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0 | -0.025 | -0.025 | 0 | 0 | -0.0125 | -0.00125 | 0 | 0.2
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 0 | -373304.3529 | -33731.1279 | 0 | 0 | -5699.6789 | -2858.1987 | 0 | 2369.069 | -413224.2894 | -1.359%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 1652335.2989 | 14558869.7624 | 1315513.9897 | 2304411.2539 | 670127.1294 | 450274.6332 | 2283700.7337 | 69378.443 | 14214.414 | 23318825.6582 | 76.68%
FALSE | FALSE | Unknown Risks: | Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.28 | 0.28 | 0.28 | 0 | 0.28 | 0.28 | 0 | 0.28 | 0.28
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.36 | 0.36 | 0.36 | 0 | 0.36 | 0.36 | 0.08 | 0.58 | 0.58
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 594840.7076 | 5375582.6815 | 485728.2424 | 0 | 241245.7666 | 164150.7524 | 182924.7146 | 40239.4969 | 6870.3001 | 7091582.662 | 23.32%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 2247176.0065 | 19934452.4438 | 1801242.2321 | 2304411.2539 | 911372.8959 | 614425.3856 | 2466625.4483 | 109617.9399 | 21084.7141 | 30410408.3202 | 100%