## OutputA
Project Name: System Strength Mitigation | [5 empty] | Indirect Cost Selection
Project Description: Synchronous condenser- 125 MVA with flywheel | [5 empty] | Total Network Elements Cost Category |  |  | $50-$100 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
[6 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View A | [5 empty] | Contract Delivery Model |  |  | EPC contract
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface.
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  | 15-10-2021
[6 empty] | Project file |  | SC 125 MVA HI - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[6 empty] | Release Date |  | 4499500%
[6 empty] | Version Number |  | 4-0
Network Element Number | Network element | Total Network Element costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Synchronous condenser | 86472427.0168 | 68383230.729 | 10384893.2598 | 2419488.3281 | 1009506.2507 | 2474476.4116 | 1582236.3205 | 159293.4791 | 11246.6108 | 48055.6272
| Total Network Element Cost | 86472427.0168 | 68383230.729 | 10384893.2598 | 2419488.3281 | 1009506.2507 | 2474476.4116 | 1582236.3205 | 159293.4791 | 11246.6108 | 48055.6272
Indirect Costs
| Project Development | 3910283.15
| Works Delivery | 4830349.77
| Land and Environment | 920066.62
| Stakeholder and Community Engagement | 805058.3
| Procurement Costs | 575041.64
| Insurance | 460033.31
| Total Indirect Cost | 11500832.79
| Total Expected Project Cost | 97973259.81

## OutputB
Project Name: System Strength Mitigation |  |  |  |  | Indirect Cost Selection
Project Description: Synchronous condenser- 125 MVA with flywheel |  |  |  |  | Total Network Elements Cost Category |  |  | $50-$100 million
[5 empty] | Greenfield or Brownfield |  |  | Brownfield
[5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
Project Cost Estimate - View B |  |  |  |  | Contract Delivery Model |  |  | EPC contract
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. |  |  |  |  | TCD Cost Estimation Tool Version
[5 empty] | Tool Version |  | 15-10-2021
[5 empty] | Project file |  | SC 125 MVA HI - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[5 empty] | Release Date |  | 4499500%
[5 empty] | Version Number |  | 4-0
| Total Expected Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 60636472.35 | 48788215.02 | 6770466.29 | 1577393.6 | 668965.4 | 1625976.72 | 1039686.38 | 105697.29 | 36514.97 | 23556.68
Adjusted Baseline Cost | 63452399.5557 | 50207952.0771 | 7580214.0583 | 1766049.8746 | 742284.0078 | 1819467.9497 | 1163409.0592 | 142162.855 | 7302.994 | 23556.68
Known Risk Allowance | 2742589.5602 | 2108733.9872 | 379010.7029 | 88302.4937 | 29691.3603 | 72778.718 | 46536.3624 | 5757.5956 | 0 | 11778.34
Unknown Risk Allowance | 20277437.9009 | 16066544.6647 | 2425668.4987 | 565135.9599 | 237530.8825 | 582229.7439 | 372290.899 | 11373.0284 | 3943.6168 | 12720.6072
Total Network Element Cost | 86472427.0168 | 68383230.729 | 10384893.2598 | 2419488.3281 | 1009506.2507 | 2474476.4116 | 1582236.3205 | 159293.4791 | 11246.6108 | 48055.6272
Indirect Costs:
Project Development | 3910283.1497
Works Delivery | 4830349.7732
Land and Environment | 920066.6235
Stakeholder and Community Engagement | 805058.2955
Procurement Costs | 575041.6397
Insurance | 460033.3117
Total Indirect Cost | 11500832.7932
Total Expected Project Cost | 97973259.81

## OutputC
Project Name: System Strength Mitigation
Project Description: Synchronous condenser- 125 MVA with flywheel
Project Cost Estimate - View C
|  | View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[8 empty] | Tool Version |  | 15-10-2021
[8 empty] | Project file |  | SC 125 MVA HI - 4-0 - 15-10-2021.xlsb
Cost and Risk Data Version
[8 empty] | Release Date |  | 4499500%
[8 empty] | Version Number |  | 4-0
Network Element 1
|  | Synchronous condenser | System Strength Mitigation
Format $ | Format Bold |  | Category | Subcategory | Details | Nominal Voltage | Qty | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of total
TRUE | FALSE | Building Blocks: | Station | Property site work | GIS site infrastructure - Small area 100m × 100m | (blank) | 1 | lot | 0 | 1572034.39 | 17864.03 | 557471.17 | 88081.08 | 0 | 105697.29 | 36514.97 | 23556.68 | 2401219.61 | 2.777%
TRUE | FALSE |  | Station | Reactive Plant | Synchronous Condenser 125MVA with flywheel | 275 | 1 | ea. | 48788215.02 | 5198431.9 | 1559529.57 | 111494.23 | 1537895.64 | 1039686.38 | 0 | 0 | 0 | 58235252.74 | 67.35%
TRUE | TRUE | Baseline Cost | [6 empty] | 48788215.02 | 6770466.29 | 1577393.6 | 668965.4 | 1625976.72 | 1039686.38 | 105697.29 | 36514.97 | 23556.68 | 60636472.35 | 70.12%
FALSE | FALSE | Adjustments: | Station project attribute | Contract delivery model | EPC contract | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Greenfield or brownfield | Partly brownfield | - | - | - | 0 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0
FALSE | FALSE |  | Station project attribute | Jurisdiction | NSW | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Land Use | Scrub | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.8 | 0
FALSE | FALSE |  | Station project attribute | Location (regional/distance factors) | Regional | - | - | - | 0.025 | 0.035 | 0.035 | 0.025 | 0.035 | 0.035 | 0.035 | 0 | 0
FALSE | FALSE |  | Station project attribute | Project network element size | # of total Bays 1 - 5 | - | - | - | 0.0041 | 0.0246 | 0.0246 | 0.0246 | 0.024 | 0.024 | 0.25 | 0 | 0
FALSE | FALSE |  | Station project attribute | Proportion of environmentally sensitive areas | None | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station project attribute | Delivery timetable | Optimum | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE | Total Adjustment Rate % | [6 empty] | 0.0291 | 0.1196 | 0.1196 | 0.1096 | 0.119 | 0.119 | 0.345 | -0.8 | 0
TRUE | TRUE | Adjusted Baseline | [6 empty] | 50207952.0771 | 7580214.0583 | 1766049.8746 | 742284.0078 | 1819467.9497 | 1163409.0592 | 142162.855 | 7302.994 | 23556.68 | 63452399.5557 | 73.38%
FALSE | FALSE | Known Risks: | Station known risk | Compulsory acquisition | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Cultural heritage | BAU |  |  |  | 0.002 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0005 | 0 | 0
FALSE | FALSE |  | Station known risk | Environmental offset risks | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5
FALSE | FALSE |  | Station known risk | Geotechnical findings | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Macroeconomic influence | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Market activity | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Outage restrictions | BAU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station known risk | Project complexity | Partly complex |  |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0 | 0
FALSE | FALSE | Total Known Risk Rate % | [6 empty] | 0.042 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.0405 | 0 | 0.5
TRUE | TRUE | Total Known Risk Rate $ | [6 empty] | 2108733.9872 | 379010.7029 | 88302.4937 | 29691.3603 | 72778.718 | 46536.3624 | 5757.5956 | 0 | 11778.34 | 2742589.5602 | 3.172%
TRUE | TRUE | Subtotal Including Known Risks | [6 empty] | 52316686.0643 | 7959224.7612 | 1854352.3683 | 771975.3682 | 1892246.6677 | 1209945.4216 | 147920.4507 | 7302.994 | 35335.02 | 66194989.1159 | 76.55%
FALSE | FALSE | Unknown Risks: | Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0 | 0
FALSE | FALSE |  | Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0.3 | 0.3
FALSE | FALSE |  | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0 | 0.24 | 0.24
FALSE | FALSE | Total Unknown Risk Rate % | [6 empty] | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.08 | 0.54 | 0.54
TRUE | TRUE | Total Unknown Risk Rate $ | [6 empty] | 16066544.6647 | 2425668.4987 | 565135.9599 | 237530.8825 | 582229.7439 | 372290.899 | 11373.0284 | 3943.6168 | 12720.6072 | 20277437.9009 | 23.45%
TRUE | TRUE | Total Expected Network Element cost | [6 empty] | 68383230.729 | 10384893.2598 | 2419488.3281 | 1009506.2507 | 2474476.4116 | 1582236.3205 | 159293.4791 | 11246.6108 | 48055.6272 | 86472427.0168 | 100%