## outputA
Project Name: CNSW-SNW H-Newcastle | [5 empty] | Indirect Cost Selection
Project Description: To provide access to port new Newcastle: • Three new 500 kV lines from Bayswater to Newcastle. • Four new 500/330 kV transformers at Newcastle. • Line shunt reactors at each of the new 500 kV lines. | [5 empty] | Total Network Elements Cost Category |  |  | $1000-$1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View A | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | CNSW-SNW H-Newcastle.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element Number | Network Element | Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Bayswater Substation | 84556401.3 | 34123871.52 | 31635797.76 | 6506653.44 | 2243673.6 | 4531231.68 | 1599093.3 | 3916080 | 0 | 0
2 | Newcastle substation | 313639146.3739 | 141524094.24 | 107060518.656 | 22815487.296 | 13278376.32 | 11826353.28 | 5347839.56 | 11368653.7102 | 132199.6634 | 285623.6484
3 | Bayswater to Newcastle | 1073306123.3834 | 289143988.5965 | 281245840.5532 | 204542429.4918 | 0 | 35772110.066 | 0 | 138386931.4236 | 39301677.4965 | 84913145.7558
| Total Network Element Cost | 1471501671.0573 | 464791954.3565 | 419942156.9692 | 233864570.2278 | 15522049.92 | 52129695.026 | 6946932.86 | 153671665.1337 | 39433877.1599 | 85198769.4042
Indirect Costs
| Project Development | 64451773.1923
| Works Delivery | 72692182.5502
| Land and Environment | 8240409.3579
| Stakeholder and Community Engagement | 7210358.1882
| Procurement Costs | 5150255.8487
| Insurance | 4120204.679
| Total Indirect Cost | 161865183.8163
| Total Expected Project Cost | 1633366854.8736

## outputB
Project Name: CNSW-SNW H-Newcastle | [5 empty] | Indirect Cost Selection
Project Description: To provide access to port new Newcastle: • Three new 500 kV lines from Bayswater to Newcastle. • Four new 500/330 kV transformers at Newcastle. • Line shunt reactors at each of the new 500 kV lines. | [5 empty] | Total Network Elements Cost Category |  |  | $1000-$1500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View B | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | CNSW-SNW H-Newcastle.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
| Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 1115158613.72 | 347318990.13 | 277752222.42 | 151667070.85 | 10800000 | 35727575.78 | 4660000 | 127133207.7 | 17206674.29 | 142892872.55
Adjusted Baseline Cost | 1094813821.0957 | 335684336.4261 | 302872471.7094 | 167662132.9513 | 11413272 | 37579143.19 | 5015836 | 137206843.8694 | 30811048.1759 | 66568736.7736
Known Risk Allowance | 40022757.3458 | 13427373.457 | 12114898.8684 | 6706485.3181 | 456530.88 | 1503165.7276 | 326029.34 | 5488273.7548 | 0 | 0
Unknown Risk Allowance | 336665092.6157 | 115680244.4734 | 104954786.3914 | 59495951.9585 | 3652247.04 | 13047386.1084 | 1605067.52 | 10976547.5096 | 8622828.984 | 18630032.6305
Total Network Element Cost | 1471501671.0573 | 464791954.3565 | 419942156.9692 | 233864570.2278 | 15522049.92 | 52129695.026 | 6946932.86 | 153671665.1337 | 39433877.1599 | 85198769.4042
Indirect Costs
Project Development | 64451773.1923
Works Delivery | 72692182.5502
Land and Environment | 8240409.3579
Stakeholder and Community Engagement | 7210358.1882
Procurement Costs | 5150255.8487
Insurance | 4120204.679
Total Indirect Cost | 161865183.8163
Total Expected Project Cost | 1633366854.8736

## outputC
Project Name: CNSW-SNW H-Newcastle
Project Description: To provide access to port new Newcastle: • Three new 500 kV lines from Bayswater to Newcastle. • Four new 500/330 kV transformers at Newcastle. • Line shunt reactors at each of the new 500 kV lines.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | CNSW-SNW H-Newcastle.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element 1
Bayswater Substation
500 kV extension
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 3 | lot | 8100000 | 12150000 | 2700000 | 600000 | 1620000 | 600000 | 2100000 | 0 | 0 | 27870000 | 32.96%
| Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 3 | lot | 4050000 | 5400000 | 1350000 | 300000 | 810000 | 300000 | 1050000 | 0 | 0 | 13260000 | 15.68%
| Station | Reactive Plant | Reactor 100MVAr | 500 | 3 | ea. | 12900000 | 3600000 | 300000 | 600000 | 600000 | 150000 | 0 | 0 | 0 | 18150000 | 21.46%
Baseline Cost | [6 empty] | 25050000 | 21150000 | 4350000 | 1500000 | 3030000 | 1050000 | 3150000 | 0 | 0 | 59280000 | 70.11%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 16 - 20 |  |  |  | 0.164% | 0.984% | 0.984% | 0.984% | 0.96% | 0.96% | 2% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 0.164% | 9.984% | 9.984% | 9.984% | 9.96% | 9.96% | 11% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 25091082 | 23261616 | 4784304 | 1649760 | 3331788 | 1154580 | 3496500 | 0 | 0 | 62769630 | 74.23%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 1003643.28 | 930464.64 | 191372.16 | 65990.4 | 133271.52 | 75047.7 | 139860 | 0 | 0 | 2539649.7 | 3.003%
Subtotal Including Known Risks | [6 empty] | 26094725.28 | 24192080.64 | 4975676.16 | 1715750.4 | 3465059.52 | 1229627.7 | 3636360 | 0 | 0 | 65309279.7 | 77.24%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 8029146.24 | 7443717.12 | 1530977.28 | 527923.2 | 1066172.16 | 369465.6 | 279720 | 0 | 0 | 19247121.6 | 22.76%
Subtotal Including Unknown Risks | [6 empty] | 34123871.52 | 31635797.76 | 6506653.44 | 2243673.6 | 4531231.68 | 1599093.3 | 3916080 | 0 | 0 | 84556401.3 | 100%
Network Element 2
Newcastle substation
500/330 kV
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 4 | lot | 16200000 | 18000000 | 5400000 | 2400000 | 3240000 | 1200000 | 3360000 | 0 | 0 | 49800000 | 15.88%
| Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 4 | ea. | 70200000 | 11160000 | 5760000 | 800000 | 1440000 | 600000 | 0 | 0 | 0 | 89960000 | 28.68%
| Station | Property site work and building | AIS site infrastructure 25000 m2 footprint area and applicable control building | N/A | 2 | lot | 2400000 | 32160000 | 2400000 | 4800000 | 960000 | 960000 | 3766022.33 | 59538.67 | 494439.01 | 48000000.01 | 15.3%
| Station | Reactive Plant | Reactor 100MVAr | 500 | 3 | ea. | 12900000 | 3600000 | 300000 | 600000 | 600000 | 150000 | 0 | 0 | 0 | 18150000 | 5.787%
| Station | AIS Switchbay | 1CB Diameter 1CB | 500 | 3 | lot | 4050000 | 5400000 | 1350000 | 300000 | 810000 | 300000 | 1050000 | 0 | 0 | 13260000 | 4.228%
| Station | AIS Switchbay | 1CB Diameter 1CB | 330 | 4 | lot | 3600000 | 6120000 | 1080000 | 400000 | 1080000 | 400000 | 1400000 | 0 | 0 | 14080000 | 4.489%
Baseline Cost | [6 empty] | 109350000 | 76440000 | 16290000 | 9300000 | 8130000 | 3610000 | 9576022.33 | 59538.67 | 494439.01 | 233250000.01 | 74.37%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 16 - 20 |  |  |  | 0.164% | 0.984% | 0.984% | 0.984% | 0.96% | 0.96% | 2% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Station project attribute | Location (regional/distance factors) | Urban |  |  |  | -5% | -7% | -7% | -5% | -3% | -3% | -5% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -4.836% | 2.984% | 2.984% | 4.984% | 6.96% | 6.96% | 6% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 104061834 | 78720969.6 | 16776093.6 | 9763512 | 8695848 | 3861256 | 10150583.6698 | 106612.6317 | 230341.6519 | 232367051.1534 | 74.09%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 4% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 4162473.36 | 3148838.784 | 671043.744 | 390540.48 | 347833.92 | 250981.64 | 406023.3468 | 0 | 0 | 9377735.2748 | 2.99%
Subtotal Including Known Risks | [6 empty] | 108224307.36 | 81869808.384 | 17447137.344 | 10154052.48 | 9043681.92 | 4112237.64 | 10556607.0166 | 106612.6317 | 230341.6519 | 241744786.4282 | 77.08%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 33299786.88 | 25190710.272 | 5368349.952 | 3124323.84 | 2782671.36 | 1235601.92 | 812046.6936 | 25587.0316 | 55281.9965 | 71894359.9457 | 22.92%
Subtotal Including Unknown Risks | [6 empty] | 141524094.24 | 107060518.656 | 22815487.296 | 13278376.32 | 11826353.28 | 5347839.56 | 11368653.7102 | 132199.6634 | 285623.6484 | 313639146.3739 | 100%
Network Element 3
Bayswater to Newcastle
500 kV line
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 90 | km | 118453759.53 | 100230104.22 | 72894621.25 | 0 | 13667741.48 | 0 | 69044084.53 | 8573567.81 | 71199216.77 | 454063095.59 | 42.31%
| Overhead line | HVAC | 4 × Orange SCST 3062 MVA | 500 | 90 | km | 94465230.6 | 79932118.2 | 58132449.6 | 0 | 10899834.3 | 0 | 45363100.84 | 8573567.81 | 71199216.77 | 368565518.12 | 34.34%
Baseline Cost | [6 empty] | 212918990.13 | 180162222.42 | 131027070.85 | 0 | 24567575.78 | 0 | 114407185.37 | 17147135.62 | 142398433.54 | 822628613.71 | 76.64%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Optimum |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | Above 200 km |  |  |  | -3% | -4.995% | -4.995% | 0% | -4.995% | -4.995% | -6% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Central - Developed |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 79.06% | -53.41%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Hilly/Undulating |  |  |  | 0% | 7.5% | 7.5% | 0% | 0% | 0% | 5% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | -3% | 11.51% | 11.51% | 0% | 4.005% | 4.005% | 8% | 79.06% | -53.41%
Adjusted Baseline | [6 empty] | 206531420.4261 | 200889886.1094 | 146101735.3513 | 0 | 25551507.19 | 0 | 123559760.1996 | 30704435.5441 | 66338395.1218 | 799677139.9423 | 74.51%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | Partly complex |  |  |  | 4% | 4% | 4% | 0% | 4% | 4% | 4% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 4% | 4% | 4% | 0% | 4% | 6.5% | 4% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 8261256.817 | 8035595.4444 | 5844069.4141 | 0 | 1022060.2876 | 0 | 4942390.408 | 0 | 0 | 28105372.3711 | 2.619%
Subtotal Including Known Risks | [6 empty] | 214792677.2431 | 208925481.5538 | 151945804.7653 | 0 | 26573567.4776 | 0 | 128502150.6076 | 30704435.5441 | 66338395.1218 | 827782512.3134 | 77.12%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 74351311.3534 | 72320358.9994 | 52596624.7265 | 0 | 9198542.5884 | 0 | 9884780.816 | 8597241.9524 | 18574750.6341 | 245523611.0701 | 22.88%
Subtotal Including Unknown Risks | [6 empty] | 289143988.5965 | 281245840.5532 | 204542429.4918 | 0 | 35772110.066 | 0 | 138386931.4236 | 39301677.4965 | 84913145.7558 | 1073306123.3834 | 100%