## outputA
Project Name: SQ-CQ Option 6 | [5 empty] | Indirect Cost Selection
• New 500 kV Halys substation with 3 x 500/275 kV 1,500 MVA transformers • New 500 kV substations west of Gladstone (CQ 500 kV substation with 3 x 500/275 kV 1,500 MVA transformers • New 500 kV substation at Auburn River with 2 x 500/275 kV 1,500 MVA transformers • Raise the double-circuit line between Halys and Auburn River substations to 500 kV operation. • Raise the double-circuit line between Auburn River and Gladstone West substations to 500 kV operation • New dynamic reactive support at Gladstone (CQ) west substation | [5 empty] | Total Network Elements Cost Category |  |  | $500-$1000 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
Project Cost Estimate - View A | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | SQ-CQ Option 6.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element Number | Network Element | Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Auburn River 500/275kV Substation | 180880104.0907 | 76322842.168 | 65075023.872 | 13620003.84 | 8126853.12 | 6665519.76 | 3307223.52 | 7598011.3126 | 21487.4595 | 143139.0386
2 | Halys 500/275kV Substation | 239279098.122 | 103204846.832 | 86487975.216 | 17552307.6 | 9959914.08 | 8194808.64 | 4235988.6 | 9423755.1585 | 28649.944 | 190852.0515
3 | Gladstone West 500/275kV Substation | 280959731.282 | 133452542.312 | 89671882.176 | 19919828.16 | 12245796 | 11084213.28 | 4734340.2 | 9631627.1585 | 28649.944 | 190852.0515
| Total Network Element Cost | 701118933.4947 | 312980231.312 | 241234881.264 | 51092139.6 | 30332563.2 | 25944541.68 | 12277552.32 | 26653393.6297 | 78787.3474 | 524843.1416
Indirect Costs
| Project Development | 30148114.1403
| Works Delivery | 16686630.6172
| Land and Environment | 9535217.4955
| Stakeholder and Community Engagement | 18789987.4177
| Procurement Costs | 5608951.468
| Insurance | 3365370.8808
| Total Indirect Cost | 84134272.0194
| Total Expected Project Cost | 785253205.5141

## outputB
Project Name: SQ-CQ Option 6 | [5 empty] | Indirect Cost Selection
• New 500 kV Halys substation with 3 x 500/275 kV 1,500 MVA transformers • New 500 kV substations west of Gladstone (CQ 500 kV substation with 3 x 500/275 kV 1,500 MVA transformers • New 500 kV substation at Auburn River with 2 x 500/275 kV 1,500 MVA transformers • Raise the double-circuit line between Halys and Auburn River substations to 500 kV operation. • Raise the double-circuit line between Auburn River and Gladstone West substations to 500 kV operation • New dynamic reactive support at Gladstone (CQ) west substation | [5 empty] | Total Network Elements Cost Category |  |  | $500-$1000 million
[6 empty] | Greenfield or Brownfield |  |  | Greenfield
Project Cost Estimate - View B | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | SQ-CQ Option 6.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
| Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 461269999.98 | 215740000 | 151130000 | 32000000 | 19000000 | 16240000 | 7560000 | 18381249.12 | 130985.06 | 1087765.8
Adjusted Baseline Cost | 495710815.3547 | 220408613.6 | 169883719.2 | 35980380 | 21360960 | 18270804 | 8496576 | 20822963.7732 | 63538.1834 | 423260.5981
Known Risk Allowance | 51817112.4346 | 22040861.36 | 16988371.92 | 3598038 | 2136096 | 1827080.4 | 1062072 | 4164592.7546 | 0 | 0
Unknown Risk Allowance | 153591005.7054 | 70530756.352 | 54362790.144 | 11513721.6 | 6835507.2 | 5846657.28 | 2718904.32 | 1665837.1019 | 15249.164 | 101582.5435
Total Network Element Cost | 701118933.4947 | 312980231.312 | 241234881.264 | 51092139.6 | 30332563.2 | 25944541.68 | 12277552.32 | 26653393.6297 | 78787.3474 | 524843.1416
Indirect Costs
Project Development | 30148114.1403
Works Delivery | 16686630.6172
Land and Environment | 9535217.4955
Stakeholder and Community Engagement | 18789987.4177
Procurement Costs | 5608951.468
Insurance | 3365370.8808
Total Indirect Cost | 84134272.0194
Total Expected Project Cost | 785253205.5141

## outputC
Project Name: SQ-CQ Option 6
• New 500 kV Halys substation with 3 x 500/275 kV 1,500 MVA transformers • New 500 kV substations west of Gladstone (CQ 500 kV substation with 3 x 500/275 kV 1,500 MVA transformers • New 500 kV substation at Auburn River with 2 x 500/275 kV 1,500 MVA transformers • Raise the double-circuit line between Halys and Auburn River substations to 500 kV operation. • Raise the double-circuit line between Auburn River and Gladstone West substations to 500 kV operation • New dynamic reactive support at Gladstone (CQ) west substation
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | SQ-CQ Option 6.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element 1
Auburn River 500/275kV Substation
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 3 | lot | 12150000 | 13500000 | 4050000 | 1800000 | 2430000 | 900000 | 2520000 | 0 | 0 | 37350000 | 20.65%
| Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/275 | 2 | ea. | 35100000 | 5580000 | 2880000 | 400000 | 720000 | 300000 | 0 | 0 | 0 | 44980000 | 24.87%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 2 | lot | 3960000 | 5400000 | 720000 | 400000 | 720000 | 400000 | 840000 | 0 | 0 | 12440000 | 6.877%
| Station | Property site work and building | AIS site infrastructure 30000 m2 footprint area and applicable control building | N/A | 1 | lot | 1400000 | 18760000 | 1400000 | 2800000 | 560000 | 560000 | 2187613.4 | 35723.2 | 296663.4 | 28000000 | 15.48%
Baseline Cost | [6 empty] | 52610000 | 43240000 | 9050000 | 5400000 | 4430000 | 2160000 | 5547613.4 | 35723.2 | 296663.4 | 122770000 | 67.87%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 5% | 5% | 5% | 5% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Greenfield |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 16 - 20 |  |  |  | 0.164% | 0.984% | 0.984% | 0.984% | 0.96% | 0.96% | 2% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | QLD - South - Scrub |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -51.49% | -61.09%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 2.164% | 5.984% | 5.984% | 5.984% | 5.96% | 5.96% | 7% | -51.49% | -61.09%
Adjusted Baseline | [6 empty] | 53748480.4 | 45827481.6 | 9591552 | 5723136 | 4694028 | 2288736 | 5935946.338 | 17328.5963 | 115434.7086 | 127942123.6429 | 70.73%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 10% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 5374848.04 | 4582748.16 | 959155.2 | 572313.6 | 469402.8 | 286092 | 1187189.2676 | 0 | 0 | 13431749.0676 | 7.426%
Subtotal Including Known Risks | [6 empty] | 59123328.44 | 50410229.76 | 10550707.2 | 6295449.6 | 5163430.8 | 2574828 | 7123135.6056 | 17328.5963 | 115434.7086 | 141373872.7105 | 78.16%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 17199513.728 | 14664794.112 | 3069296.64 | 1831403.52 | 1502088.96 | 732395.52 | 474875.707 | 4158.8631 | 27704.3301 | 39506231.3802 | 21.84%
Subtotal Including Unknown Risks | [6 empty] | 76322842.168 | 65075023.872 | 13620003.84 | 8126853.12 | 6665519.76 | 3307223.52 | 7598011.3126 | 21487.4595 | 143139.0386 | 180880104.0907 | 100%
Network Element 2
Halys 500/275kV Substation
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 1 | lot | 2700000 | 4050000 | 900000 | 200000 | 540000 | 200000 | 700000 | 0 | 0 | 9290000 | 3.882%
| Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/275 | 3 | ea. | 52650000 | 8370000 | 4320000 | 600000 | 1080000 | 450000 | 0 | 0 | 0 | 67470000 | 28.2%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 3 | lot | 5940000 | 8100000 | 1080000 | 600000 | 1080000 | 600000 | 1260000 | 0 | 0 | 18660000 | 7.798%
| Station | Property site work and building | AIS site infrastructure 40000 m2 footprint area and applicable control building | N/A | 1 | lot | 1750000 | 23450000 | 1750000 | 3500000 | 700000 | 700000 | 2706817.86 | 47630.93 | 395551.2 | 34999999.99 | 14.63%
| Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 2 | lot | 8100000 | 9000000 | 2700000 | 1200000 | 1620000 | 600000 | 1680000 | 0 | 0 | 24900000 | 10.41%
Baseline Cost | [6 empty] | 71140000 | 52970000 | 10750000 | 6100000 | 5020000 | 2550000 | 6346817.86 | 47630.93 | 395551.2 | 155319999.99 | 64.91%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 5% | 5% | 5% | 5% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 16 - 20 |  |  |  | 0.164% | 0.984% | 0.984% | 0.984% | 0.96% | 0.96% | 2% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | QLD - South - Scrub |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -51.49% | -61.09%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 2.164% | 14.98% | 14.98% | 14.98% | 14.96% | 14.96% | 16% | -51.49% | -61.09%
Adjusted Baseline | [6 empty] | 72679469.6 | 60907024.8 | 12360780 | 7014024 | 5770992 | 2931480 | 7362308.7176 | 23104.7935 | 153912.9448 | 169203096.8559 | 70.71%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 10% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 7267946.96 | 6090702.48 | 1236078 | 701402.4 | 577099.2 | 366435 | 1472461.7435 | 0 | 0 | 17712125.7835 | 7.402%
Subtotal Including Known Risks | [6 empty] | 79947416.56 | 66997727.28 | 13596858 | 7715426.4 | 6348091.2 | 3297915 | 8834770.4611 | 23104.7935 | 153912.9448 | 186915222.6394 | 78.12%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 23257430.272 | 19490247.936 | 3955449.6 | 2244487.68 | 1846717.44 | 938073.6 | 588984.6974 | 5545.1504 | 36939.1067 | 52363875.4826 | 21.88%
Subtotal Including Unknown Risks | [6 empty] | 103204846.832 | 86487975.216 | 17552307.6 | 9959914.08 | 8194808.64 | 4235988.6 | 9423755.1585 | 28649.944 | 190852.0515 | 239279098.122 | 100%
Network Element 3
Gladstone West 500/275kV Substation
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/275 | 3 | ea. | 52650000 | 8370000 | 4320000 | 600000 | 1080000 | 450000 | 0 | 0 | 0 | 67470000 | 24.01%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 275 | 3 | lot | 5940000 | 8100000 | 1080000 | 600000 | 1080000 | 600000 | 1260000 | 0 | 0 | 18660000 | 6.642%
| Station | Reactive Plant | SVC ±200MVAr | 275 | 1 | ea. | 19500000 | 1500000 | 1000000 | 1000000 | 1500000 | 200000 | 0 | 0 | 0 | 24700000 | 8.791%
| Station | AIS Switchbay | 3CB Diameter 3CBs | 500 | 3 | lot | 12150000 | 13500000 | 4050000 | 1800000 | 2430000 | 900000 | 2520000 | 0 | 0 | 37350000 | 13.29%
| Station | Property site work and building | AIS site infrastructure 40000 m2 footprint area and applicable control building | N/A | 1 | lot | 1750000 | 23450000 | 1750000 | 3500000 | 700000 | 700000 | 2706817.86 | 47630.93 | 395551.2 | 34999999.99 | 12.46%
Baseline Cost | [6 empty] | 91990000 | 54920000 | 12200000 | 7500000 | 6790000 | 2850000 | 6486817.86 | 47630.93 | 395551.2 | 183179999.99 | 65.2%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 5% | 5% | 5% | 5% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 16 - 20 |  |  |  | 0.164% | 0.984% | 0.984% | 0.984% | 0.96% | 0.96% | 2% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | QLD - South - Scrub |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -51.49% | -61.09%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 2.164% | 14.98% | 14.98% | 14.98% | 14.96% | 14.96% | 16% | -51.49% | -61.09%
Adjusted Baseline | [6 empty] | 93980663.6 | 63149212.8 | 14028048 | 8623800 | 7805784 | 3276360 | 7524708.7176 | 23104.7935 | 153912.9448 | 198565594.8559 | 70.67%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 10% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 9398066.36 | 6314921.28 | 1402804.8 | 862380 | 780578.4 | 409545 | 1504941.7435 | 0 | 0 | 20673237.5835 | 7.358%
Subtotal Including Known Risks | [6 empty] | 103378729.96 | 69464134.08 | 15430852.8 | 9486180 | 8586362.4 | 3685905 | 9029650.4611 | 23104.7935 | 153912.9448 | 219238832.4394 | 78.03%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 30073812.352 | 20207748.096 | 4488975.36 | 2759616 | 2497850.88 | 1048435.2 | 601976.6974 | 5545.1504 | 36939.1067 | 61720898.8426 | 21.97%
Subtotal Including Unknown Risks | [6 empty] | 133452542.312 | 89671882.176 | 19919828.16 | 12245796 | 11084213.28 | 4734340.2 | 9631627.1585 | 28649.944 | 190852.0515 | 280959731.282 | 100%