## outputA
Project Name: REZ N5 Option 1 | [5 empty] | Indirect Cost Selection
• Expand the existing Dinawan to 500/330kV substation with 3 x 500/330/33kV 1,500MVA transformers • Expand the existing 500 kV Gugga substation to accommodate new Dinawan - Gugga 500 kV line • Re-terminate the Dinawan - Wagga 330 kV DCST line (already built for 500 kV) at Dinawan 500 kV • Re-terminate the Gugga - Wagga 330 kV DCST line (already built for 500 kV) at Gugga 500 kV • Re-arrange the Dinawan - Wagga 330 kV DCST and Wagga - Gugga 330 kV DCST lines by disconnecting from Wagga and connecting together (bypassing Wagga) to make the 500 kV DCST transmission line between Dinawan and Gugga • 500 kV line shunt reactors at Dinawan and Gugaa on the Dinawan- Gugga 500 kV DCST transmission line • Terminate Lower Tumut - Wagga 330 kV SCST line (line O51) at Gugga 330 kV • Build 330 kV DCST transmission line between Gugga and Wagga, using the Line 051 easement | [5 empty] | Total Network Elements Cost Category |  |  | $500-$1000 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View A | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ N5 Option 1.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element Number | Network Element | Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Dinawan 500kv Station Upgrade | 273893451.4707 | 115329181.712 | 103893179.904 | 18213006.336 | 11197870.08 | 8460768.96 | 4204360.44 | 12111804.4705 | 111759.3959 | 371520.1723
2 | Gugga 500kv Expansion | 77930338.421 | 25893486.432 | 34812201.984 | 4446213.12 | 3622840.32 | 2897072.64 | 1306534.32 | 4855333.7004 | 22351.8717 | 74304.033
3 | Gugga to Wagga | 61659300.0012 | 16371803.1887 | 15724647.9359 | 11436107.5802 | 0 | 2144270.1778 | 0 | 7601468.2344 | 1938124.0861 | 6442878.798
4 | 500kv Line switch over | 36355180.5475 | 10122900.3383 | 8991075.9939 | 6538964.39 | 0 | 1226055.8019 | 0 | 5485230.2903 | 922916.2047 | 3068037.5284
5 | 330 kV line demolison and cut overs | 58022305.3724 | 15415611.9068 | 14806253.6129 | 10768184.4267 | 0 | 2019034.5844 | 0 | 5933801.0517 | 2099634.4234 | 6979785.3665
| Total Network Element Cost | 507860575.8128 | 183132983.5777 | 178227359.4307 | 51402475.8529 | 14820710.4 | 16747202.1641 | 5510894.76 | 35987637.7473 | 5094785.9818 | 16936525.8982
Indirect Costs
| Project Development | 23971019.1784
| Works Delivery | 27221326.8636
| Land and Environment | 3250307.6852
| Stakeholder and Community Engagement | 2844019.2246
| Procurement Costs | 2031442.3033
| Insurance | 1625153.8426
| Total Indirect Cost | 60943269.0975
| Total Expected Project Cost | 568803844.9103

## outputB
Project Name: REZ N5 Option 1 | [5 empty] | Indirect Cost Selection
• Expand the existing Dinawan to 500/330kV substation with 3 x 500/330/33kV 1,500MVA transformers • Expand the existing 500 kV Gugga substation to accommodate new Dinawan - Gugga 500 kV line • Re-terminate the Dinawan - Wagga 330 kV DCST line (already built for 500 kV) at Dinawan 500 kV • Re-terminate the Gugga - Wagga 330 kV DCST line (already built for 500 kV) at Gugga 500 kV • Re-arrange the Dinawan - Wagga 330 kV DCST and Wagga - Gugga 330 kV DCST lines by disconnecting from Wagga and connecting together (bypassing Wagga) to make the 500 kV DCST transmission line between Dinawan and Gugga • 500 kV line shunt reactors at Dinawan and Gugaa on the Dinawan- Gugga 500 kV DCST transmission line • Terminate Lower Tumut - Wagga 330 kV SCST line (line O51) at Gugga 330 kV • Build 330 kV DCST transmission line between Gugga and Wagga, using the Line 051 easement | [5 empty] | Total Network Elements Cost Category |  |  | $500-$1000 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View B | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Commensurate with land use
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ N5 Option 1.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
| Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 332525448.09 | 124435345.01 | 107283753.48 | 30526366.17 | 9000000 | 10043693.65 | 3290000 | 23460476.73 | 2631609 | 21854204.05
Adjusted Baseline Cost | 359834962.008 | 128158278.7025 | 124749694.032 | 35644358.7157 | 10437120 | 11689822.8522 | 3813768 | 28115341.9901 | 3983681.3685 | 13242896.347
Known Risk Allowance | 37167716.8283 | 12815827.8703 | 12474969.4032 | 3564435.8716 | 1043712 | 1168982.2852 | 476721 | 5623068.398 | 0 | 0
Unknown Risk Allowance | 110857896.9765 | 42158877.0049 | 41002695.9955 | 12193681.2657 | 3339878.4 | 3888397.0268 | 1220405.76 | 2249227.3592 | 1111104.6133 | 3693629.5512
Total Network Element Cost | 507860575.8128 | 183132983.5777 | 178227359.4307 | 51402475.8529 | 14820710.4 | 16747202.1641 | 5510894.76 | 35987637.7473 | 5094785.9818 | 16936525.8982
Indirect Costs
Project Development | 23971019.1784
Works Delivery | 27221326.8636
Land and Environment | 3250307.6852
Stakeholder and Community Engagement | 2844019.2246
Procurement Costs | 2031442.3033
Insurance | 1625153.8426
Total Indirect Cost | 60943269.0975
Total Expected Project Cost | 568803844.9103

## outputC
Project Name: REZ N5 Option 1
• Expand the existing Dinawan to 500/330kV substation with 3 x 500/330/33kV 1,500MVA transformers • Expand the existing 500 kV Gugga substation to accommodate new Dinawan - Gugga 500 kV line • Re-terminate the Dinawan - Wagga 330 kV DCST line (already built for 500 kV) at Dinawan 500 kV • Re-terminate the Gugga - Wagga 330 kV DCST line (already built for 500 kV) at Gugga 500 kV • Re-arrange the Dinawan - Wagga 330 kV DCST and Wagga - Gugga 330 kV DCST lines by disconnecting from Wagga and connecting together (bypassing Wagga) to make the 500 kV DCST transmission line between Dinawan and Gugga • 500 kV line shunt reactors at Dinawan and Gugaa on the Dinawan- Gugga 500 kV DCST transmission line • Terminate Lower Tumut - Wagga 330 kV SCST line (line O51) at Gugga 330 kV • Build 330 kV DCST transmission line between Gugga and Wagga, using the Line 051 easement
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ N5 Option 1.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element 1
Dinawan 500kv Station Upgrade
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | Property site work and building | AIS site infrastructure 25000 m2 footprint area and applicable control building | N/A | 2 | lot | 2400000 | 32160000 | 2400000 | 4800000 | 960000 | 960000 | 3766022.33 | 59538.67 | 494439.01 | 48000000.01 | 17.53%
| Station | Transformer | 2 winding Tx (3 banks of 1ph) 1500MVA | 500/330 | 3 | ea. | 52650000 | 8370000 | 4320000 | 600000 | 1080000 | 450000 | 0 | 0 | 0 | 67470000 | 24.63%
| Station | AIS Switchbay | 3CB Diameter 1CB | 500 | 2 | lot | 3060000 | 4680000 | 900000 | 200000 | 540000 | 200000 | 980000 | 0 | 0 | 10560000 | 3.856%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 500 | 3 | lot | 8100000 | 12150000 | 2700000 | 600000 | 1620000 | 600000 | 2100000 | 0 | 0 | 27870000 | 10.18%
| Station | AIS Switchbay | 3CB Diameter 2CBs | 330 | 1 | lot | 2160000 | 3330000 | 540000 | 200000 | 540000 | 200000 | 910000 | 0 | 0 | 7880000 | 2.877%
| Station | Reactive Plant | Reactor 200MVAr | 500 | 2 | ea. | 11000000 | 2400000 | 200000 | 400000 | 400000 | 100000 | 0 | 0 | 0 | 14500000 | 5.294%
Baseline Cost | [6 empty] | 79370000 | 63090000 | 11060000 | 6800000 | 5140000 | 2510000 | 7756022.33 | 59538.67 | 494439.01 | 176280000.01 | 64.36%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 5% | 5% | 5% | 5% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 6 - 10 |  |  |  | 0.328% | 1.968% | 1.968% | 1.968% | 1.92% | 1.92% | 8% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Southern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.38% | -39.4%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 2.328% | 15.97% | 15.97% | 15.97% | 15.92% | 15.92% | 22% | 51.38% | -39.4%
Adjusted Baseline | [6 empty] | 81217733.6 | 73164211.2 | 12826060.8 | 7885824 | 5958288 | 2909592 | 9462347.2426 | 90128.5451 | 299613.0422 | 193813798.4298 | 70.76%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 10% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 8121773.36 | 7316421.12 | 1282606.08 | 788582.4 | 595828.8 | 363699 | 1892469.4485 | 0 | 0 | 20361380.2085 | 7.434%
Subtotal Including Known Risks | [6 empty] | 89339506.96 | 80480632.32 | 14108666.88 | 8674406.4 | 6554116.8 | 3273291 | 11354816.6911 | 90128.5451 | 299613.0422 | 214175178.6384 | 78.2%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 25989674.752 | 23412547.584 | 4104339.456 | 2523463.68 | 1906652.16 | 931069.44 | 756987.7794 | 21630.8508 | 71907.1301 | 59718272.8323 | 21.8%
Subtotal Including Unknown Risks | [6 empty] | 115329181.712 | 103893179.904 | 18213006.336 | 11197870.08 | 8460768.96 | 4204360.44 | 12111804.4705 | 111759.3959 | 371520.1723 | 273893451.4707 | 100%
Network Element 2
Gugga 500kv Expansion
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Station | AIS Switchbay | 3CB Diameter 1CB | 500 | 4 | lot | 6120000 | 9360000 | 1800000 | 400000 | 1080000 | 400000 | 1960000 | 0 | 0 | 21120000 | 27.1%
| Station | Property site work and building | AIS site infrastructure 10000 m2 footprint area and applicable control building | N/A | 1 | lot | 700000 | 9380000 | 700000 | 1400000 | 280000 | 280000 | 1149204.47 | 11907.73 | 98887.8 | 14000000 | 17.96%
| Station | Reactive Plant | Reactor 200MVAr | 500 | 2 | ea. | 11000000 | 2400000 | 200000 | 400000 | 400000 | 100000 | 0 | 0 | 0 | 14500000 | 18.61%
Baseline Cost | [6 empty] | 17820000 | 21140000 | 2700000 | 2200000 | 1760000 | 780000 | 3109204.47 | 11907.73 | 98887.8 | 49620000 | 63.67%
Adjustments | Station project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 5% | 5% | 5% | 5% | 0% | 0%
| Station project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 9% | 9% | 9% | 9% | 0% | 0%
| Station project attribute | Project network element size | # of total Bays 6 - 10 |  |  |  | 0.328% | 1.968% | 1.968% | 1.968% | 1.92% | 1.92% | 8% | 0% | 0%
| Station project attribute | Jurisdiction + Land use | NSW - Southern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.38% | -39.4%
| Station project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 2.328% | 15.97% | 15.97% | 15.97% | 15.92% | 15.92% | 22% | 51.38% | -39.4%
Adjusted Baseline | [6 empty] | 18234849.6 | 24515635.2 | 3131136 | 2551296 | 2040192 | 904176 | 3793229.4534 | 18025.703 | 59922.6072 | 55248462.5636 | 70.89%
Known Risks | Station known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 10% | 10% | 10% | 20% | 0% | 0%
| Station known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Station known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 10% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 1823484.96 | 2451563.52 | 313113.6 | 255129.6 | 204019.2 | 113022 | 758645.8907 | 0 | 0 | 5918978.7707 | 7.595%
Subtotal Including Known Risks | [6 empty] | 20058334.56 | 26967198.72 | 3444249.6 | 2806425.6 | 2244211.2 | 1017198 | 4551875.3441 | 18025.703 | 59922.6072 | 61167441.3343 | 78.49%
Unknown Risk | Station unknown risk | Scope and technology risks | Class 5b |  |  |  | 24% | 24% | 24% | 24% | 24% | 24% | 0% | 24% | 24%
| Station unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 8% | 8% | 8% | 0% | 0% | 0%
| Station unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Station unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 32% | 32% | 32% | 32% | 32% | 32% | 8% | 24% | 24%
Total Unknown Risk Rate $ | [6 empty] | 5835151.872 | 7845003.264 | 1001963.52 | 816414.72 | 652861.44 | 289336.32 | 303458.3563 | 4326.1687 | 14381.4257 | 16762897.0867 | 21.51%
Subtotal Including Unknown Risks | [6 empty] | 25893486.432 | 34812201.984 | 4446213.12 | 3622840.32 | 2897072.64 | 1306534.32 | 4855333.7004 | 22351.8717 | 74304.033 | 77930338.421 | 100%
Network Element 3
Gugga to Wagga
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 2 x Olive DCST 2212 MVA | 330 | 12 | km | 10643093.99 | 9005694.92 | 6549596.3 | 0 | 1228049.31 | 0 | 4919356.41 | 1000249.58 | 8306575.29 | 41652615.8 | 67.55%
Baseline Cost | [6 empty] | 10643093.99 | 9005694.92 | 6549596.3 | 0 | 1228049.31 | 0 | 4919356.41 | 1000249.58 | 8306575.29 | 41652615.8 | 67.55%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 0% | 5% | 5% | 5% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 5 to 100 km |  |  |  | 3.36% | 5.594% | 5.594% | 0% | 5.594% | 5.594% | 6.72% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Southern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.38% | -39.4%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Flat/Farmland |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 5.36% | 19.59% | 19.59% | 0% | 19.59% | 19.59% | 20.72% | 51.38% | -39.4%
Adjusted Baseline | [6 empty] | 11213563.8279 | 10770306.8054 | 7832950.3974 | 0 | 1468678.204 | 0 | 5938647.0582 | 1514159.4423 | 5033499.061 | 43771804.7961 | 70.99%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 0% | 10% | 10% | 20% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 0% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 1121356.3828 | 1077030.6805 | 783295.0397 | 0 | 146867.8204 | 0 | 1187729.4116 | 0 | 0 | 4316279.3351 | 7%
Subtotal Including Known Risks | [6 empty] | 12334920.2107 | 11847337.4859 | 8616245.4371 | 0 | 1615546.0244 | 0 | 7126376.4698 | 1514159.4423 | 5033499.061 | 48088084.1312 | 77.99%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 4036882.978 | 3877310.4499 | 2819862.1431 | 0 | 528724.1534 | 0 | 475091.7647 | 423964.6438 | 1409379.7371 | 13571215.87 | 22.01%
Subtotal Including Unknown Risks | [6 empty] | 16371803.1887 | 15724647.9359 | 11436107.5802 | 0 | 2144270.1778 | 0 | 7601468.2344 | 1938124.0861 | 6442878.798 | 61659300.0012 | 100%
Network Element 4
500kv Line switch over
Cut into 500kV Line at Dinawan, Swing PEC 500kV over to transmission line from Wagga to Gugga , Extend 500kV around Gugga substation
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 1 | km | 1316152.88 | 1113667.82 | 809940.24 | 0 | 151863.79 | 0 | 767156.49 | 95261.86 | 791102.41 | 5045145.49 | 13.88%
| Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 1 | km | 1316152.88 | 1113667.82 | 809940.24 | 0 | 151863.79 | 0 | 767156.49 | 95261.86 | 791102.41 | 5045145.49 | 13.88%
| Overhead line | HVAC | 4 × Orange DCST 6124 MVA | 500 | 3 | km | 3948458.65 | 3341003.47 | 2429820.71 | 0 | 455591.38 | 0 | 2301469.48 | 285785.59 | 2373307.23 | 15135436.51 | 41.63%
Baseline Cost | [6 empty] | 6580764.41 | 5568339.11 | 4049701.19 | 0 | 759318.96 | 0 | 3835782.46 | 476309.31 | 3955512.05 | 25225727.49 | 69.39%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 0% | 5% | 5% | 5% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Greenfield |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Project network element size | 5 to 100 km |  |  |  | 3.36% | 5.594% | 5.594% | 0% | 5.594% | 5.594% | 6.72% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Southern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.38% | -39.4%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Flat/Farmland |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 5.36% | 10.59% | 10.59% | 0% | 10.59% | 10.59% | 11.72% | 51.38% | -39.4%
Adjusted Baseline | [6 empty] | 6933493.3824 | 6158271.2287 | 4478742.7329 | 0 | 839764.2479 | 0 | 4285336.1643 | 721028.2849 | 2396904.3191 | 25813540.3601 | 71%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 0% | 10% | 10% | 20% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 0% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 693349.3382 | 615827.1229 | 447874.2733 | 0 | 83976.4248 | 0 | 857067.2329 | 0 | 0 | 2698094.392 | 7.421%
Subtotal Including Known Risks | [6 empty] | 7626842.7206 | 6774098.3515 | 4926617.0062 | 0 | 923740.6727 | 0 | 5142403.3972 | 721028.2849 | 2396904.3191 | 28511634.7522 | 78.43%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 2496057.6177 | 2216977.6423 | 1612347.3838 | 0 | 302315.1292 | 0 | 342826.8931 | 201887.9198 | 671133.2093 | 7843545.7953 | 21.57%
Subtotal Including Unknown Risks | [6 empty] | 10122900.3383 | 8991075.9939 | 6538964.39 | 0 | 1226055.8019 | 0 | 5485230.2903 | 922916.2047 | 3068037.5284 | 36355180.5475 | 100%
Network Element 5
330 kV line demolison and cut overs
Demolish Line 51 Gugga 330kV Substation to Wagga 330kV substation Cut line 51 into Gugga 500kV substation Connect Dinawan 330kV Substation to Dinawan 500kV substation
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 11 | km | 8373348.6 | 7085141.13 | 5152829.91 | 0 | 966155.61 | 0 | 3144317.63 | 916895.45 | 7614360.68 | 33253049.01 | 57.31%
| Overhead line | HVAC | 2 x Olive SCST 1106MVA | 330 | 1 | km | 761213.51 | 644103.74 | 468439.08 | 0 | 87832.33 | 0 | 285847.06 | 83354.13 | 692214.61 | 3023004.46 | 5.21%
| Overhead line | HVAC | 2 x Olive DCST 2212 MVA | 330 | 1 | km | 886924.5 | 750474.58 | 545799.69 | 0 | 102337.44 | 0 | 409946.37 | 83354.13 | 692214.61 | 3471051.32 | 5.982%
Baseline Cost | [6 empty] | 10021486.61 | 8479719.45 | 6167068.68 | 0 | 1156325.38 | 0 | 3840111.06 | 1083603.71 | 8998789.9 | 39747104.79 | 68.5%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 0% | 5% | 5% | 5% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 5 to 100 km |  |  |  | 3.36% | 5.594% | 5.594% | 0% | 5.594% | 5.594% | 6.72% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | NSW - Southern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 51.38% | -39.4%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Flat/Farmland |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 5.36% | 19.59% | 19.59% | 0% | 19.59% | 19.59% | 20.72% | 51.38% | -39.4%
Adjusted Baseline | [6 empty] | 10558638.2923 | 10141269.5979 | 7375468.7854 | 0 | 1382900.4003 | 0 | 4635782.0716 | 1640339.3933 | 5452957.3176 | 41187355.8584 | 70.99%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | Tight |  |  |  | 10% | 10% | 10% | 0% | 10% | 10% | 20% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | High |  |  |  | 0% | 0% | 0% | 0% | 0% | 2.5% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 10% | 10% | 10% | 0% | 10% | 12.5% | 20% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 1055863.8292 | 1014126.9598 | 737546.8785 | 0 | 138290.04 | 0 | 927156.4143 | 0 | 0 | 3872984.1219 | 6.675%
Subtotal Including Known Risks | [6 empty] | 11614502.1215 | 11155396.5577 | 8113015.664 | 0 | 1521190.4403 | 0 | 5562938.486 | 1640339.3933 | 5452957.3176 | 45060339.9803 | 77.66%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 3801109.7852 | 3650857.0552 | 2655168.7628 | 0 | 497844.1441 | 0 | 370862.5657 | 459295.0301 | 1526828.0489 | 12961965.3921 | 22.34%
Subtotal Including Unknown Risks | [6 empty] | 15415611.9068 | 14806253.6129 | 10768184.4267 | 0 | 2019034.5844 | 0 | 5933801.0517 | 2099634.4234 | 6979785.3665 | 58022305.3724 | 100%