## outputA
Project Name: REZ T3 Option 2 | [5 empty] | Indirect Cost Selection
Re-build of Palmerston-Hadspen- George Town 220 kV transmission line. | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View A | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Sensitive
View A illustrates the cost breakdown for each network element and the total expected project cost after accounting for the indirect costs. The costs for each network element is adjusted for the respectively chosen project attributes and risks. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ T3 Option 2.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element Number | Network Element | Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
1 | Line Palmerston - Hadspen | 178892304.4888 | 36076003.5488 | 40444548.1935 | 29414216.8611 | 0 | 4724995.6212 | 0 | 15368573.3335 | 4809193.3459 | 48054773.5847
2 | Line Hadspen - George Town | 234790916.449 | 50506404.9626 | 48509955.021 | 35279967.288 | 0 | 6614993.8665 | 0 | 19870041.6227 | 6732870.6651 | 67276683.0232
| Total Network Element Cost | 413683220.9378 | 86582408.5114 | 88954503.2145 | 64694184.1491 | 0 | 11339989.4877 | 0 | 35238614.9562 | 11542064.011 | 115331456.6078
Indirect Costs
| Project Development | 20270477.826
| Works Delivery | 23579943.5935
| Land and Environment | 3309465.7675
| Stakeholder and Community Engagement | 106316587.781
| Procurement Costs | 2068416.1047
| Insurance | 1654732.8838
| Total Indirect Cost | 157199623.9564
| Total Expected Project Cost | 570882844.8942

## outputB
Project Name: REZ T3 Option 2 | [5 empty] | Indirect Cost Selection
Re-build of Palmerston-Hadspen- George Town 220 kV transmission line. | [5 empty] | Total Network Elements Cost Category |  |  | $100-$500 million
[6 empty] | Greenfield or Brownfield |  |  | Brownfield
Project Cost Estimate - View B | [5 empty] | Stakeholder and Community Sensitive Region |  |  | Sensitive
View B provides a high level overview of the cost breakdown and the total expected project cost accounting for the indirect costs. The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advanced knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors.This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | Contract Delivery Model |  |  | EPC contract
TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ T3 Option 2.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
| Total Network Element Costs | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs
Baseline Cost | 237677294.2 | 60424768.1 | 51128649.94 | 37184472.68 | 0 | 6972088.63 | 0 | 26126365.65 | 6001497.47 | 49839451.73
Adjusted Baseline Cost | 316727024.4025 | 63663535.6702 | 65407722.9518 | 47569253.0508 | 0 | 8338227.5645 | 0 | 32628347.1817 | 9017237.5086 | 90102700.4749
Known Risk Allowance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unknown Risk Allowance | 96956196.5353 | 22918872.8413 | 23546780.2627 | 17124931.0983 | 0 | 3001761.9232 | 0 | 2610267.7745 | 2524826.5024 | 25228756.133
Total Network Element Cost | 413683220.9378 | 86582408.5114 | 88954503.2145 | 64694184.1491 | 0 | 11339989.4877 | 0 | 35238614.9562 | 11542064.011 | 115331456.6078
Indirect Costs
Project Development | 20270477.826
Works Delivery | 23579943.5935
Land and Environment | 3309465.7675
Stakeholder and Community Engagement | 106316587.781
Procurement Costs | 2068416.1047
Insurance | 1654732.8838
Total Indirect Cost | 157199623.9564
Total Expected Project Cost | 570882844.8942

## outputC
Project Name: REZ T3 Option 2
Re-build of Palmerston-Hadspen- George Town 220 kV transmission line.
Project Cost Estimate - View C
View C provides a detailed cost breakdown of the selected building blocks, adjustment factors and risk factors for each network element. Indirect costs are only applied at a project level and are hence exlcuded from View C (network element level). The TCD is designed to compile Class 5b project cost estimates (+/- 50%) using the selection of the provided building blocks, attributes and risk factors based on unbiased and objective user judgement. While the TCD allows the selection of other or more mature classes of cost estimates for unknown risk factors, it is expected to be used only in special circumstances where the user has advance knowledge of project scope and cost resulting in bespoke description and quantities of building blocks and project attributes. For further qualification of this cost estimate output, please refer to the Section 9 of the TCD report and also the messages in description and note field when selecting unknown risk factors. This cost estimate is subject to the full legal disclaimer listed in the TCD user interface. | [5 empty] | TCD Cost Estimation Tool Version
[6 empty] | Tool Version |  |  | 15-05-2025
[6 empty] | Project file |  |  | REZ T3 Option 2.xlsx
Cost and Risk Data Version
[6 empty] | Release Date |  |  | 7-03-2025
[6 empty] | Version Number |  |  | 5-0
Network Element 1
Line Palmerston - Hadspen
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 1 x Sulphur DCST 862 MVA | 220 | 35 | km | 25176986.71 | 21303604.14 | 15493530.28 | 0 | 2905036.93 | 0 | 10885985.69 | 2500623.95 | 20766438.22 | 99032205.92 | 55.36%
Baseline Cost | [6 empty] | 25176986.71 | 21303604.14 | 15493530.28 | 0 | 2905036.93 | 0 | 10885985.69 | 2500623.95 | 20766438.22 | 99032205.92 | 55.36%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 0% | 5% | 5% | 5% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 5 to 100 km |  |  |  | 3.36% | 5.594% | 5.594% | 0% | 5.594% | 5.594% | 6.72% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | TAS - Northern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50.25% | 80.79%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Mountainous |  |  |  | 0% | 20% | 20% | 0% | 0% | 0% | 10% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 5.36% | 39.59% | 39.59% | 0% | 19.59% | 19.59% | 30.72% | 50.25% | 80.79%
Adjusted Baseline | [6 empty] | 26526473.1977 | 29738638.3776 | 21628100.6332 | 0 | 3474261.4862 | 0 | 14230160.494 | 3757182.3015 | 37542791.863 | 136897608.3532 | 76.53%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Subtotal Including Known Risks | [6 empty] | 26526473.1977 | 29738638.3776 | 21628100.6332 | 0 | 3474261.4862 | 0 | 14230160.494 | 3757182.3015 | 37542791.863 | 136897608.3532 | 76.53%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 9549530.3512 | 10705909.8159 | 7786116.2279 | 0 | 1250734.135 | 0 | 1138412.8395 | 1052011.0444 | 10511981.7216 | 41994696.1357 | 23.47%
Subtotal Including Unknown Risks | [6 empty] | 36076003.5488 | 40444548.1935 | 29414216.8611 | 0 | 4724995.6212 | 0 | 15368573.3335 | 4809193.3459 | 48054773.5847 | 178892304.4888 | 100%
Network Element 2
Line Hadspen - George Town
| Category | Subcategory | Details | Nominal Voltage | QTY | UOM | Plant and Materials | Civil and Structural Works | Electrical Works | Secondary Systems | Design & Survey | Testing & Commissioning | Contractor Project Management & Overheads | Easement/ Property Costs | Environmental Offset Costs | Total Network Element costs | Percent of Total
Building Blocks | Overhead line | HVAC | 1 x Sulphur DCST 862 MVA | 220 | 49 | km | 35247781.39 | 29825045.8 | 21690942.4 | 0 | 4067051.7 | 0 | 15240379.96 | 3500873.52 | 29073013.51 | 138645088.28 | 59.05%
Baseline Cost | [6 empty] | 35247781.39 | 29825045.8 | 21690942.4 | 0 | 4067051.7 | 0 | 15240379.96 | 3500873.52 | 29073013.51 | 138645088.28 | 59.05%
Adjustments | Overhead line project attribute | Contract delivery model | EPC contract |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Delivery timetable | Tight |  |  |  | 2% | 5% | 5% | 0% | 5% | 5% | 5% | 0% | 0%
| Overhead line project attribute | Greenfield or brownfield | Brownfield |  |  |  | 0% | 9% | 9% | 0% | 9% | 9% | 9% | 0% | 0%
| Overhead line project attribute | Project network element size | 5 to 100 km |  |  |  | 3.36% | 5.594% | 5.594% | 0% | 5.594% | 5.594% | 6.72% | 0% | 0%
| Overhead line project attribute | Jurisdiction + Land use | TAS - Northern - Grazing |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50.25% | 80.79%
| Overhead line project attribute | Location (regional/distance factors) | Regional |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Location wind loading zones | Non-cyclone region |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Land Use | NA |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Terrain | Flat/Farmland |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line project attribute | Proportion of environmentally sensitive areas |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Adjustment Rate % | [6 empty] | 5.36% | 19.59% | 19.59% | 0% | 19.59% | 19.59% | 20.72% | 50.25% | 80.79%
Adjusted Baseline | [6 empty] | 37137062.4725 | 35669084.5742 | 25941152.4176 | 0 | 4863966.0783 | 0 | 18398186.6877 | 5260055.2071 | 52559908.6118 | 179829416.0493 | 76.59%
Known Risks | Overhead line known risk | Macroeconomic influence | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Market activity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Weather delays | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Project complexity | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Compulsory acquisition | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Environmental offset risks | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Geotechnical findings | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Outage restrictions | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line known risk | Cultural heritage | BAU |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate % | [6 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Total Known Risk Rate $ | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Subtotal Including Known Risks | [6 empty] | 37137062.4725 | 35669084.5742 | 25941152.4176 | 0 | 4863966.0783 | 0 | 18398186.6877 | 5260055.2071 | 52559908.6118 | 179829416.0493 | 76.59%
Unknown Risk | Overhead line unknown risk | Scope and technology risks | Class 5b |  |  |  | 28% | 28% | 28% | 0% | 28% | 28% | 0% | 28% | 28%
| Overhead line unknown risk | Productivity and labour cost risks | Class 5b |  |  |  | 0% | 8% | 8% | 0% | 8% | 8% | 0% | 0% | 0%
| Overhead line unknown risk | Plant procurement cost risks | Class 5b |  |  |  | 8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Overhead line unknown risk | Project overhead risks | Class 5b |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 8% | 0% | 0%
Total Unknown Risk Rate % | [6 empty] | 36% | 36% | 36% | 0% | 36% | 36% | 8% | 28% | 28%
Total Unknown Risk Rate $ | [6 empty] | 13369342.4901 | 12840870.4467 | 9338814.8703 | 0 | 1751027.7882 | 0 | 1471854.935 | 1472815.458 | 14716774.4113 | 54961500.3997 | 23.41%
Subtotal Including Unknown Risks | [6 empty] | 50506404.9626 | 48509955.021 | 35279967.288 | 0 | 6614993.8665 | 0 | 19870041.6227 | 6732870.6651 | 67276683.0232 | 234790916.449 | 100%